## 1. Neknampur
Name of the work: Erection of new 33/11 kV Sub Station with 2x12.5 MVA PTRS and 33 kV and 11 Kv connecting lines at Neknampur Sy.No.20 of Narsingi section in Ibarahimbagh division of Cybercity circle of ECGH Division /Masterplan/RR Circle
WBS No. S-1785-13-03-02-01-001
Sl No | Estimate Quantity | Description of item | Work Type | Item Short Description | APSS / Month Cl.NumberSSR 11 & 12 | Rate (INR) | UOM | AMOUNT
1 | 16 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | ELEC | Labour | SWR11039 | 928 | EA | 14848
2 | 5.76 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ELEC | Labour | SWR10868 | 6852 | TO | 39467.52
3 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELEC | supply | SMR40009 | 2181 | TO | 12562.56
4 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELEC | labour | SWR10877 | 851 | TO | 4901.76
5 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELEC | supply | SMR40010 | 1293 | TO | 7447.68
6 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELEC | labour | SWR10879 | 482 | TO | 2776.32
7 | 5.76 | Fabrication & erection of Channels-Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ELEC | labour | SWR10867 | 1470 | TO | 8467.2
8 | 16 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-R.S. Joists 150 x 150 mm | ELEC | labour | SWR10348 | 1952.61 | EA | 31241.76
9 | 17.758 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 116829.882
10 | 9.24 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ELEC | labour | SWR10862 | 373 | M2 | 3446.52
11 | 16 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | ELEC | labour | SWR11089 | 48 | EA | 768
12 | 4 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-8.0Mtrs PSCC Poles 0.76 M x 0.76M x 1.52M (2.6" x 2.6" x 5.0') 0.88 cum | ELEC | labour | SWR11037 | 793 | EA | 3172
13 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELEC | supply | SMR40009 | 2181 | TO | 2181
14 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELEC | labour | SWR10877 | 851 | TO | 851
15 | 1 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELEC | supply | SMR40010 | 1293 | TO | 1293
16 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELEC | labour | SWR10879 | 482 | TO | 482
17 | 4 | R.S Joist box poles erection complete | ELEC | labour | SWR20863 | 1044.23 | EA | 4176.92
18 | 2.65 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 17434.35
19 | 2.31 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ELEC | labour | SWR10862 | 373 | M2 | 861.63
20 | 4 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | ELEC | labour | SWR11089 | 48 | EA | 192
21 | 5.063 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ELEC | labour | SWR10868 | 6852 | TO | 34691.676
22 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELEC | supply | SMR40009 | 2181 | TO | 11042.403
23 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELEC | labour | SWR10877 | 851 | TO | 4308.613
24 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELEC | labour | SMR40010 | 1293 | TO | 6546.459
25 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELEC | labour | SWR10879 | 482 | TO | 2440.366
26 | 5.063 | Fabrication & erection of Channels-Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ELEC | labour | SWR10867 | 1470 | TO | 7442.61
27 | 13 | Erection of AB Switch and aligment complete Erection of 33 KV AB Switch including alignment and earthing | ELEC | labour | SWR10392 | 4500 | EA | 58500
28 | 34 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Note:-The requirement of 2nd coat is to be justified by the concerned Divisional Engineer /Executive Engineer before execution of this work Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | ELEC | labour | SWR10881 | 142 | EA | 4828
29 | 34 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | ELEC | labour | SWR12331 | 146.63 | EA | 4985.42
30 | 6 | Loading of 33 KV CTs/ PTs | ELEC | labour | SWR10200 | 165 | EA | 990
31 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
32 | 6 | Un loading of 33 KV CTs/ PTs | ELEC | labour | SWR10518 | 128 | EA | 768
33 | 2 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33kv single phase PT s | ELEC | labour | SWR10401 | 1079 | SET | 2158
34 | 12 | Loading of 33 KV, 10 KA LAs Station typ | ELEC | labour | SWR10266 | 41 | EA | 492
35 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
36 | 12 | Un loading of 33 KV, 10 KA LAs Station type | ELEC | labour | SWR10584 | 35 | EA | 420
37 | 4 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33 KV LAS station/Line type including earthing | ELEC | labour | SWR10396 | 880 | SET | 3520
38 | 2 | Loading of 33 KV VCBs along with Panel boards | ELEC | labour | SWR10198 | 1024 | EA | 2048
39 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
40 | 2 | Un loading of 33 KV VCBs along with Panel boards | ELEC | labour | SWR10516 | 1044.48 | EA | 2088.96
41 | 12.584 | Excavate-Pit for 33KV VCB | ELEC | labour | SWR23224 | 331 | M3 | 4165.304
42 | 14.52 | Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x 1.8 x 0.75 cum for VCB Plinth | ELEC | labour | SWR20685 | 5160 | M3 | 74923.2
43 | 2 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33 KV VCB with Control Panel | ELEC | labour | SWR10460 | 12500 | EA | 25000
44 | 2 | Loading and unloading of PTR on constructed plinth-Loading of 12.5 MVA PTR | ELEC | labour | SWR10614 | 12044.93 | EA | 24089.86
45 | 2 | Transport of Power transformers (0 to 100 KM) from one place to another place in GHMC Area.(excluding of loading & unloading )-12.5 MVA power transformer | ELEC | labour | SWR10855 | 27431 | EA | 54862
46 | 2 | Loading and unloading of PTR on constructed plinth-Unloading of 12.5 MVA PTR | ELEC | labour | SWR10628 | 12044.93 | EA | 24089.86
47 | 700 | S/o rail poles 90/105lb (250x2N) | ELEC | supply | SMR22718 | 47.27 | KG | 33089
48 | 14 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Rail pole 90 lbs | ELEC | labour | SWR10344 | 3510 | EA | 49140
49 | 2 | Erection of PTR on constructed plinth-Erection of 12.5 MVA PTR. | ELEC | labour | SWR10929 | 51818 | EA | 103636
50 | 0.436 | Extention of 33KV Bay at 132/33KV Sub-station-Zebra condutor | ELEC | supply | SMR24910 | 299369 | KM | 130524.884
51 | 30 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing | ELEC | supply | SMR11915 | 2055 | SET | 61650
52 | 30 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of I-Bolts | ELEC | supply | SMR22473 | 294 | EA | 8820
53 | 45 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 "to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating . Sup T clamp LM6 Al alloy of 12 mm, 800 A | ELEC | labour | SMR40011 | 299 | EA | 13455
54 | 6 | Bus stringing Hoisting of Insulators and hardware, stretching the conductor and stringing of 33 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bussection of 4.5mt) Hoisting post ins&hrd wr 1panther 33kv | ELEC | labour | SWR21240 | 781 | EA | 4686
55 | 84 | Stringing of bus with panther conductor including jumpering etc., complete to all the equipment in SS fixing to all clamps and equipment.(3 Conductors) | ELEC | labour | SWR10404 | 327.68 | M | 27525.12
56 | 30 | Bus stringing Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | ELEC | labour | SWR10884 | 224 | EA | 6720
57 | 75 | Labour for Fixing of all types of clamps | ELEC | labour | SWR10917 | 65 | EA | 4875
58 | 25 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | ELEC | labour | SWR11039 | 928 | EA | 23200
59 | 8.68 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ELEC | labour | SWR10868 | 6852 | TO | 59475.36
60 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELEC | supply | SMR40009 | 2181 | TO | 18931.08
61 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELEC | labour | SWR10877 | 851 | TO | 7386.68
62 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELEC | supply | SMR40010 | 1293 | TO | 11223.24
63 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELEC | labour | SWR10879 | 482 | TO | 4183.76
64 | 8.68 | Fabrication & erection of Channels-Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ELEC | labour | SWR10867 | 1470 | TO | 12759.6
65 | 25 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-R.S. Joists 150 x 150 mm | ELEC | labour | SWR10348 | 1952.61 | EA | 48815.25
66 | 27.75 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 182567.25
67 | 17.91 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ELEC | labour | SWR10862 | 373 | M2 | 6680.43
68 | 25 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | ELEC | labour | SWR11089 | 48 | EA | 1200
69 | 4.642 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ELEC | labour | SWR10868 | 6852 | TO | 31806.984
70 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELEC | supply | SMR40009 | 2181 | TO | 10124.202
71 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELEC | labour | SWR10877 | 851 | TO | 3950.342
72 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELEC | supply | SMR40010 | 1293 | TO | 6002.106
73 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELEC | labour | SWR10879 | 482 | TO | 2237.444
74 | 4.642 | Fabrication & erection of Channels-Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ELEC | labour | SWR10867 | 1470 | TO | 6823.74
75 | 17 | Erection of AB Switch and aligment complete-Erection of 11KV 800A double throw AB Switches | ELEC | labour | SWR21277 | 3500 | EA | 59500
76 | 3 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | ELEC | labour | SWR10393 | 3200 | EA | 9600
77 | 2 | Loading of 11 KV CT - PT Sets | ELEC | labour | SWR10201 | 190 | EA | 380
78 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
79 | 2 | Un loading of 11 KV CT - PT Sets | ELEC | labour | SWR10519 | 101 | EA | 202
80 | 2 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc-Erection of 11 KV three phase PTs | ELEC | labour | SWR10402 | 800 | SET | 1600
81 | 24 | Loading of 11 KV, 10 KA LAs Station type | ELEC | labour | SWR10264 | 32 | EA | 768
82 | 2 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 6599.4
83 | 24 | Un loading of 11 KV, 10 KA LAs Station type | ELEC | labour | SWR10582 | 32 | EA | 768
84 | 2 | Erection of 11 KV LAS station type including earthing | ELEC | labour | SWR10397 | 559 | SET | 1118
85 | 6 | Erection of 11 KV LAS line type including earthing | ELEC | labour | SWR10398 | 505 | SET | 3030
86 | 8 | Loading of 11 KV VCBs along with Panel boards | ELEC | labour | SWR10199 | 1024 | EA | 8192
87 | 4 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 13198.8
88 | 8 | Un Loading of 11 KV VCBs along with Panel boards | ELEC | labour | SWR10517 | 1044.48 | EA | 8355.84
89 | 41.6 | Excavate-Pit for 33KV VCB | ELEC | labour | SWR23224 | 331 | M3 | 13769.6
90 | 48 | Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x 1.8 x 0.75 cum for VCB Plinth | ELEC | labour | SWR20685 | 5160 | M3 | 247680
91 | 8 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc-Erection of 11 KV VCB with Control Panel | ELEC | labour | SWR10461 | 12000 | EA | 96000
92 | 12 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing | ELEC | supply | SMR11915 | 2055 | SET | 24660
93 | 12 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of I-Bolts | ELEC | supply | SMR22473 | 294 | EA | 3528
94 | 45 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 "to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating . Sup T clamp LM6 Al alloy of 12 mm, 800 A | ELEC | supply | SMR40011 | 299 | EA | 13455
95 | 2 | Bus Stringing -Hoisting of Insulators and hardware, stretching the conductor and stringing of 11 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 3.5mt) Hoisting post ins&hrd wr 1panther 11kv | ELEC | labour | SWR21241 | 507 | EA | 1014
96 | 63 | Stringing of bus with panther conductor including jumpering etc., complete to all the equipment in SS fixing to all clamps and equipment.(3 Conductors) | ELEC | labour | SWR10404 | 327.68 | M | 20643.84
97 | 45 | Bus stringing Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | ELEC | labour | SWR10884 | 224 | EA | 10080
98 | 57 | Labour for Fixing of all types of clamps | ELEC | labour | SWR10917 | 65 | EA | 3705
99 | 584 | Laying of earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication 75x 8mm MS Flat / GI Flat. Laying of earth mat,excavation 75x 8mm | ELEC | labour | SWR10920 | 65 | RMT | 37960
100 | 1010 | Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) Earthing for raisers of SS Flat 50x6 mm. | ELEC | labour | SWR10919 | 41 | RMT | 41410
101 | 36 | Supply of earthing pipe with materials -Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | ELEC | supply | SMR11482 | 3486 | EA | 125496
102 | 36 | Providing of Earthing-Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | ELEC | labour | SWR10357 | 1234.2 | EA | 44431.2
103 | 36 | Providing of RCC collar to earth pit-Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINES-Providing of RCC collar | ELEC | labour | SWR10359 | 386 | EA | 13896
104 | 2 | Supply of Copper Flexible jumper with 75 X 8 of length 250 mm at neutral of Power tranformer end and 50 X 6 of length 50mm two Nos at double neutral end duly brasing with flexible jumper of capacity of 5kA/3 sec for power transformer neutral. SupCU Flexi jumper for Power T/F Neutral | ELEC | supply | SMR40033 | 4725 | EA | 9450
105 | 2 | Providing of earthing with various types of earth electrodes-Providing of double earthing for neutral with flexible copper jumpers including arrangement by fixing M.S.Channel 100x50mm. | ELEC | labour | SWR11892 | 1323 | EA | 2646
106 | 80 | Providing of control cable trench as per DATA-XII | ELEC | labour | SWR22093 | 3148 | RMT | 251840
107 | 3074 | Control Cable-Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends . Lay-4C/10C 2.5Sqmm Control Cable | ELEC | labour | SWR11879 | 27 | M | 82998
108 | 270 | Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per specification (including cost of ferrules, lugs and glands) | ELEC | labour | SWR12510 | 27 | EA | 7290
109 | 4 | Marshalling Box Supply of FRP PT Marshalling Box | ELEC | supply | SMR40048 | 4463 | EA | 17852
110 | 4 | Marshalling Box Erection of Marshalling boxes | ELEC | labour | SWR10940 | 374.85 | EA | 1499.4
111 | 1 | Loading of 220 V Batterry with charger | ELEC | labour | SWR11166 | 1612 | SET | 1612
112 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
113 | 1 | Un loading of 220 V Batterry with charger | ELEC | labour | SWR11147 | 1024 | SET | 1024
114 | 1 | Batteries-Erection of 220 V, 200 AH battery in complete shape fit for charging . Conventional lead acid | ELEC | labour | SWR12350 | 7666 | EA | 7666
115 | 1 | Control Panels -Supply of DC Annunciation & relay panel for 10 feeder panel including the cost of LED Indiacation lamps, VAA auxilairy relays, Electronic Hooters complete as per specification. | ELEC | supply | SMR40044 | 42500 | EA | 42500
116 | 1 | Control Panels -Supply of AC Supply panel inluding providing of changeover switch, SFU, metering unit, 32 A three phase MCB, 16 A Single phase MCB complete as per specification. Supply of AC Supply panel complete | ELEC | supply | SMR40045 | 42000 | EA | 42000
117 | 2 | Fixing of AC/DC Panel and giving Connections to the protection equipment and Metering circuits as per the specification and standards. The 3 1/2 core 25 Sqmm power cable required from distribution box to AC/DC panel in the control room is also to be supply | ELEC | labour | SWR20025 | 7871.85 | SET | 15743.7
118 | 8 | Yard lightning-Supply of stepped tubular poles single way made of steel of length 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9 mm, 2.1 mtrs with outer dia 76.1 mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79 kgf as per IS 2713 | ELEC | supply | SMR40051 | 13913 | EA | 111304
119 | 8 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE/CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA /OSRAM /SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty S-90W LED fixture set | ELEC | labour | SMR11594 | 8200 | EA | 65600
120 | 8 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | ELEC | labour | SWR11039 | 928 | EA | 7424
121 | 8 | Erection of tubular poles | ELEC | labour | SWR10955 | 1379 | EA | 11032
122 | 5.27 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 34671.33
123 | 8 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE/CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA /OSRAM /SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty. Fixing of Metal halide lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5 GI pipe complete Fixing of LED/Metal halide complete. | ELEC | labour | SWR10956 | 1268 | EA | 10144
124 | 45 | Supply of HBG metal-Supply & spreading of 20mm machine crushed metal (HBG) including cost of conveneyance of all materials, labour charges etc complete for finished item of work and directed by the engineer incharge | ELEC | labour | SWR10860 | 2113 | M3 | 95085
125 | 2 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M Ex of Hard pit w/o blast 0.75X0.9X1.95M | ELEC | labour | SWR11040 | 990.68 | EA | 1981.36
126 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELEC | Supply | SMR40009 | 2181 | TO | 1635.75
127 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELEC | labour | SWR10877 | 851 | TO | 638.25
128 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELEC | Supply | SMR40010 | 1293 | TO | 969.75
129 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELEC | labour | SWR10879 | 482 | TO | 361.5
130 | 1 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Box pole 12 Mtr | ELEC | labour | SWR11267 | 3901.37 | EA | 3901.37
131 | 2.22 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 14605.38
132 | 1.16 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ELEC | labour | SWR10862 | 373 | M2 | 432.68
133 | 2 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | ELEC | labour | SWR11089 | 48 | EA | 96
134 | 1 | Construction of DTR Plinth-RCC Column type DTR Plinth of size 1'X1'X10',topslab 4'x4'x6" & beam size 4'X8'X8" upto 160KVA | ELEC | labour | SWR21843 | 25967.57 | EA | 25967.57
135 | 1 | Loading of 50,63, 75 & 100 KVA DTR | ELEC | labour | SWR10195 | 350 | EA | 350
136 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
137 | 1 | Un loading of 50,63, 75 & 100 KVA DTR | ELEC | labour | SWR10513 | 280 | EA | 280
138 | 1 | Erection of DTR's including loading and Unloading DTR on the Structure/Plinth etc-Erection of 3 Phase DTRs 63,75 & 100 KVA | ELEC | labour | SWR20905 | 1650 | EA | 1650
139 | 1 | Erection of AB Switch and aligment complete Erection of 11KV 200A TT type AB Switch including fixing of cross angles and alignment complete | ELEC | labour | SWR20102 | 1813.49 | EA | 1813.49
140 | 1 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erect. of 11kv HG Fuseset incl earthing | ELEC | labour | SWR10395 | 740.52 | SET | 740.52
141 | 40 | Excavation & laying of UG Cable in Single Run Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.-In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road-11KV 3x185 Sqmm Cable | ELEC | labour | SWR11920 | 465.46 | M | 18618.4
142 | 20 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-11 KV 3x185 Sqmm Cable | ELEC | labour | SWR11956 | 126.23 | M | 2524.6
143 | 2 | Making of Outdoor/Indoor End Termination Making 11 KV 3x185 Sqmm Cable Out Door/Indoor end termination | ELEC | labour | SWR10390 | 2370.63 | EA | 4741.26
144 | 1 | Erection of LT distribution box including laying of LT cable from distribution box to LT OH line and DTR to distribution box including earthing of distribution box and crimping of lugs connecting of jumpers etc | ELEC | labour | SWR10674 | 1594.67 | EA | 1594.67
145 | 85 | LAYING OF 33KV, 11KV UG CABLE Excavation & laying of UG Cable in Single Run Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road-LT 3 1/2 x 185 Sqmm Cable | ELEC | labour | SWR11923 | 377.63 | M | 32098.55
146 | 15 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-LT 3 1/2 x 185 Sqmm Cable | ELEC | labour | SWR11959 | 85.43 | M | 1281.45
147 | 2 | UG Cables Joints :-Making of Outdoor/Indoor End Termination -Supply & fixing of Oout Door/Indoor end termination LT 3 1/2 x 185 Sqmm Cable | ELEC | labour | SWR10765 | 968.9 | EA | 1937.8
148 | 1 | Supply and fixing of Substation board of size 3'x2.5' indicating the layout of switchyard Sup &fix of board ind Switchyard layout | ELEC | labour | SWR20032 | 1654 | EA | 1654
149 | 1 | Supply and fixing of safety instructions/Substation operation instruction board. Sup& fix safety inst/SS Op. inst board | ELEC | labour | SWR22090 | 2205 | EA | 2205
150 | 750 | Control Panels Supplying & fabrication erection of 6mm Checkerd plates as per the field conditions Supply,fabricati of 6mm Checkerd plates | ELEC | Labour | SWR10873 | 83 | KG | 62250
151 | 1 | T & P Supply of Wall clock standard make | ELEC | Supply | SMR40059 | 578 | EA | 578
152 | 1 | S-10ft Aluminium Ladder | ELEC | Supply | SMR12378 | 1654 | EA | 1654
153 | 1 | Sup Alluminium Ladder for indoor works | ELEC | Supply | SMR40062 | 4410 | EA | 4410
154 | 30 | T & P Painting of Name Plates for any equipmen | ELEC | labour | SWR10963 | 122 | EA | 3660
155 | 1 | T & P Supply of Taparia Tool kit of Size 20”x10”x15” with tier arrangements Tool box with locking arrangement & key containing (1) Double Ended fix Spanner sets, (Ribbed) 6 x 7, 8 x 9, 10 x 11, 12 x 13, 14 x 15, 16 x 17, 18 x19, 20 x 22, 21 x 23, 24 x 27, 25 x28, 30 x 32, (2) Double Ended Ring Spanners sets, 6 x 7 , 8 x 9, 10 x 11, 12 x 13, 14 x 15. 16 x 17 , 18 x 19, 20 x 22 , 21 x 23, 24 x 27, 25 x28, 30 x 32 mm, (3) Adjustable Spanner 305 mm length least maximum opening 35mm chrome, (4) Pipe Wrench Length 350 mm 14”, (5) Soft faced Hammer with suitable handle 2 lb, (6) Hacksaw frame with metal handle heavy duty for 12" hacksaw blade with High Speed blade, (7) Insulated Screw drivers Transparent Green Handle Set Length 6”, 8” & 12”, (8) Star Screw Driver Transparent Green Handle Length 6”, (9) Insulated Wire Cutter, (10) Insulated Cutting Plier Length 8” with cable stripper insulated with thick C. A. sleeve confirming to IS: 4378 - 1990, (11) Long Nose Plier insulated with thick C.A. sleeve generally confirming to IS:3552-1989, (12) Tester type screw driver (special with neon bulb) generally confirm to IS: 5579- 1985 Grade:II handle yellow/ green colour overall length 130 mm, (13) Insulated Crimping Plier of all Taparia make. SupTaparia Tool kit complete as per Spec | ELEC | Supply | SMR40063 | 4925 | SET | 4925
156 | 1 | T & P Sup Rechargeable LED torch light of Standard make | ELEC | Supply | SMR40064 | 1733 | EA | 1733
157 | 1 | T & P-Steel almarah(61/2 X 3ft) Godrej | ELEC | Supply | SMR40061 | 9818 | EA | 9818
158 | 1 | T & P-Table (3x6ft) Godrej | ELEC | Supply | SMR40057 | 6050 | EA | 6050
159 | 4 | T & P-S type chairs (Godrej) | ELEC | Supply | SMR40058 | 924 | EA | 3696
160 | 1 | T & P Sup Angle racks(18x36.6inches) Godrej | ELEC | Supply | SMR40060 | 1733 | EA | 1733
161 | 1 | T & P Supply of Hack saw (12 inches) | ELEC | Supply | SMR40065 | 289 | EA | 289
162 | 4 | Sup Earth Rods (8ft) Screw & clamp type | ELEC | Supply | SMR40066 | 578 | EA | 2312
163 | 2 | Supply of Hand Gloves | ELEC | Supply | SMR40067 | 289 | SET | 578
164 | 12 | SupRubber mats( 6'x3')size fo indoorSS | ELEC | Supply | SMR40068 | 1386 | EA | 16632
165 | 1 | Biometric Time attendence System & Telecom Sup Stand basic cell phone with charger | ELEC | Supply | SMR40069 | 1386 | EA | 1386
166 | 14 | Supply of Danger boards with clamps | ELEC | Supply | SMR40070 | 116 | EA | 1624
167 | 2 | Supply of Materials -Fire bucket stand with 3 buckets (8 -10 ltr capacity) | ELEC | Supply | SMR40088 | 1386 | SET | 2772
168 | 2 | Room fire extinguisher (2 ltrs capacity) for control room | ELEC | Supply | SMR40089 | 4620 | EA | 9240
169 | 4 | Sup TrollyMounted Co2 (6.5Kgs) Cylinders(IS-2878) | ELEC | Supply | SMR40087 | 9240 | EA | 36960
170 | 6 | Supply of Safety Helmet of standard make | ELEC | Supply | SMR40071 | 231 | EA | 1386
171 | 8 | Supply of LC Boards | ELEC | Supply | SMR40072 | 116 | EA | 928
172 | 4 | Supply of Gum Boots(Pairs) | ELEC | Supply | SMR40073 | 693 | EA | 2772
173 | 1 | Supply of 5000v megger | ELEC | Supply | SMR40074 | 13860 | EA | 13860
174 | 1 | Supply of Earth megger (1000v) | ELEC | Supply | SMR40075 | 8085 | EA | 8085
175 | 1 | Supply of Digital clamp meter. | ELEC | Supply | SMR40076 | 2888 | EA | 2888
176 | 1 | Name board of the 33/11kV Sub-Station(As per Standard Specification) Sup 33/11kv S.S Permanent name board | ELEC | Supply | SMR40086 | 10238 | EA | 10238
177 | 800 | Supply of Hot dip galvanized/zinc coated bolts & nuts including spring washers, pack washers and flat washers etc. | ELEC | Supply | SMR12488 | 90 | KG | 72000
178 | 2 | Fabrication of poles-Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | ELEC | labour | SWR10642 | 512.55 | EA | 1025.1
179 | 1 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-RS Joists 150x75/175 x 85 mm | ELEC | labour | SWR10346 | 1934 | EA | 1934
180 | 5760 | S-Supply of RS Joist Grider Pole (150x150mm) | ELEC | Supply | SMR12302 | 59.25 | KG | 341280
181 | 1000 | S-Supply of RS Joist Pole (175x85mm) | ELEC | Supply | SMR12303 | 60.75 | KG | 60750
182 | 5063 | S- Supply of MS Channel 100x50mm | ELEC | Supply | SMR22745 | 57.45 | KGS | 290869.35
183 | 13 | S-Supply of 33KV 800A DB Break AB Switch | ELEC | Supply | SMR12315 | 40658.78 | EA | 528564.14
184 | 8680 | S-Supply of RS Joist Grider Pole (150x150mm) | ELEC | Supply | SMR12302 | 59.25 | KG | 514290
185 | 4642 | S- Supply of MS Channel 100x50mm | ELEC | Supply | SMR22745 | 57.45 | KGS | 266682.9
186 | 17 | S-Supply of 11KV 800A DB Break AB Switch | ELEC | Supply | SMR12316 | 30847.46 | EA | 524406.82
187 | 3 | S-Supply of 11KV 400A DB Break AB Switch | ELEC | Supply | SMR12317 | 18150 | EA | 54450
188 | 3045 | S-Supply of MS Flat 75x8mm | ELEC | Supply | SMR12321 | 56.42 | KG | 171798.9
189 | 2666 | S-Supply of MS Flat 50x6mm | ELEC | Supply | SMR12322 | 56.5 | KG | 150629
190 | 750 | S-Supply of RS Joist Pole (175x85mm) | ELEC | Supply | SMR12303 | 60.75 | KG | 45562.5
191 | 1 | S-Supply of 11KV 200A Tilting Type AB Switch | ELEC | Supply | SMR12318 | 8991 | EA | 8991
192 | 1 | S-Supply of 11KV HG FuseSet for StationTransformer | ELEC | Supply | SMR12324 | 1974 | EA | 1974
193 | 1 | S-Supply of LT Distribution Box (SMC) | ELEC | Supply | SMR25200 | 7797 | EA | 7797
194 | 2 | S-Supply of 11KV 3x185 Heat Shble O/d End Term Kit | ELEC | Supply | SMR25201 | 1182.97 | EA | 2365.94
195 | 40 | S-Supply of LT XLPE Cable 1C 150 sqmm | ELEC | Supply | SMR25203 | 114.83 | M | 4593.2
196 | 100 | S-Supply of LT XLPE Cable 3 1/2 C 185 sqmm | ELEC | Supply | SMR25204 | 547 | M | 54700
197 | 4 | Loading of LT AB Cable 3X16+25 Sqmm | ELEC | labour | SWR11702 | 200 |  | 800
198 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 |  | 3299.7
199 | 4 | Un loading of LT AB Cable 3X16+25 Sqmm | ELEC | labour | SWR11713 | 204 |  | 816
200 | 5 | survey line&cabl inc peg mark&tree clear | ELEC | labour | SWR22092 | 765 | KM | 3825
201 | 60 | S-Supply of M+3 Tower GAV | ELEC | SUPPLY | smr11683 | 140674.3 | EA | 8440458
202 | 60 | Erection of M+3Tower GALV | ELEC | supply | SMR11684 | 28520.64 | EA | 1711238.4
203 | 60 | Erection of M+3 Tower (Galvanized) | ELEC | labour | SWR11850 | 64576 | EA | 3874560
204 | 60 | Erection of Extension of 3Mtrs for M+3 (Galvanized) | ELEC | labour | SWR11851 | 5168.95 | EA | 310137
205 | 285.12 | Earth work excavation of pits in hard murram/rock boul | ELEC | labour | SWR20959 | 1530 | M3 | 436233.6
206 | 8 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-12Mtrs/Spun Pole 0.92 M x 0.92M x 2.3M (3.0" x 3.0" x 7.6") | ELEC | labour | SWR11041 | 1466.25 | EA | 11730
207 | 8 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Box pole 12 Mtr | ELEC | labour | SWR11267 | 3901.37 | EA | 31210.96
208 | 16 | Fabrication of poles-Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | ELEC | labour | SWR10642 | 512.55 | EA | 8200.8
209 | 16 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | ELEC | labour | SWR10640 | 1132 | EA | 18112
210 | 13.84 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 91053.36
211 | 0.248 | Mass Concreting for pole-Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | ELEC | labour | SWR11890 | 3893 | M3 | 965.464
212 | 50 | Formation of Cut points-Formation of Cut point for 33 KV Double circuit line excluding pole erection and stays | ELEC | labour | SWR10466 | 3198.72 | EA | 159936
213 | 5 | Paving out and stringing of conductor by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location-100 Sqmm Single Circuit (3 Conductors) | ELEC | labour | SWR10366 | 13856.7 | KM | 69283.5
214 | 150 | Loading of 33 KV Pin insulators | ELEC | labour | SWR10211 | 3 | CRT | 450
215 | 150 | Un loading of 33 KV Pin insulators | ELEC | labour | SWR10529 | 3 | CRT | 450
216 | 2 | Loading of 33 KV Metal parts | ELEC | labour | SWR10618 | 65 | BAG | 130
217 | 4 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 20 Km and upto 30 Km with Lorry for each trip | ELEC | labour | SWR11862 | 3691.38 | EA | 14765.52
218 | 200 | Supply of earthing pipe with materials S-GI Bolts & Nuts,Washers etc., | ELEC | supply | SMR11488 | 117.5 | KG | 23500
219 | 4 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 20 Km and upto 30 Km with Lorry for each trip | ELEC | labour | SWR11862 | 3691.38 | EA | 14765.52
220 | 1 | Load-11/33KV XLPE UG Cable for all sizes | ELEC | labour | SWR11230 | 1024 | DR | 1024
221 | 1 | Unload-11/33KV XLPE UG Cable for all sizes | ELEC | labour | SWR11231 | 1024 | DR | 1024
222 | 450 | Excavation & laying of UG Cable in Single Run-Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs-In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road-33 KV 3x400 Sqmm Cable | ELEC | labour | SWR11918 | 572.1 | M | 257445
223 | 50 | Excavation & laying of UG Cable in Single Run-Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs-Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-33 KV 3x400 Sqmm Cable | ELEC | labour | SWR11954 | 135.66 | M | 6783
224 | 12 | Making of Outdoor/Indoor End Making 33 KV 3x400 Sqmm Cable Out Door/Indoor end termination TerminationOD/Idoor end termination 33kv 3x400 xlpe | ELEC | labour | SWR10387 | 2764.76 | EA | 33177.12
225 | 2 | UG Cables Joints 33 KV 3x400 Sqmm Cable Straight through joint 33kv 3x400 xlpe | ELEC | labour | SWR10382 | 5700.78 | EA | 11401.56
226 | 3 | Erection of AB Switch and aligment complete Erection of 33 KV AB Switch including alignment and earthing | ELEC | labour | SWR10392 | 4500 | EA | 13500
227 | 3 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | ELEC | labour | SWR10881 | 142 | EA | 426
228 | 2 | S&E-Smart RFID marker | ELEC | labour | SWR25089 | 2745 | EA | 5490
229 | 2 | Cost of Pipes and slabs-Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters , CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | ELEC | supply | SMR40085 | 484 | EA | 968
230 | 1500 | Supply of Materials -- Supply of MS Channel 100X50mm | ELEC | supply | SMR22745 | 57.45 | KGS | 86175
231 | 500 | Supply of Materials -- Supply of MS Flat 75x8 mm | ELEC | supply | SMR12321 | 56.42 | KG | 28210
232 | 12 | UG Cables Joints : Making of Outdoor/Indoor End Termination -- Supply 33KV 3x400Sqmm Outdoor | ELEC | supply | SMR22222 | 4554 | EA | 54648
233 | 2 | UG Cables Joints : Making of Straight through joints -- Supply of 33KV 3x400SQmm Straight Through Joint Kit | ELEC | supply | SMR22223 | 24151 | EA | 48302
234 | 3 | Supply of Materials -- Supply of 33 kV 800 A Double break AB switch | ELEC | supply | SMR12315 | 40658.78 | EA | 121976.34
235 | 4000 | Supply of Materials -- supply of RS Joist Poles (175X85mm) | ELEC | supply | SMR12303 | 60.75 | KG | 243000
236 | 200 | Supply of Materials -- Supply of MS Flat 50x6 mm | ELEC | supply | SMR12322 | 56.5 | KG | 11300
237 | 5 | UNLOADING of Conductor drums | ELEC | labour | SWR10509 | 100 | EA | 500
238 | 5 | LOADING of Conductor drums | ELEC | labour | SWR10191 | 202 | EA | 1010
239 | 2 | Un loading of 33 KV Metal parts | ELEC | labour | SWR10632 | 65 | BAG | 130
240 | 145 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M Ex of Hard pit w/o blast 0.75X0.9X1.95M | ELEC | labour | SWR11040 | 990.68 | EA | 143648.6
241 | 145 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Errection of 11 M long PSCC pole | ELEC | labour | SWR10978 | 4336.85 | EA | 628843.25
242 | 290 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | ELEC | Labour | SWR11039 | 928 | EA | 269120
243 | 290 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-9.1 M long PSCC pole | ELEC | labour | SWR10343 | 2400 | EA | 696000
244 | 79.112 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 520477.848
245 | 10 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-12Mtrs/Spun Pole 0.92 M x 0.92M x 2.3M (3.0" x 3.0" x 7.6") | ELEC | labour | SWR11041 | 1466.25 | EA | 14662.5
246 | 10 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Box pole 12 Mtr | ELEC | labour | SWR11267 | 3901.37 | EA | 39013.7
247 | 20 | Fabrication of poles-Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | ELEC | labour | SWR10642 | 512.55 | EA | 10251
248 | 20 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | ELEC | labour | SWR10640 | 1132 | EA | 22640
249 | 17.3 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 113816.7
250 | 0.31 | Mass Concreting for pole-Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | ELEC | labour | SWR11890 | 3893 | M3 | 1206.83
251 | 70 | Formation of Cut points - Formation of Cut point for 11 KV Single Circuit line excluding pole erection and stays Formatn of Horiz Cut point for 11KV line | ELEC | labour | SWR10653 | 1435.81 | EA | 100506.7
252 | 7.1 | Fabrication & erection of Channels -Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to theRS-Joist poles excluding cost of Mild Steel and transportcharges to substation site, including erection. Fabrication of struc.with welding. | ELEC | labour | SWR10869 | 3426 | TO | 24324.6
253 | 8 | Paving out and stringing of conductor by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location-100 Sqmm Single Circuit (3 Conductors) | ELEC | labour | SWR10366 | 13856.7 | KM | 110853.6
254 | 1850 | Excavation & laying of UG Cable in Single Run-Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs-In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road-11 KV 3x300 Sqmm Cable | ELEC | labour | SWR11919 | 465.46 | M | 861101
255 | 150 | Excavation & laying of UG Cable in Single Run-Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs-Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe-11 KV 3x300 Sqmm Cable | ELEC | labour | SWR11955 | 144.08 | M | 21612
256 | 8 | Making of Outdoor/Indoor End Termination-Making 11 KV 3x300 Sqmm Cable Out Door/Indoor end termination | ELEC | labour. | SWR10391 | 2370.63 | EA | 18965.04
257 | 4 | UG Cables Joints Making of Straight through joints-11 KV 3x300 Sqmm Cable | ELEC | labour. | SWR10386 | 3725.45 | EA | 14901.8
258 | 11 | Stringing of HT AB Cable with GI Metal Parts-HT AB Cable 11 KV 3x185+70 Sqmm | ELEC | labour | SWR10454 | 41876.1 | KM | 460637.1
259 | 10 | Straight through joints of AB cable (each lead)-120 Sqmm to 185 Sqmm | ELEC | labour | SWR10669 | 920 | EA | 9200
260 | 290 | Straight through joints of AB cable (each lead)-Supply and ere Straight line Asmbly kits | ELEC | labour | SWR10672 | 1661 | EA | 481690
261 | 70 | Straight through joints of AB cable (each lead)-Supply and ere Angle line Asmbly kits | ELEC | labour | SWR10673 | 2124 | EA | 148680
262 | 66 | End Termination of AB cable (each lead):-Supply of 11KV 3x185+70sq.mm/ 3x70+70sq.mm/3x35+35sq.mm AB cable end Kits | ELEC | labour | SMR11504 | 950 | SET | 62700
263 | 66 | End Termination of AB cable (each lead):-120 Sqmm to 185 Sqmm | ELEC | labour | SWR10667 | 800 | EA | 52800
264 | 22 | T Branch Kit-Supply and erection of T-Branch kit | ELEC | labour | SWR24971 | 3215 | EA | 70730
265 | 22 | T Branch KitErection of Assemble Kit for 'T' Branche | ELEC | supply | SWR10671 | 1800 | EA | 39600
266 | 290 | Supply and Erection of I Hook and Suspension Hook-Supply of I hook | ELEC | supply | SMR12099 | 158 | EA | 45820
267 | 290 | Supply and Erection of I Hook and Suspension Hook-Erection of I hook | ELEC | labour | SWR12099 | 55 | EA | 15950
268 | 198 | Supply of 120 Sqmm Aluminium lugs | ELEC | supply | SMR40132 | 12.52 | EA | 2478.96
269 | 10 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | ELEC | labour | SWR10393 | 3200 | EA | 32000
270 | 10 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | ELEC | labour | SWR10881 | 142 | EA | 1420
271 | 100 | Supply of earthing pipe with materials-Supply of GI Flat 25X3 mm | ELEC | supply | SMR11485 | 105 | KG | 10500
272 | 22 | Un loading of 11 KV AB Cable (XLPE) 3 Core upto 500 Mts. Drum (including Accessories ) | ELEC | labour | SWR12431 | 438 | DR | 9636
273 | 22 | Loading of 11 KV AB Cable (XLPE) 3 Core upto 500 Mts. Drum (including Accessories ) | ELEC | labour | SWR12413 | 584 | DR | 12848
274 | 480 | Loading of 11KV pin insulators/Post type insulators/ Solid core insulators | ELEC | labour | SWR10212 | 1 | CRT | 480
275 | 480 | Un loading of 33 & 11 KV Disc insulators | ELEC | labour | SWR10631 | 2 | CRT | 960
276 | 28 | Loading of 11 KV Metal parts | ELEC | labour | SWR12402 | 48 | BAG | 1344
277 | 28 | Un loading of 11 KV Metal parts | ELEC | labour | SWR12421 | 48 | BAG | 1344
278 | 13 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 20 Km and upto 30 Km with Lorry for each trip | ELEC | labour | SWR11862 | 3691.38 | EA | 47987.94
279 | 20 | Supply of earthing pipe with materials-Supply of CI eath pipe with 50mm dia,2.0 M Length | ELEC | supply | SMR11484 | 2441 | EA | 48820
280 | 20 | Providing of RCC collar to earth pit-Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINES-Providing of RCC collar | ELEC | labour | SWR10359 | 386 | EA | 7720
281 | 20 | Providing of Earthing-Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | ELEC | labour | SWR10357 | 1234.2 | EA | 24684
282 | 300 | Supply of earthing pipe with materials-Supply of GI Flat 25X3 mm | ELEC | supply | SMR11485 | 105 | KG | 31500
283 | 30 | Supply of Danger boards with clamps | ELEC | supply | SMR40070 | 116 | EA | 3480
284 | 4 | Load-11/33KV XLPE UG Cable for all sizes | ELEC | labour | SWR11230 | 1024 | DR | 4096
285 | 4 | Unload-11/33KV XLPE UG Cable for all sizes | ELEC | labour | SWR11231 | 1024 | DR | 4096
286 | 4 | S&E-Smart RFID marker | ELEC | labour | SWR25089 | 2745 | EA | 10980
287 | 4 | Cost of Pipes and slabs-Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters , CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | ELEC | supply | SMR40085 | 484 | EA | 1936
288 | 145 | Supply of PSCC Pole 11Mtr 365KG | ELEC | supply | SMR25236 | 5399 | EA | 782855
289 | 290 | Supply of PSCC Pole 9.1Mtr 280KG | ELEC | supply | SMR25233 | 3109.41 | EA | 901728.9
290 | 10 | Supply of Materials -- Supply of 11 kV 400 A Double break AB switch | ELEC | supply | SMR12317 | 18150 | EA | 181500
291 | 5000 | Supply of Materials -- supply of RS Joist Poles (175X85mm) | ELEC | supply | SMR12303 | 60.75 | KG | 303750
292 | 1500 | Supply of Materials -- Supply of MS Flat 50x6 mm | ELEC | supply | SMR12322 | 56.5 | KG | 84750
293 | 1800 | Supply of MS Angle 50x50x6 | ELEC | supply | SMR25206 | 58.15 | KG | 104670
294 | 2800 | Supply of MS Channel 75x40 mm | ELEC | supply | SMR25205 | 58.45 | KG | 163660
295 | 8 | Supply of 11KV 3x300 Heat Shble O/d End Term Kit | ELEC | supply | SMR25208 | 1372.88 | EA | 10983.04
296 | 4 | Supply of 11KV 3x300 Heat Shble stright through joint Kit | ELEC | supply | SMR25210 | 4110.17 | EA | 16440.68
297 | 1000 | Supply of Materials -- Supply of MS Channel 100X50mm | ELEC | supply | SMR22745 | 57.45 | KGS | 57450
298 | 5 | LOADING of Conductor drums | ELEC | labour | SWR10191 | 202 | EA | 1010
299 | 5 | UNLOADING of Conductor drums | ELEC | labour | SWR10509 | 100 | EA | 500
Sub Total: | [7 empty] | 30618482.447
18% Service tax on labour: | [7 empty] | 5511326.8405
Total Rs. | [7 empty] | 36129809.2875
Civil labour-WBS. No. S-1785-13-07-01-01-001
Sl.No. | Estimate Quantity (only Figures) | Item Detailed Specification Description | Work Type eg. Earth Work, Electrical works. etc (upto 200 Characters) | Item Short Description (upto 100 Characters) | APSS / Morth Cl. Number (upto 200 Characters) | Rate (INR) (Upto 2 Decimals ) | UOM (upto 50 Characters) | Amount
1 | 32 | Leveliing the site by cutting and levelling with the help of JCB including cost,conveyance of all materials,hire chareges etc complete for finished item of work as directed by Engineer-in-charge. | Civil | Labour | SWR34179 | 2165 | Hrs | 69280
2 | 149.95 | Earth Work Mass Excavation (hard rock) to a depth as directed, in soils such as hard rock requiring blasting in prohibited area and all conditions such as dry, wet, slurry etc.and in dense or hard soils, disposal and depositing of excavated soil with intial lead of 10 mt and intial lift of 2m or as directed, including cost and conveyance of all materials, ramping and lifting of materials, and labour charges, hire charges of machinery, tools & plants, bailing of water ( either sub soil water, stoMts water, rain water, surface water or of any kind) if any at any stage of work until all works below ground level is finished to the satisfaction ,and from work such as shoring, timbering, strutting with required supports etc. for the work and removal of form work after completion of work etc all complete as directed by the engineer-incharge. | Civil | Labour | SWR33018 | 1440 | cum | 215928
3 | 115.65 | Earth work excavation in all type of ordinary soils red earth, Hard gravelly soils, earth mixed with sand and sandy soils etc., in all conditions such as slushy and dry with initial leads and lifts for foundations. Ordinary Soil | Civil | Labour | SWR33015 | 486 | cum | 56205.9
4 | 22.79 | PCC (1:4:8) using 40 mm metal with concrete Mixture. All work upto Plinth level including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete as directed by Engineer incharge of the work | Civil | Labour | SWR33028 | 4771 | cum | 108731.09
5 | 108.3 | Coursed Rubble stone CRS masonry 2nd sort with hard granite stones in cement mortar CM (1:6) for basement, including cost and conveyance of all materials, labour charges, curing, all leads and lifts, etc, complete for finished item of work. | Civil | Labour | SWR33041 | 4892 | cum | 529803.6
6 |  | RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge
7 | 1.09 | RCC M20 Grade Footing 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33098 | 9523 | cum | 10380.07
8 | 1.58 | RCC M20 Grade Column 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33100 | 13272 | cum | 20969.76
9 | 1.15 | RCC M20 Grade plinth beam 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33099 | 12394 | cum | 14253.1
10 | 0.46 | Reinforcement steel Supplying, Cutting, bending, binding, placing in position and tying reinforcement steel in all heights including cost and conveyance of steel and binding wire etc,. With all leads and lifts, labour charges, etc., complete for finished item of work. | Civil | Labour | SWR33144 | 70687 | MT | 32516.02
11 | 66.71 | Brick masonry in CM (1:6) for superstructure using well burnt country made second class bricks of approved quality including cost and conveyance of all materials curing, scaffolding with all leads and lifts in all heights etc., complete for finished item of work | Civil | Labour | SWR33068 | 8285 | cum | 552692.35
12 | 6.98 | PCC (1:2:4) using 20mm size well graded HBG metal for foundations, including cost, conveyance of all materials,labour all leads and lifts,consolidation and all operations, formwork as required, curing,etc. complete for finished item of work | Civil | Labour | SWR33030 | 6140 | cum | 42857.2
13 | 630.95 | Plastering with CM 2 coats, 20 mm thick, base coat in CM (1:6), 16 mm thick and top coat in CM (1:4), 4mm thick with Dubara sponze finishing including cost of all materials, seigniorage charges, excluding conveyance charges of materials and including all operational, incidental and labour charges for mixing mortar, laying rendering smooth and thread lining, curing, rounding off junctions of wall and slab etc., complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33163 | 564 | Sqm | 355855.8
14 | 27 | Painting with two coats of Plastic Emulsn paint over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33356 | 210 | Sqm | 5670
15 | 781.85 | Painting with two coats of Surya Cem paint over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33329 | 85 | Sqm | 66457.25
16 | 380 | Supplying and fixing Structural Steel angles channal etc.Manufacturing, Supplying and fixing of MS grill for (Gate and raillings) of approved design as per drawings, including cost and conveyance of all materials, labour charges etc.,complete for finished item of work as directed by the Engineer- in-charge. | Civil | Labour | SWR33145 | 128 | kgs | 48640
17 | 3 | Supply and Fixng of MS Name Board including cost & conveyance of all materials,labour charges etc complete for finished item of work. | Civil | Labour | SWR33421 | 4326 | sqm | 12978
18 | 1 | Geophysical Investgation charges for water point by Geologist | Civil | Labour | SWR33608 | 5000 | EA | 5000
19 |  | Drilling of 165mm bore well with machine rig including deployment and hire charges of rig and other machinery and equipment labour charges , measuring the yeild of borewell including cost and conveyance etc complete
20 | 90 | Drill-165mm Bore Well 0 to 90 | Civil | Labour | SWR33609 | 336 | M | 30240
21 | 30 | Drill-165mm Bore Well 90M to 120M | Civil | Labour | SWR34830 | 369 | M | 11070
22 | 30 | Drill-165mm Bore Well 120M to 150M | Civil | Labour | SWR34831 | 394 | M | 11820
23 | 30 | Drill-165mm Bore Well 150M to 180M | Civil | Labour | SWR34832 | 492 | M | 14760
24 | 30 | Drill-165mm Bore Well 180M to 210M | Civil | Labour | SWR34833 | 623 | M | 18690
25 | 30 | Drill-165mm Bore Well 210M to 240M | Civil | Labour | SWR34834 | 754 | M | 22620
26 | 30 | Drill-165mm Bore Well 240M to 270M | Civil | Labour | SWR34835 | 918 | M | 27540
27 | 80 | Drill-165mm Bore Well 270M and above | Civil | Labour | SWR34836 | 1082 | M | 86560
28 | 40 | Supply and fixing of 160mm dia PVC casing of A class 6Kg point pressure including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR33611 | 883 | M | 35320
29 | 1 | Supply and erecting, ISI mark submersible 5.0 HP, three Phase 30 stages pumpset suitable for 106/156mm dia borewell including cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33640 | 48007 | EA | 48007
30 | 290 | Supply and fixing of HDPE pipe 40mm dia of 16Kg/cm2 including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR34410 | 180 | M | 52200
31 | 1 | Supply and erecting D.O.L Starter 415V ,3 phase,50Hz with SS enclouserincluding cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33645 | 7854 | EA | 7854
32 | 310 | Supply of 3 Core 2.5 Sqmm Flat Copper cable of ISI for Submersible Motors of makes Finolex / Polycab / Gold Medal / Million / Payal / Sun Light / Power Flex / Fortune Art | Civil | Labour | SWR33641 | 192 | M | 59520
33 | 6 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-28.60mm OD Pipe - SDR 11 | Civil | Labour | SWR34363 | 410 | M | 2460
34 | 1 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type - 25mm NB Size | Civil | Labour | SWR34346 | 466 | EA | 466
35 | 64.95 | Earth work excavation in all type of ordinary soils red earth, Hard gravelly soils, earth mixed with sand and sandy soils etc., in all conditions such as slushy and dry with initial leads and lifts for foundations. | Civil | Labour | SWR33015 | 486 | Cum | 31565.7
36 | 13.54 | PCC (1:4:8) using 40mm HBG metal for foundations and leveling course, including cost and conveyance of all materials, labour all leads and lifts, consolidation and all operations, formwork as required, curing, etc. complete for finished item w | Civil | Labour | SWR33028 | 4771 | Cum | 64599.34
37 | 26.08 | CRS Coursed Rubble Stone masonry 2nd sort with hard granite stones in cement mortar (1:6) for basement, including cost and conveyance of all materials, labour charges, curing, all leads and lifts, etc, complete for finished item of work. | Civil | Labour | SWR33041 | 4892 | Cum | 127583.36
38 | 51.88 | Supplying and filling the substation site with borrowed gravel, watering, ramming, thoroughly complying with the standard specification. | Civil | Labour | SWR33052 | 309 | Cum | 16030.92
39 |  | 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge
40 | 3.56 | a) RCC M20 Grade Footings 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33098 | 9523 | Cum | 33901.88
41 | 2.28 | b)RCC M20 Grade Columns 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33100 | 13272 | Cum | 30260.16
42 | 2.25 | c)RCC M20 Grade Plinth Beams 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33099 | 12394 | Cum | 27886.5
43 | 3.17 | D) RCC M20 Grade Roof Beams 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33121 | 12310 | Cum | 39022.7
44 | 0.58 | e) RCC M20 Grade Lintels 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33107 | 13101 | Cum | 7598.58
45 | 2.7 | f) RCC M20 Grade Sunshades 600mm wide and 75mm thick 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33114 | 1378 | Sqm | 3720.6
46 | 15.22 | g) RCC M20 Grade Roof Slab 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33128 | 10898 | Cum | 165867.56
47 | 3 | reinforcement steel Supplying, Cutting, bending, binding, placing in position and tying reinforcement steel in all heights including cost and conveyance of steel and binding wire etc,. With all leads and lifts, labour charges, etc., complete for finished item of work. | Civil | Labour | SWR33144 | 70687 | MT | 212061
48 | 38.36 | Brick masonry in CM (1:6) for superstructure using well burnt country made second class bricks of approved quality including cost and conveyance of all materials curing, scaffolding with all leads and lifts in all heights etc., complete for fin | Civil | Labour | SWR33068 | 8285 | Cum | 317812.6
49 | 517.26 | Plastering with CM 2 coats, 20 mm thick, base coat in CM (1:6), 16 mm thick and top coat in CM (1:4), 4mm thick with Dubara sponze finishing including cost of all materials, seigniorage charges, excluding conveyance charges of materials and including all operational, incidental and labour charges for mixing mortar, laying rendering smooth and thread lining, curing, rounding off junctions of wall and slab etc., complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33163 | 564 | Sqm | 291734.64
50 | 16.56 | Providing Design R.C.M. drop wall of 40mm thickness with cm 1:2 and 6mm dia MS bars at 150mm both ways and chicken mesh in two coats 20mm thick each plastering including cost and conveyance of all materials with leads and lifts, scaffolding and curing, labo | Civil | Labour | SWR33203 | 3109 | Sqm | 51485.04
51 | 12.24 | Supply and fixing of MS ornamental safety grill of approved design including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33310 | 2990 | Sqm | 36597.6
52 | 5.91 | Supply and fixing of doors with the MT Wood frames the door shall be made well seasoned mt wood of cross section 100x75mm. The shutter shall be made isi mark flushed door with decolam sheets pasted on both sides with PVC beading 40mm width all round.Frame shall be painted with two coats of synthetic enamel paint of approved color over one coat of primer over luppum with spary with 3 no 150mm brass hinges 1 no brass door stoper, 1 no 250mm brass aldrops. 2 no 300 mm aluminium tower bolts, 2 no 150mm brass fancy door handlers, 1 no keyless lockset with cp handel. The quoted rate shall include cost and conveyance of the meterials, fixig, labour carges, tools, handles,locking arrangementts and other fixtures & fittings for finished item work as directed by the Engineer - in- charge. | Civil | Labour | SWR33264 | 7314 | Sqm | 43225.74
53 | 20.25 | Raised pointing to the exposed surfaces of CRS masonry in cm 1:3 prop. including cost and conveyance of all materials, labour charges, all leads and lifts curing etc, complete for finished item of work. | Civil | Labour | SWR33184 | 125 | sqm | 2531.25
54 | 8.64 | Supplying and fixing Aluminium sliding windows with grill and fixed glass panels using anodised aluminium extruded sections of mat finish for frames and mullions made from approved aluminium sections 62x32x1.2mm at 0.73kg/Rm providing 5mm plain glass fix | Civil | Labour | SWR33277 | 3623 | sqm | 31302.72
55 | 16.56 | Supply and laying of Ceramic floor over of CM 1:3 20 mm thick including required materials and labour charges etc complete for item of work | Civil | Labour | SWR33224 | 914 | Sqm | 15135.84
56 | 121.92 | Flooring with double machine polished and hand cut Tandur blue stone 20mm thick of approved colour, quality and of minimum of 300x300mm size over a bed of cement mortar 1:3 20mm thick including cost of all materials, with all leads and lifts jointing and | Civil | Labour | SWR33219 | 788 | Sqm | 96072.96
57 | 6.74 | Supply and fixing of 4" high skirting of shabad stone to the walls including cost and conveyance of all materials, labour etc for finished item of work. | Civil | Labour | SWR33236 | 877 | Sqm | 5910.98
58 | 243.69 | Painting with two coats of OBD over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials labour charges etc., complete for finished item of work. | Civil | Labour | SWR33333 | 146 | Sqm | 35578.74
59 | 349.52 | Painting with two coats of Plastic emulsn paint 2 coat of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33356 | 210 | Sqm | 73399.2
60 | 101.17 | Providing impervious coat over RCC roof slab to requried slopes with 20mm thick in CM 1:3 mixed with approved brand of water proffing compound inclding cost and conveyance of all materials, labour charges, curing, rounding off junctions of wall and slab, all leads and lifts, etc . complete for finished item of work as directed by the Engineer - in - charge. | Civil | Labour | SWR33156 | 586 | Sqm | 59285.62
61 | 60 | Supply & fixing of 25mm dia 2mm thick surface P.V.C. pipe (ISI MARK) Concealed in wall with all required accessories including masonary work and labour charges etc.complete. | Civil | Labour | SWR33441 | 108 | M | 6480
62 | 1 | Supply & fixing TPNDB Distribution board with IP-42 protection (Metal Door)suitable for 3 phase ELCB/RCCB/FP Isolator as incomer and 10kA SP MCBs as out going including internal connection and labour charges for surface / flush mounting etc Complete. | Civil | Labour | SWR33526 | 11353 | EA | 11353
63 | 10 | Supply & fixing Flush type of 6A 3 pin wall plug socket with 6A switch control on a common switch board with earth continuity including wire leads,earth connection along with all labour charges etc., complete | Civil | Labour | SWR33468 | 166 | EA | 1660
64 | 6 | Supply & fixing Flush type of 16A 3 pin and 6A 3pin plug Flush type socket with indicator lamp and 16Amps fuse unit and 16Amps switch control (5 in one )duly recessed in wall with wooden deep box of 6'' x 8'' x 2 1/2'' size covered with hylam sheet earth connection and all labour charges etc., complete on wall. | Civil | Labour | SWR33470 | 449 | EA | 2694
65 | 24 | Supply and Fixing of modular switch, LP,FP,EFP,Wiring with 2 runs of 14/0.3mm (1.0 sq.mm)Fire Retardant (FR) P.V.C. insulated flexible copper cable (ISI MARK) in existing pipe with 6A Flush type Switch,ceiling rose and 3mm thick hylam sheet covering to switch control box including all labour charges etc., complete for light points, bell , fan and exhaust fan points in Non-Residential Buildings. | Civil | Labour | SWR33457 | 676 | EA | 16224
66 | 12 | Supply & Fixing of 28W T5 fluorescent tube. | Civil | Labour | SWR33558 | 148 | EA | 1776
67 | 1 | Supply of 12" (300mm)ISI, 900 RPM light duty exhaust fan with metallic blades with Mark of makes Crompton / Bajaj / Havells / Orient. | Civil | Labour | SWR33571 | 2192 | EA | 2192
68 | 180 | Supply and run of 2 of 22/0.3mm (1.5 sq.mm) (FR) P.V.C. insulated flexible copper cable in existing pipe for mains including all labour charges complete. | Civil | Labour | SWR33496 | 75 | M | 13500
69 | 180 | Supply and run of 2 of 36/0.3mm (2.5 sq.mm) FR P.V.C. insulated flexible copper cable in existing pipe for mains including all labour charges complete. | Civil | Labour | SWR33497 | 103 | M | 18540
70 | 12 | Supply & fixing of batten holder /slanting holder in lieu of ceiling rose of light point complete with all connection and all labour charges with 40W bulb (for new installation). | Civil | Labour | SWR33484 | 141 | EA | 1692
71 | 4 | Supply & fixing of 1200mm (48'') sweep 230v,A.C 50 Hz.Ceiling fan with 3 Blades and double ball bearings with all standared accessories. | Civil | Labour | SWR33563 | 2277 | EA | 9108
72 | 4 | Supply & fixing of Electronic Regulator for ceiling fans 900/1200/1400mm sweep including cost of material, Electrical charges complete for finished item of work | Civil | Labour | SWR33564 | 589 | EA | 2356
73 | 1 | Providing independent EARTHING by excavating a trench to a depth of 2.1M in all solid,as per size specified in the Data,using 40mm dia 'B' class GI pipe of 2.5 Mtrs length with necessary accessories with hume pipe ring duly providing staggered holes including filling with equal proportion of salt and Charcoal in layers and all labour charges etc., compiete for small quarters. | Civil | Labour | SWR33596 | 5345 | EA | 5345
74 | 35 | Supplying, laying, jointing and testing 101.6 mm SWG SP-1 pipes of ISI make conforming to ISI 651 & 4127 with airtight cement joints in CM 1.5:1 prop. Including excavation of trenches and socket pits in any soil (except rock requiring blasting) up to 1524 mm(5'0") depth and refilling with watering and tamping. | Civil | Labour | SWR34281 | 755 | M | 26425
75 | 3 | Constructing 904.0 mm (3#0#) dia brick masonry inspection chamber as per IS - 4111: Part-1:1986 with cement mortar (1:6) prop using 2nd Class Clay Bricks of 225 mm thick from approved source having a minimum crushing strength of 5 N/sq.mm including plastering with cement mortar 1:3 prop; ½# thick both inside and outside fitted with 20# dia RCC manhole covers and frames including excavating pits up to a depth of 904 mm (3'-0") in all sorts of soils (excluding rock) and laying cement concrete (1:4:8) 150 mm thick using 40 mm HBG Metal and P.C.C. 1:2:4 benching and channel 100 mm thick as per Standard specification and including cost and conveyance of all materials like cement, sand, bricks, water etc., to site, cost of seigniorage charges on all materials and all incidental and operational, labour charges like mixing cement mortar, constructing masonry, lift charges, curing etc., complete for finished item of work as per Standard specification. | Civil | Labour | SWR34296 | 8766 | EA | 26298
76 | 4 | Supply & fixing of 110 mm dia - Door Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34381 | 128 | EA | 512
77 | 4 | Supply & fixing of 110 mm dia - Plain Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34380 | 100 | EA | 400
78 | 12 | Supply & fixing of 110 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand | Civil | Labour | SWR34377 | 462 | M | 5544
79 | 18 | Supply & fixing of 90 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand | Civil | Labour | SWR34378 | 410 | M | 7380
80 | 3 | Supplying & fixing 150 mm x 100 mm SWG gully traps conforming to ISI 651 & 4127 with C.I Grating & Cost. Brick masonry in CM 1:6 prop. Intermediate chamber and fitted with 304.8 mm x 288.6mm (12"x9") C.I Frame and hinged cover | Civil | Labour | SWR34286 | 767 | EA | 2301
81 | 1 | Supplying and Fixing of European Water Closet of 1st Quality | Civil | Labour | SWR34314 | 2228 | EA | 2228
82 | 6 | Supply & fixing 15 mm angle stop cock Indian make 400 grams Seiko/ Senior/ Nice/ Senior/ Nice or equivalent | Civil | Labour | SWR34328 | 721 | EA | 4326
83 | 4 | S&F 15 mm N.P bib tap Indian make 400 grams full turn Seiko/ Senior/ Nice or equivalent | Civil | Labour | SWR34329 | 296 | EA | 1184
84 | 1 | Supplying & Fixing Indian make Flat Back Wash Hand Basin (HSW/Parryware/ Neycer) 1st quality conforming to IS:2556-Part-4:1972 with waste fittings like rubber plug, chain, 32 mm nominal size C.P. Fitting with parallel pipe thread conforming to IS:2963-1979 and fitted with 15 mm nominal bore Chromium Plated Pillar Tap of 1st quality Indian make 400 grams Seiko/ Senior/ Nice/ Esso or equivalent complete with standard CI brackets including wooden block: 550 x 400 mm - Single C.P. Pillar cock | Civil | Labour | SWR34316 | 1717 | EA | 1717
85 | 2 | Supply & fixing 38.1 mm C.P waste coupling Half or Full Thread 1st Quality Indian make Parryware or equivalent | Civil | Labour | SWR34428 | 309 | EA | 618
86 | 2 | Supply & fixing of 4" (101.6 mm ) Nahany Trap ( Without Jali with inlet)UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34387 | 134 | EA | 268
87 | 1000 | Providing & Placing on Terrace (at all floor levels) polyethylene water storage tank with Double layer approved brand & manufacture with cover and suitable locking arrangement & making necessary holes for inlet & outlets and over flow pipes but with NECESSARY fittings & base support for tanks | Civil | Labour | SWR34375 | 10 | L | 10000
88 | 2 | Supply & fixing 31.75 mm dia PVC flexible waste pipe of 914.4 mm length of Ist quality | Civil | Labour | SWR34426 | 33 | EA | 66
89 | 45 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)- 15.90mm OD Pipe - SDR 11 | Civil | Labour | SWR34361 | 239 | M | 10755
90 | 40 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-22.20mm OD Pipe - SDR 11 | Civil | Labour | SWR34362 | 313 | M | 12520
91 | 65 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-28.60mm OD Pipe - SDR 11 | Civil | Labour | SWR34363 | 410 | M | 26650
92 | 4 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type - 25mm NB Size | Civil | Labour | SWR34346 | 466 | EA | 1864
93 | 4 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type -20mm NB Size | Civil | Labour | SWR34345 | 331 | EA | 1324
94 | 1 | Supply & fixing 25.4 mm dia & 609.6 mm long aluminium anodized towel rod with brackets and aluminium screws | Civil | Labour | SWR34430 | 489 | EA | 489
95 | 85.51 | Earth work excavation in all type of Ordinary soils red earth, Hard gravelly soils, earth mixed with sand and sandy soils etc., in all conditions such as slushy and dry with initial leads and lifts for foundations. Ordinary Soil | Civil | Labour | SWR33015 | 486 | cum | 41557.86
96 | 18.91 | PCC (1:4:8) using 40mm HBG metal for foundations and leveling course, including cost and conveyance of all materials, labour all leads and lifts, consolidation and all operations, formwork as required, curing, etc. complete for finished item w | Civil | Labour | SWR33028 | 4771 | cum | 90219.61
97 | 91.8 | Coursed Rubble stone masonry (CRS) 2nd sort with hard granite stones in cement mortar (1:6) for basement, including cost and conveyance of all materials, labour charges, curing, all leads and lifts, etc, complete for finished item of work. | Civil | Labour | SWR33041 | 4892 | cum | 449085.6
98 | 36 | PCC (1:3:6) using 40mm HBG metal for foundations and leveling course, including cost and conveyance of all materials, labour all leads and lifts, consolidation and all operations, formwork as required, curing, etc. complete for finished item w | Civil | Labour | SWR33029 | 5061 | cum | 182196
99 | 108 | Raised pointing to the exposed surfaces of CRS masonry in cm 1:3 prop. including cost and conveyance of all materials, labour charges, all leads and lifts curing etc, complete for finished item of work. | Civil | Labour | SWR33184 | 125 | sq.mm | 13500
100 | 787.5 | Supplying and filling the substation site with borrowed gravel, watering, ramming, thoroughly complying with the standard specification. | Civil | Labour | SWR33052 | 309 | cum | 243337.5
101 | 88.8 | Plastering with CM 2 coats, 20 mm thick, base coat in CM (1:6), 16 mm thick and top coat in CM (1:4), 4mm thick with Dubara sponze finishing including cost of all materials, seigniorage charges, excluding conveyance charges of materials and including all operational, incidental and labour charges for mixing mortar, laying rendering smooth and thread lining, curing, rounding off junctions of wall and slab etc., complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33163 | 564 | sq.mm | 50083.2
102 | 200.85 | Painting with two coats of Surya Cem paint over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33329 | 85 | sq.mm | 17072.25
103 | 120 | Supply&Fabrication and fixing of Welded wire mesh ( 2" x 2") of 3mm dia. with ISMC (75x40x4.4mm) and Pheriperal frame of ISA(35x35x3mm) incldg cost& conveyance painting with synthetic enamil paint two coats over a coat of red oxide primer etc complete for finished item of work.. | Civil | Labour | SWR33403 | 2310 | sq.mm | 277200
104 | 160 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-22.20mm OD Pipe - SDR 11 | Civil | Labour | SWR34362 | 313 | M | 50080
105 | 30 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type - 25mm NB Size | Civil | Labour | SWR34346 | 466 | EA | 13980
106 | 1 | Providing Consultancy services for arranging contour surveying with total station incuding preparation of boundary and contour levels with 2 Nos. Hard copies and soft copies complete for finished items of work | Civil | Labour | SWR33427 | 5665 | EA | 5665
107 | 425.08 | Seigniorage Charges - Sand | Civil | Labour | SWR34470 | 40 | cum | 17003.2
108 | 1434.28 | Seigniorage Charges - Metal | Civil | Labour | SWR34471 | 97.5 | cum | 139842.3
109 | 839.38 | Seigniorage Charges - Gravel | Civil | Labour | SWR34472 | 30 | cum | 25181.4
110 | 60 | Supply and fixing of RCC fencing poles of size 0.1mx0.1mx1.8m (security fencing of sub station), including cost and conveyance of all labour, materials,and hire chareges etc complete for finished item of work. | Civil | Labour | SWR33405 | 1444 | ea | 86640
111 | 1200 | Supply and fixing of galvanised barded wire (1 horizantal & 2 cross strands. including cost and conveyance of all labour, materials,and hire chareges etc complete for finished item of work. | Civil | Labour | SWR33408 | 16 | M | 19200
Total Rs. | [7 empty] | 6355149.29
Total Elec+Civil withouit GST | [7 empty] | 36973631.737

## 2. Gouse Nagar
Name of the work: Estimate for erection of new 33/11kV Ashmabad(Ghousenagar) Outdoor Sub-Station with 2x8 MVA PTRS and connected 33kV and 11kV Lines at Ashmabad in Rajendranagar ECGH Division /Masterplan/RR Circle
S-1786-13-03-02-01-001
Sl No | Estimate Quantity | Description of item | Work Type | Item Short Description | APSS / Month Cl.NumberSSR 11 & 12 | Rate (INR) | UOM | AMOUNT
1 | 16 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | ELECT | Labour | SWR11039 | 928 | EA | 14848
2 | 5.76 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ELECT | Labour | SWR10868 | 6852 | TO | 39467.52
3 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELECT | supply | SMR40009 | 2181 | TO | 12562.56
4 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELECT | labour | SWR10877 | 851 | TO | 4901.76
5 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELECT | supply | SMR40010 | 1293 | TO | 7447.68
6 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELECT | labour | SWR10879 | 482 | TO | 2776.32
7 | 5.76 | Fabrication & erection of Channels-Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ELECT | labour | SWR10867 | 1470 | TO | 8467.2
8 | 16 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-R.S. Joists 150 x 150 mm | ELECT | labour | SWR10348 | 1952.61 | EA | 31241.76
9 | 17.758 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELECT | labour | SWR10356 | 6579 | M3 | 116829.882
10 | 9.24 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ELECT | labour | SWR10862 | 373 | M2 | 3446.52
11 | 16 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | ELECT | labour | SWR11089 | 48 | EA | 768
12 | 4 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-8.0Mtrs PSCC Poles 0.76 M x 0.76M x 1.52M (2.6" x 2.6" x 5.0') 0.88 cum | ELECT | labour | SWR11037 | 793 | EA | 3172
13 | 1 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ELECT | Labour | SWR10868 | 6852 | TO | 6852
14 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELECT | supply | SMR40009 | 2181 | TO | 2181
15 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELECT | labour | SWR10877 | 851 | TO | 851
16 | 1 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELECT | supply | SMR40010 | 1293 | TO | 1293
17 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELECT | labour | SWR10879 | 482 | TO | 482
18 | 1 | Fabrication & erection of Channels-Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ELECT | labour | SWR10867 | 1470 | TO | 1470
19 | 4 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Box pole 12 Mtr | ELECT | labour | SWR11267 | 3901.37 | EA | 15605.48
20 | 2.65 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELECT | labour | SWR10356 | 6579 | M3 | 17434.35
21 | 2.31 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ELECT | labour | SWR10862 | 373 | M2 | 861.63
22 | 4 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | ELECT | labour | SWR11089 | 48 | EA | 192
23 | 5.063 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ELECT | Labour | SWR10868 | 6852 | TO | 34691.676
24 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELECT | supply | SMR40009 | 2181 | TO | 11042.403
25 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELECT | labour | SWR10877 | 851 | TO | 4308.613
26 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELECT | supply | SMR40010 | 1293 | TO | 6546.459
27 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELECT | labour | SWR10879 | 482 | TO | 2440.366
28 | 5.063 | Fabrication & erection of Channels-Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ELECT | labour | SWR10867 | 1470 | TO | 7442.61
29 | 13 | Erection of AB Switch and aligment complete Erection of 33 KV AB Switch including alignment and earthing | ELECT | labour | SWR10392 | 4500 | EA | 58500
30 | 34 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | ELECT | labour | SWR10881 | 142 | EA | 4828
31 | 34 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | ELECT | labour | SWR12331 | 146.63 | EA | 4985.42
32 | 6 | Loading of 33 KV CTs/ PTs | ELECT | labour | SWR10200 | 165 | EA | 990
33 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELECT | labour | SWR11861 | 3299.7 | EA | 3299.7
34 | 6 | Un loading of 33 KV CTs/ PTs | ELECT | labour | SWR10518 | 128 | EA | 768
35 | 2 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33kv single phase PT s | ELECT | labour | SWR10401 | 1079 | SET | 2158
36 | 12 | Loading of 33 KV, 10 KA LAs Station typ | ELECT | labour | SWR10266 | 41 | EA | 492
37 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELECT | labour | SWR11861 | 3299.7 | EA | 3299.7
38 | 12 | Un loading of 33 KV, 10 KA LAs Station type | ELECT | labour | SWR10584 | 35 | EA | 420
39 | 4 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33 KV LAS station/Line type including earthing | ELECT | labour | SWR10396 | 880 | SET | 3520
40 | 2 | Loading of 33 KV VCBs along with Panel boards | ELECT | labour | SWR10198 | 1024 | EA | 2048
41 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELECT | labour | SWR11861 | 3299.7 | EA | 3299.7
42 | 2 | Un loading of 33 KV VCBs along with Panel boards | ELECT | labour | SWR10516 | 1044.48 | EA | 2088.96
43 | 12.584 | Excavate-Pit for 33KV VCB | ELECT | labour | SWR23224 | 331 | M3 | 4165.304
44 | 14.52 | Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x 1.8 x 0.75 cum for VCB Plinth | ELECT | labour | SWR20685 | 5160 | M3 | 74923.2
45 | 2 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33 KV VCB with Control Panel | ELECT | labour | SWR10460 | 12500 | EA | 25000
46 | 2 | Loading and unloading of PTR on constructed plinth-Loading of 8MVA PTR | ELECT | labour | SWR10613 | 5805.84 | EA | 11611.68
47 | 2 | Transport of Power transformers (0 to 100 KM) from one place to another place in GHMC Area.(excluding of loading & unloading )-8MVA power transformer | ELECT | labour | SWR10854 | 21945 | EA | 43890
48 | 2 | Loading and unloading of PTR on constructed plinth-Unloading of 8MVA PTR | ELECT | labour | SWR10627 | 5805.84 | EA | 11611.68
49 | 700 | S/o rail poles 90/105lb (250x2N) | ELECT | supply | SMR22718 | 47.27 | KG | 33089
50 | 14 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Rail pole 90 lbs | ELECT | labour | SWR10344 | 3510 | EA | 49140
51 | 2 | Erection of PTR on constructed plinth-Erection of 8 MVA PTR. | ELECT | labour | SWR21321 | 49480.2 | EA | 98960.4
52 | 0.436 | Extention of 33KV Bay at 132/33KV Sub-station-Zebra condutor | ELECT | supply | SMR24910 | 299369 | KM | 130524.884
53 | 30 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing | ELECT | supply | SMR11915 | 2055 | SET | 61650
54 | 30 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of I-Bolts | ELECT | supply | SMR22473 | 294 | EA | 8820
55 | 45 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 "to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating . Sup T clamp LM6 Al alloy of 12 mm, 800 A | ELECT | supply | SMR40011 | 299 | EA | 13455
56 | 6 | Bus stringing Hoisting of Insulators and hardware, stretching the conductor and stringing of 33 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bussection of 4.5mt) Hoisting post ins&hrd wr 1panther 33kv | ELECT | labour | SWR21240 | 781 | EA | 4686
57 | 84 | Stringing of bus with panther conductor including jumpering etc., complete to all the equipment in SS fixing to all clamps and equipment.(3 Conductors) | ELECT | labour | SWR10404 | 327.68 | M | 27525.12
58 | 30 | Bus stringing Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | ELECT | labour | SWR10884 | 224 | EA | 6720
59 | 75 | Labour for Fixing of all types of clamps | ELECT | labour | SWR10917 | 65 | EA | 4875
60 | 25 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | ELECT | Labour | SWR11039 | 928 | EA | 23200
61 | 8.68 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ELECT | Labour | SWR10868 | 6852 | TO | 59475.36
62 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELECT | supply | SMR40009 | 2181 | TO | 18931.08
63 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELECT | labour | SWR10877 | 851 | TO | 7386.68
64 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELECT | supply | SMR40010 | 1293 | TO | 11223.24
65 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELECT | labour | SWR10879 | 482 | TO | 4183.76
66 | 8.68 | Fabrication & erection of Channels-Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ELECT | labour | SWR10867 | 1470 | TO | 12759.6
67 | 25 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-R.S. Joists 150 x 150 mm | ELECT | labour | SWR10348 | 1952.61 | EA | 48815.25
68 | 27.75 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELECT | labour | SWR10356 | 6579 | M3 | 182567.25
69 | 17.91 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ELECT | labour | SWR10862 | 373 | M2 | 6680.43
70 | 25 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | ELECT | labour | SWR11089 | 48 | EA | 1200
71 | 4.642 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ELECT | Labour | SWR10868 | 6852 | TO | 31806.984
72 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELECT | supply | SMR40009 | 2181 | TO | 10124.202
73 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELECT | labour | SWR10877 | 851 | TO | 3950.342
74 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELECT | supply | SMR40010 | 1293 | TO | 6002.106
75 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELECT | labour | SWR10879 | 482 | TO | 2237.444
76 | 4.642 | Fabrication & erection of Channels-Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ELECT | labour | SWR10867 | 1470 | TO | 6823.74
77 | 17 | Erection of AB Switch and aligment complete-Erection of 11KV 800A double throw AB Switches | ELECT | labour | SWR21277 | 3500 | EA | 59500
78 | 3 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | ELECT | labour | SWR10393 | 3200 | EA | 9600
79 | 2 | Loading of 11 KV CT - PT Sets | ELECT | labour | SWR10201 | 190 | EA | 380
80 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELECT | labour | SWR11861 | 3299.7 | EA | 3299.7
81 | 2 | Un loading of 11 KV CT - PT Sets | ELECT | labour | SWR10519 | 101 | EA | 202
82 | 2 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc-Erection of 11 KV three phase PTs | ELECT | labour | SWR10402 | 800 | SET | 1600
83 | 24 | Loading of 11 KV, 10 KA LAs Station type | ELECT | labour | SWR10264 | 32 | EA | 768
84 | 2 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELECT | labour | SWR11861 | 3299.7 | EA | 6599.4
85 | 24 | Un loading of 11 KV, 10 KA LAs Station type | ELECT | labour | SWR10582 | 32 | EA | 768
86 | 2 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc-Erection of 11 KV LAS station type including earthing | ELECT | labour | SWR10397 | 559 | SET | 1118
87 | 6 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc-Erection of 11 KV LAS line type including earthing | ELECT | labour | SWR10398 | 505 | SET | 3030
88 | 8 | Loading of 11 KV VCBs along with Panel boards | ELECT | labour | SWR10199 | 1024 | EA | 8192
89 | 4 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELECT | labour | SWR11861 | 3299.7 | EA | 13198.8
90 | 8 | Un Loading of 11 KV VCBs along with Panel boards | ELECT | labour | SWR10517 | 1044.48 | EA | 8355.84
91 | 41.6 | Excavate-Pit for 33KV VCB | ELECT | labour | SWR23224 | 331 | M3 | 13769.6
92 | 48 | Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x 1.8 x 0.75 cum for VCB Plinth | ELECT | labour | SWR20685 | 5160 | M3 | 247680
93 | 8 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc-Erection of 11 KV VCB with Control Panel | ELECT | labour | SWR10461 | 12000 | EA | 96000
94 | 12 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing | ELECT | supply | SMR11915 | 2055 | SET | 24660
95 | 12 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of I-Bolts | ELECT | supply | SMR22473 | 294 | EA | 3528
96 | 45 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 "to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating . Sup T clamp LM6 Al alloy of 12 mm, 800 A | ELECT | supply | SMR40011 | 299 | EA | 13455
97 | 2 | Bus Stringing -Hoisting of Insulators and hardware, stretching the conductor and stringing of 11 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 3.5mt) Hoisting post ins&hrd wr 1panther 11kv | ELECT | labour | SWR21241 | 507 | EA | 1014
98 | 63 | Stringing of bus with panther conductor including jumpering etc., complete to all the equipment in SS fixing to all clamps and equipment.(3 Conductors) | ELECT | labour | SWR10404 | 327.68 | M | 20643.84
99 | 45 | Bus stringing Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | ELECT | labour | SWR10884 | 224 | EA | 10080
100 | 57 | Labour for Fixing of all types of clamps | ELECT | labour | SWR10917 | 65 | EA | 3705
101 | 584 | Laying of earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication 75x 8mm MS Flat / GI Flat. Laying of earth mat,excavation 75x 8mm | ELECT | labour | SWR10920 | 65 | RMT | 37960
102 | 1010 | Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) Earthing for raisers of SS Flat 50x6 mm. | ELECT | labour | SWR10919 | 41 | RMT | 41410
103 | 36 | Supply of earthing pipe with materials -Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | ELECT | supply | SMR11482 | 3486 | EA | 125496
104 | 36 | Providing of Earthing-Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | ELECT | labour | SWR10357 | 1234.2 | EA | 44431.2
105 | 36 | Providing of RCC collar to earth pit-Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINES-Providing of RCC collar | ELECT | labour | SWR10359 | 386 | EA | 13896
106 | 2 | Supply of Copper Flexible jumper with 75 X 8 of length 250 mm at neutral of Power tranformer end and 50 X 6 of length 50mm two Nos at double neutral end duly brasing with flexible jumper of capacity of 5kA/3 sec for power transformer neutral. SupCU Flexi jumper for Power T/F Neutral | ELECT | supply | SMR40033 | 4725 | EA | 9450
107 | 2 | Providing of earthing with various types of earth electrodes-Providing of double earthing for neutral with flexible copper jumpers including arrangement by fixing M.S.Channel 100x50mm. | ELECT | labour | SWR11892 | 1323 | EA | 2646
108 | 80 | Providing of control cable trench as per DATA-XII | ELECT | labour | SWR22093 | 3148 | RMT | 251840
109 | 3074 | Control Cable-Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends . Lay-4C/10C 2.5Sqmm Control Cable | ELECT | labour | SWR11879 | 27 | M | 82998
110 | 270 | Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per specification (including cost of ferrules, lugs and glands) | ELECT | labour | SWR12510 | 27 | EA | 7290
111 | 4 | Marshalling Box Supply of FRP PT Marshalling Box | ELECT | supply | SMR40048 | 4463 | EA | 17852
112 | 4 | Marshalling Box Erection of Marshalling boxes | ELECT | labour | SWR10940 | 374.85 | EA | 1499.4
113 | 1 | Loading of 220 V Batterry with charger | ELECT | labour | SWR11166 | 1612 | SET | 1612
114 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELECT | labour | SWR11861 | 3299.7 | EA | 3299.7
115 | 1 | Un loading of 220 V Batterry with charger | ELECT | labour | SWR11147 | 1024 | SET | 1024
116 | 1 | Batteries-Erection of 220 V, 200 AH battery in complete shape fit for charging . Conventional lead acid | ELECT | labour | SWR12350 | 7666 | EA | 7666
117 | 1 | Control Panels -Supply of DC Annunciation & relay panel for 10 feeder panel including the cost of LED Indiacation lamps, VAA auxilairy relays, Electronic Hooters complete as per specification. | ELECT | supply | SMR40044 | 42500 | EA | 42500
118 | 1 | Control Panels -Supply of AC Supply panel inluding providing of changeover switch, SFU, metering unit, 32 A three phase MCB, 16 A Single phase MCB complete as per specification. Supply of AC Supply panel complete | ELECT | supply | SMR40045 | 42000 | EA | 42000
119 | 2 | Fixing of AC/DC Panel and giving Connections to the protection equipment and Metering circuits as per the specification and standards. The 3 1/2 core 25 Sqmm power cable required from distribution box to AC/DC panel in the control room is also to be supply | ELECT | labour | SWR20025 | 7871.85 | SET | 15743.7
120 | 8 | Yard lightning-Supply of stepped tubular poles single way made of steel of length 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9 mm, 2.1 mtrs with outer dia 76.1 mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79 kgf as per IS 2713 | ELECT | Supply | SMR40051 | 13913 | EA | 111304
121 | 8 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE/CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA /OSRAM /SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty S-90W LED fixture set | ELECT | suppply | SMR11594 | 8200 | EA | 65600
122 | 8 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | ELECT | Labour | SWR11039 | 928 | EA | 7424
123 | 8 | Erection of tubular poles | ELECT | labour | SWR10955 | 1379 | EA | 11032
124 | 5.27 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELECT | labour | SWR10356 | 6579 | M3 | 34671.33
125 | 8 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE/CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA /OSRAM /SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty. Fixing of Metal halide lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5 GI pipe complete Fixing of LED/Metal halide complete. | ELECT | labour | SWR10956 | 1268 | EA | 10144
126 | 45 | Supply of HBG metal-Supply & spreading of 20mm machine crushed metal (HBG) including cost of conveneyance of all materials, labour charges etc complete for finished item of work and directed by the engineer incharge | ELECT | labour | SWR10860 | 2113 | M3 | 95085
127 | 2 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M Ex of Hard pit w/o blast 0.75X0.9X1.95M | ELECT | labour | SWR11040 | 990.68 | EA | 1981.36
128 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELECT | supply | SMR40009 | 2181 | TO | 1635.75
129 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELECT | labour | SWR10877 | 851 | TO | 638.25
130 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELECT | supply | SMR40010 | 1293 | TO | 969.75
131 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELECT | labour | SWR10879 | 482 | TO | 361.5
132 | 1 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Box pole 12 Mtr | ELECT | labour | SWR11267 | 3901.37 | EA | 3901.37
133 | 2.22 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELECT | labour | SWR10356 | 6579 | M3 | 14605.38
134 | 1.16 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ELECT | labour | SWR10862 | 373 | M2 | 432.68
135 | 2 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | ELECT | labour | SWR11089 | 48 | EA | 96
136 | 1 | Construction of DTR Plinth-RCC Column type DTR Plinth of size 1'X1'X10',topslab 4'x4'x6" & beam size 4'X8'X8" upto 160KVA | ELECT | labour | SWR21843 | 25967.57 | EA | 25967.57
137 | 1 | Loading of 50,63, 75 & 100 KVA DTR | ELECT | labour | SWR10195 | 350 | EA | 350
138 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELECT | labour | SWR11861 | 3299.7 | EA | 3299.7
139 | 1 | Un loading of 50,63, 75 & 100 KVA DTR | ELECT | labour | SWR10513 | 280 | EA | 280
140 | 1 | Erection of DTR's including loading and Unloading DTR on the Structure/Plinth etc-Erection of 3 Phase DTRs 63,75 & 100 KVA | ELECT | labour | SWR20905 | 1650 | EA | 1650
141 | 1 | Erection of AB Switch and aligment complete Erection of 11KV 200A TT type AB Switch including fixing of cross angles and alignment complete | ELECT | labour | SWR20102 | 1813.49 | EA | 1813.49
142 | 1 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erect. of 11kv HG Fuseset incl earthing | ELECT | labour | SWR10395 | 740.52 | SET | 740.52
143 | 40 | Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.-In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road-11KV 3x185 Sqmm Cable | ELECT | labour | SWR11920 | 465.46 | M | 18618.4
144 | 20 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-11 KV 3x185 Sqmm Cable | ELECT | labour | SWR11956 | 126.23 | M | 2524.6
145 | 2 | Making of Outdoor/Indoor End Termination -Making 11 KV 3x185 Sqmm Cable Out Door/Indoor end termination | ELECT | labour | SWR10390 | 2370.63 | EA | 4741.26
146 | 1 | Erection of AB Switch and aligment complete-Erection of LT distribution box including laying of LT cable from distribution box to LT OH line and DTR to distribution box including earthing of distribution box and crimping of lugs connecting of jumpers etc | ELECT | labour | SWR10674 | 1594.67 | EA | 1594.67
147 | 85 | LAYING OF 33KV, 11KV UG CABLE Excavation & laying of UG Cable in Single Run Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road-LT 3 1/2 x 185 Sqmm Cable | ELECT | labour | SWR11923 | 377.63 | M | 32098.55
148 | 15 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-LT 3 1/2 x 185 Sqmm Cable | ELECT | labour | SWR11959 | 85.43 | M | 1281.45
149 | 2 | Making of Outdoor/Indoor End Termination-Supply of 31/2x185Sqmm UG O/D end termination kits | ELECT | supply | SMR40140 | 550 | EA | 1100
150 | 2 | UG Cables Joints :-Making of Outdoor/Indoor End Termination -Supply & fixing of Oout Door/Indoor end termination LT 3 1/2 x 185 Sqmm Cable | ELECT | labour | SWR10765 | 968.9 | EA | 1937.8
151 | 1 | Supply and fixing of Substation board of size 3'x2.5' indicating the layout of switchyard Sup &fix of board ind Switchyard layout | ELECT | labour | SWR20032 | 1654 | EA | 1654
152 | 1 | Supply and fixing of safety instructions/Substation operation instruction board. Sup& fix safety inst/SS Op. inst board | ELECT | labour | SWR22090 | 2205 | EA | 2205
153 | 750 | Control Panels Supplying & fabrication erection of 6mm Checkerd plates as per the field conditions Supply,fabricati of 6mm Checkerd plates | ELECT | labour | SWR10873 | 83 | KG | 62250
154 | 1 | T & P Supply of Wall clock standard make | ELECT | supply | SMR40059 | 578 | EA | 578
155 | 1 | S-10ft Aluminium Ladder | ELECT | supply | SMR12378 | 1654 | EA | 1654
156 | 1 | Sup Alluminium Ladder for indoor works | ELECT | supply | SMR40062 | 4410 | EA | 4410
157 | 30 | T & P Painting of Name Plates for any equipmen | ELECT | labour | SWR10963 | 122 | EA | 3660
158 | 1 | T & P Supply of Taparia Tool kit of Size 20”x10”x15” with tier arrangements Tool box with locking arrangement & key containing (1) Double Ended fix Spanner sets, (Ribbed) 6 x 7, 8 x 9, 10 x 11, 12 x 13, 14 x 15, 16 x 17, 18 x19, 20 x 22, 21 x 23, 24 x 27, 25 x28, 30 x 32, (2) Double Ended Ring Spanners sets, 6 x 7 , 8 x 9, 10 x 11, 12 x 13, 14 x 15. 16 x 17 , 18 x 19, 20 x 22 , 21 x 23, 24 x 27, 25 x28, 30 x 32 mm, (3) Adjustable Spanner 305 mm length least maximum opening 35mm chrome, (4) Pipe Wrench Length 350 mm 14”, (5) Soft faced Hammer with suitable handle 2 lb, (6) Hacksaw frame with metal handle heavy duty for 12" hacksaw blade with High Speed blade, (7) Insulated Screw drivers Transparent Green Handle Set Length 6”, 8” & 12”, (8) Star Screw Driver Transparent Green Handle Length 6”, (9) Insulated Wire Cutter, (10) Insulated Cutting Plier Length 8” with cable stripper insulated with thick C. A. sleeve confirming to IS: 4378 - 1990, (11) Long Nose Plier insulated with thick C.A. sleeve generally confirming to IS:3552-1989, (12) Tester type screw driver (special with neon bulb) generally confirm to IS: 5579- 1985 Grade:II handle yellow/ green colour overall length 130 mm, (13) Insulated Crimping Plier of all Taparia make. SupTaparia Tool kit complete as per Spec | ELECT | supply | SMR40063 | 4925 | SET | 4925
159 | 1 | T & P Sup Rechargeable LED torch light of Standard make | ELECT | supply | SMR40064 | 1733 | EA | 1733
160 | 1 | T & P-Steel almarah(61/2 X 3ft) Godrej | ELECT | supply | SMR40061 | 9818 | EA | 9818
161 | 1 | T & P-Table (3x6ft) Godrej | ELECT | supply | SMR40057 | 6050 | EA | 6050
162 | 4 | T & P-S type chairs (Godrej) | ELECT | supply | SMR40058 | 924 | EA | 3696
163 | 1 | T & P Sup Angle racks(18x36.6inches) Godrej | ELECT | supply | SMR40060 | 1733 | EA | 1733
164 | 1 | T & P Supply of Hack saw (12 inches) | ELECT | supply | SMR40065 | 289 | EA | 289
165 | 4 | Sup Earth Rods (8ft) Screw & clamp type | ELECT | supply | SMR40066 | 578 | EA | 2312
166 | 2 | Supply of Hand Gloves | ELECT | supply | SMR40067 | 289 | SET | 578
167 | 12 | SupRubber mats( 6'x3')size fo indoorSS | ELECT | supply | SMR40068 | 1386 | EA | 16632
168 | 1 | Biometric Time attendence System & Telecom Sup Stand basic cell phone with charger | ELECT | supply | SMR40069 | 1386 | EA | 1386
169 | 14 | Supply of Danger boards with clamps | ELECT | supply | SMR40070 | 116 | EA | 1624
170 | 2 | Supply of Materials -Fire bucket stand with 3 buckets (8 -10 ltr capacity) | ELECT | supply | SMR40088 | 1386 | SET | 2772
171 | 2 | Room fire extinguisher (2 ltrs capacity) for control room | ELECT | supply | SMR40089 | 4620 | EA | 9240
172 | 4 | Sup TrollyMounted Co2 (6.5Kgs) Cylinders(IS-2878) | ELECT | supply | SMR40087 | 9240 | EA | 36960
173 | 6 | Supply of Safety Helmet of standard make | ELECT | supply | SMR40071 | 231 | EA | 1386
174 | 8 | Supply of LC Boards | ELECT | supply | SMR40072 | 116 | EA | 928
175 | 4 | Supply of Gum Boots(Pairs) | ELECT | supply | SMR40073 | 693 | EA | 2772
176 | 1 | Supply of 5000v megger | ELECT | supply | SMR40074 | 13860 | EA | 13860
177 | 1 | Supply of Earth megger (1000v) | ELECT | supply | SMR40075 | 8085 | EA | 8085
178 | 1 | Supply of Digital clamp meter. | ELECT | supply | SMR40076 | 2888 | EA | 2888
179 | 1 | Name board of the 33/11kV Sub-Station(As per Standard Specification) Sup 33/11kv S.S Permanent name board | ELECT | supply | SMR40086 | 10238 | EA | 10238
180 | 800 | Supply of Hot dip galvanized/zinc coated bolts & nuts including spring washers, pack washers and flat washers etc. | ELECT | supply | SMR12488 | 90 | KG | 72000
181 | 2 | Fabrication of poles-Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | ELECT | labour | SWR10642 | 512.55 | EA | 1025.1
182 | 1 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-RS Joists 150x75/175 x 85 mm | ELECT | labour | SWR10346 | 1934 | EA | 1934
183 | 5760 | Supply of Materials -- Supply of RS Joist girder Poles (150X150mm) | ELECT | labour | SMR12302 | 59.25 | KG | 341280
184 | 1000 | Supply of Materials -- supply of RS Joist Poles (175X85mm) | ELECT | labour | SMR12303 | 60.75 | KG | 60750
185 | 5063 | Supply of Materials -- Supply of MS Channel 100X50mm | ELECT | labour | SMR22745 | 57.45 | KGS | 290869.35
186 | 13 | Supply of Materials -- Supply of 33 kV 800 A Double break AB switch | ELECT | labour | SMR12315 | 40658.78 | EA | 528564.14
187 | 8680 | Supply of Materials -- Supply of RS Joist girder Poles (150X150mm) | ELECT | labour | SMR12302 | 59.25 | KG | 514290
188 | 4642 | Supply of Materials -- Supply of MS Channel 100X50mm | ELECT | labour | SMR22745 | 57.45 | KGS | 266682.9
189 | 17 | Supply of Materials -- Supply of 11 kV 800 A Double break AB switch | ELECT | labour | SMR12316 | 30847.46 | EA | 524406.82
190 | 3 | Supply of Materials -- Supply of 11 kV 400 A Double break AB switch | ELECT | labour | SMR12317 | 18150 | EA | 54450
191 | 3045 | Supply of Materials -- Supply of MS Flat 75x8 mm | ELECT | labour | SMR12321 | 56.42 | KG | 171798.9
192 | 2666 | Supply of Materials -- Supply of MS Flat 50x6 mm | ELECT | labour | SMR12322 | 56.5 | KG | 150629
193 | 750 | Supply of Materials -- supply of RS Joist Poles (175X85mm) | ELECT | labour | SMR12303 | 60.75 | KG | 45562.5
194 | 1 | Supply of Materials -- Supply of 11 kV 200 A Tilting type AB switch | ELECT | labour | SMR12318 | 8991 | EA | 8991
195 | 1 | Supply of Materials -- Supply of 11KV HG fuse set for station transformer | ELECT | labour | SMR12324 | 1974 | EA | 1974
196 | 1 | Supply of LT Distribution Box (SMC) | ELECT | labour | SMR25200 | 7797 | EA | 7797
197 | 40 | Supply of XLPE Cable 1 C 150 sqmm | ELECT | labour | SMR25203 | 114.83 | M | 4593.2
198 | 100 | Supply of XLPE Cable 3 1/2 C 185 sqmm | ELECT | labour | SMR25204 | 547 | M | 54700
199 | 2 | Supply of 11KV 3x185 Heat Shble O/d End Term Kit | ELECT | labour | SMR25201 | 1182.97 | EA | 2365.94
200 | 4 | Loading of LT AB Cable 3X16+25 Sqmm | ELECT | supply | SWR11702 | 200 | DR | 800
201 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) - Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates -Above 10 Km and upto 20 Km with Lorry for each trip | ELECT | supply | SWR11861 | 3299.7 | EA | 3299.7
202 | 4 | Un loading of LT AB Cable 3X16+25 Sqmm | ELECT | supply | SWR11713 | 204 | DR | 816
203 | 7 | survey line&cabl inc peg mark&tree clear | ELECT | labour | SWR22092 | 765 | KM | 5355
204 | 7 | Paving out and stringing of conductor by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location-100 Sqmm Single Circuit (3 Conductors) | ELECT | labour | SWR10366 | 13856.7 | KM | 96996.9
205 | 140 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M Ex of Hard pit w/o blast 0.75X0.9X1.95M | ELECT | labour | SWR11040 | 990.68 | EA | 138695.2
206 | 140 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Errection of 11 M long PSCC pole | ELECT | labour | SWR10978 | 4336.85 | EA | 607159
207 | 49.256 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELECT | labour | SWR10356 | 6579 | M3 | 324055.224
208 | 140 | Painting of poles-Numbering of poles incl. cost of paint | ELECT | labour | SWR10378 | 32 | EA | 4480
209 | 40 | Excavation of pits in all soils except hard rock requiring blasting-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") 1.05 cum | ELECT | labour | SWR10107 | 700 | EA | 28000
210 | 40 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Erec of 9.1 Mts PSCC poles for stuts | ELECT | labour | SWR11083 | 2400 | EA | 96000
211 | 21 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELECT | labour | SWR10356 | 6579 | M3 | 138159
212 | 28 | Formation of Cut points - Formation of Cut point for 11 KV Single Circuit line excluding pole erection and stays Formatn of Horiz Cut point for 11KV line | ELECT | labour | SWR10653 | 1435.81 | EA | 40202.68
213 | 200 | Supply of earthing pipe with materials S-GI Bolts & Nuts,Washers etc., | ELECT | supply | SMR11488 | 117.5 | KG | 23500
214 | 11 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 50 Km and upto 80 Km with Lorry for each trip | ELECT | labour | SWR11864 | 5290.74 | EA | 58198.14
215 | 7 | LOADING of Conductor drums | ELECT | labour | SWR10191 | 202 | EA | 1414
216 | 7 | UNLOADING of Conductor drums | ELECT | labour | SWR10509 | 100 | EA | 700
217 | 45 | Loading of 33 KV Pin insulators | ELECT | labour | SWR10211 | 3 | CRT | 135
218 | 45 | Un loading of 33 KV Pin insulators | ELECT | labour | SWR10529 | 3 | CRT | 135
219 | 8 | Loading of 33 KV Metal parts | ELECT | labour | SWR10618 | 65 | BAG | 520
220 | 8 | Un loading of 33 KV Metal parts | ELECT | labour | SWR10632 | 65 | BAG | 520
221 | 1960 | Excavation & laying of UG Cable (Double Run) Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, Along the CC / BT multi layer road requiring compressor-33 KV 3x400 Sqmm Cable | ELECT | labour | SWR11980 | 1388.84 | M | 2722126.4
222 | 1960 | Laying of 2nd cable in excavated trench | ELECT | labour | SWR10988 | 204.1 | M | 400036
223 | 40 | Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-33 KV 3x400 Sqmm Cable | ELECT | labour | SWR12004 | 323.85 | M | 12954
224 | 12 | Cost of Pipes and slabs-Supply of 6" B class GI pipe | ELECT | supply | SMR40081 | 1044 | M | 12528
225 | 30 | Cost of Pipes and slabs-Supply of 250 mm Hume pipe of class NP3 with compresive strength of 35N/mm2 for 28 days curing,barewall thickness of 30mm,1.25kG linear/meter and withstanding capability of 22.50KN/linear meter as per IS 458-1993. | ELECT | supply | SMR40077 | 363 | M | 10890
226 | 14 | Cost of Pipes and slabs-Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters , CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | ELECT | supply | SMR40085 | 484 | EA | 6776
227 | 14 | Load-11/33KV XLPE UG Cable for all sizes | ELECT | labour | SWR11230 | 1024 | DR | 14336
228 | 14 | Unload-11/33KV XLPE UG Cable for all sizes | ELECT | labour | SWR11231 | 1024 | DR | 14336
229 | 8 | Making of Outdoor/Indoor End Making 33 KV 3x400 Sqmm Cable Out Door/Indoor end termination TerminationOD/Idoor end termination 33kv 3x400 xlpe | ELECT | labour | SWR10387 | 2764.76 | EA | 22118.08
230 | 14 | UG Cables Joints 33 KV 3x400 Sqmm Cable Straight through joint 33kv 3x400 xlpe | ELECT | labour | SWR10382 | 5700.78 | EA | 79810.92
231 | 2.4 | Fabrication & erection of Channels -Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to theRS-Joist poles excluding cost of Mild Steel and transportcharges to substation site, including erection. Fabrication of struc.with welding. | ELECT | labour | SWR10869 | 3426 | TO | 8222.4
232 | 50 | Supply of earthing pipe with materials-Supply of GI wire No 8 | ELECT | supply | SMR11486 | 105 | KG | 5250
233 | 2 | Supply of earthing pipe with materials-Supply of CI eath pipe with 80mm dia,2.0 M Length | ELECT | labour | SMR11483 | 2789 | EA | 5578
234 | 2 | Providing of Earthing-Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | ELECT | labour | SWR10357 | 1234.2 | EA | 2468.4
235 | 2 | Providing of RCC collar to earth pit-Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINES-Providing of RCC collar | ELECT | labour | SWR10359 | 386 | EA | 772
236 | 40 | Supply of earthing pipe with materials-Supply of GI Flat 25X3 mm | ELECT | supply | SMR11485 | 105 | KG | 4200
237 | 20 | Supply of Danger boards with clamps | ELECT | supply | SMR40070 | 116 | EA | 2320
238 | 14 | S&E-Smart RFID marker | ELECT | labour | SWR25089 | 2745 | EA | 38430
239 | 140 | Supply of PSCC Pole 11Mtr 365KG | ELECT | supply | SMR25236 | 5399 | EA | 755860
240 | 40 | Supply of PSCC Pole 9.1Mtr 280KG | ELECT | supply | SMR25233 | 3109.41 | EA | 124376.4
241 | 112 | Supply of 33KV V-Cross Arm without Clamps | ELECT | supply | SMR25229 | 1678 | EA | 187936
242 | 1500 | Supply of Materials -- Supply of MS Channel 100X50mm | ELECT | supply | SMR22745 | 57.45 | KGS | 86175
243 | 200 | Supply of Materials -- Supply of MS Flat 75x8 mm | ELECT | supply | SMR12321 | 56.42 | KG | 11284
244 | 700 | Supply of MS Angle 65x65x6 | ELECT | supply | SMR25207 | 57.25 | KG | 40075
245 | 8 | UG Cables Joints : Making of Outdoor/Indoor End Termination -- Supply 33KV 3x400Sqmm Outdoor | ELECT | supply | SMR22222 | 4554 | EA | 36432
246 | 14 | UG Cables Joints : Making of Straight through joints -- Supply of 33KV 3x400SQmm Straight Through Joint Kit | ELECT | supply | SMR22223 | 24151 | EA | 338114
247 | 9 | survey line&cabl inc peg mark&tree clear | ELECT | labour | SWR22092 | 765 | KM | 6885
248 | 9 | Paving out and stringing of conductor by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location-55 Sqmm Single Circuit (3 Conductors) | ELECT | labour | SWR10365 | 9454.81 | KM | 85093.29
249 | 175 | Excavation of pits in all soils except hard rock requiring blasting-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") 1.05 cum | ELECT | labour | SWR10107 | 700 | EA | 122500
250 | 50 | Excavation of pits in hard rock requiring blasting. (other than SS)-9.1Mtrs PSCC Pole 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | ELECT | labour | SWR10112 | 1770 | EA | 88500
251 | 213 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-9.1 M long PSCC pole | ELECT | labour | SWR10343 | 2400 | EA | 511200
252 | 37.8 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELECT | labour | SWR10356 | 6579 | M3 | 248686.2
253 | 225 | Painting of poles-Numbering of poles incl. cost of paint | ELECT | labour | SWR10378 | 32 | EA | 7200
254 | 80 | Excavation of pits in all soils except hard rock requiring blasting-Stud Poles 0.6 M x 0.9 M x 1.5 M | ELECT | labour | SWR10106 | 645 | EA | 51600
255 | 80 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-8.0 m long PSCC poles for Strut | ELECT | labour | SWR21590 | 1500 | EA | 120000
256 | 32 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELECT | labour | SWR10356 | 6579 | M3 | 210528
257 | 40 | Formation of Cut points - Formation of Cut point for 11 KV Single Circuit line excluding pole erection and stays Formatn of Horiz Cut point for 11KV line | ELECT | labour | SWR10653 | 1435.81 | EA | 57432.4
258 | 350 | Supply of earthing pipe with materials S-GI Bolts & Nuts,Washers etc., | ELECT | supply | SMR11488 | 117.5 | KG | 41125
259 | 5 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 50 Km and upto 80 Km with Lorry for each trip | ELECT | labour | SWR11864 | 5290.74 | EA | 26453.7
260 | 4 | LOADING of Conductor drums | ELECT | labour | SWR10191 | 202 | EA | 808
261 | 4 | UNLOADING of Conductor drums | ELECT | labour | SWR10509 | 100 | EA | 400
262 | 6 | Supply of earthing pipe with materials-Supply of CI eath pipe with 50mm dia,2.0 M Length | ELECT | supply | SMR11484 | 2441 | EA | 14646
263 | 6 | Providing of Earthing-Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | ELECT | labour | SWR10357 | 1234.2 | EA | 7405.2
264 | 6 | Providing of RCC collar to earth pit-Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINES-Providing of RCC collar | ELECT | labour | SWR10359 | 386 | EA | 2316
265 | 6 | Assembly and erection of Structure as per specification which includes fixing of top channels and cross bracings, transport of all materials from road side to the location, earthing, back filling with earth ramming etc excluding pit excavation and concreting.-11KV DP Structure with 9.1 Mtrs PSCC Poles | ELECT | labour | SWR21130 | 3363.96 | SET | 20183.76
266 | 6 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | ELECT | labour | SWR10393 | 3200 | EA | 19200
267 | 6 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | ELECT | labour | SWR10881 | 142 | EA | 852
268 | 50 | Supply of earthing pipe with materials-Supply of GI wire No 8 | ELECT | supply | SMR11486 | 105 | KG | 5250
269 | 675 | Loading of 11KV Polymer Pin Insulators with GI pins | ELECT | labour | SWR11248 | 1 | EA | 675
270 | 675 | Un loading of 11KV Polymer Pin Insulators with GI pins | ELECT | labour | SWR11249 | 1 | EA | 675
271 | 240 | Loading of 11KV Polymer Pin Insulators with GI pins | ELECT | labour | SWR11248 | 1 | EA | 240
272 | 240 | Un loading of 11KV Polymer Pin Insulators with GI pins | ELECT | labour | SWR11249 | 1 | EA | 240
273 | 6 | Loading of 11 KV Metal parts | ELECT | labour | SWR12402 | 48 | BAG | 288
274 | 6 | Un loading of 11 KV Metal parts | ELECT | labour | SWR12421 | 48 | BAG | 288
275 | 960 | Laying of 2nd cable in excavated trench | ELECT | labour | SWR10988 | 204.1 | M | 195936
276 | 72 | Cost of Pipes and slabs-Supply of 6" B class GI pipe | ELECT | supply | SMR40081 | 1044 | M | 75168
277 | 200 | Cost of Pipes and slabs-Supply of 250 mm Hume pipe of class NP3 with compresive strength of 35N/mm2 for 28 days curing,barewall thickness of 30mm,1.25kG linear/meter and withstanding capability of 22.50KN/linear meter as per IS 458-1993. | ELECT | supply | SMR40077 | 363 | M | 72600
278 | 6 | Cost of Pipes and slabs-Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters , CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | ELECT | supply | SMR40085 | 484 | EA | 2904
279 | 5 | Load-11/33KV XLPE UG Cable for all sizes | ELECT | labour | SWR11230 | 1024 | DR | 5120
280 | 5 | Unload-11/33KV XLPE UG Cable for all sizes | ELECT | labour | SWR11231 | 1024 | DR | 5120
281 | 1.1 | Fabrication & erection of Channels -Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to theRS-Joist poles excluding cost of Mild Steel and transportcharges to substation site, including erection. Fabrication of struc.with welding. | ELECT | labour | SWR10869 | 3426 | TO | 3768.6
282 | 50 | Supply of Danger boards with clamps | ELECT | supply | SMR40070 | 116 | EA | 5800
283 | 6 | S&E-Smart RFID marker | ELECT | labour | SWR25089 | 2745 | EA | 16470
284 | 960 | Excavation & laying of UG Cable (Double Run)-Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts,-In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil/CC-11 KV 3x300 Sqmm Cable | ELECT | labour | SWR11973 | 631.06 | M | 605817.6
285 | 240 | Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-11 KV 3x300 Sqmm Cable | ELECT | labour | SWR12005 | 275.4 | M | 66096
286 | 24 | Making of Outdoor/Indoor End Termination-Making 11 KV 3x300 Sqmm Cable Out Door/Indoor end termination | ELECT | labour. | SWR10391 | 2370.63 | EA | 56895.12
287 | 6 | UG Cables Joints Making of Straight through joints-11 KV 3x300 Sqmm Cable | ELECT | labour. | SWR10386 | 3725.45 | EA | 22352.7
288 | 225 | Supply of PSCC Pole 9.1Mtr 280KG | ELECT | supply | SMR25233 | 3109.41 | EA | 699617.25
289 | 80 | Supply of PSCC Pole 8Mtr 140KG | ELECT | supply | SMR25232 | 1580 | EA | 126400
290 | 80 | Supply of 11KV Horizontal Cross Arm | ELECT | supply | SMR25223 | 528 | EA | 42240
291 | 185 | Supply of 33KV V X- Arm with MS Channel 75x40 | ELECT | supply | SMR25219 | 561 | EA | 103785
292 | 185 | Supply of 11KVTop Cleat with Clamps | ELECT | supply | SMR25224 | 178 | SET | 32930
293 | 24 | Supply of 11KV 3x300 Heat Shble O/d End Term Kit | ELECT | supply | SMR25208 | 1372.88 | EA | 32949.12
294 | 6 | Supply of 11KV 3x300 Heat Shble stright through joint Kit | ELECT | supply | SMR25210 | 4110.17 | EA | 24661.02
295 | 500 | Supply of MS Channel 75x40 mm | ELECT | supply | SMR25205 | 58.45 | KG | 29225
296 | 400 | Supply of MS Angle 50x50x6 | ELECT | supply | SMR25206 | 58.15 | KG | 23260
297 | 200 | Supply of Materials -- Supply of MS Flat 50x6 mm | ELECT | supply | SMR12322 | 56.5 | KG | 11300
298 | 6 | Supply of Materials --- Supply of 11 kV 400 A Double break AB switch | ELECT | supply | SMR12317 | 18150 | EA | 108900
Sub Total: | [7 empty] | 17111488.819
Civil labour WBS. No. S-1786-13-07-01-01-001
Sl No | Estimate Quantity | Description of item | Work Type | Item Short Description | APSS / Month Cl.NumberSSR 11 & 12 | Rate (INR) | UOM | AMOUNT
1 | 32 | Leveliing the site by cutting and levelling with the help of JCB including cost,conveyance of all materials,hire chareges etc complete for finished item of work as directed by Engineer-in-charge. | Civil | Labour | SWR34179 | 2165 | Hrs | 69280
2 | 135.61 | Earth work excavation in all type of ordinary soils red earth, Hard gravelly soils, earth mixed with sand and sandy soils etc., in all conditions such as slushy and dry with initial leads and lifts for foundations. | Civil | Labour | SWR33015 | 486 | m3 | 65906.46
3 | 32.45 | Plain Cement concrete PCC (1:4:8) using 40mm HBG metal for foundations and leveling course, including cost and conveyance of all materials, labour all leads and lifts, consolidation and all operations, formwork as required, curing, etc. complete for finished item w | Civil | Labour | SWR33028 | 4786 | m3 | 155305.7
4 | 117.88 | Coursed Rubble stone (CRS) masonry 2nd sort with hard granite stones in cement mortar (1:6) for basement, including cost and conveyance of all materials, labour charges, curing, all leads and lifts, etc, complete for finished item of work. | Civil | Labour | SWR33041 | 4902 | m3 | 577847.76
5 |  | 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge
6 | 3.564 | RCC M20 Grade footing 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33098 | 9537 | m3 | 33989.868
7 | 2.28 | RCC M20 Grade Coloumn . 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33100 | 13286 | m3 | 30292.08
8 | 2.25 | RCC M20 Grade Plinth beams 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33099 | 12408 | m3 | 27918
9 | 3.17 | D) RCC M20 Grade Roof Beams landing beam 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33121 | 12324 | m3 | 39067.08
10 | 0.58 | e)RCC M20 Grade Lintels 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33107 | 13116 | m3 | 7607.28
11 | 2.7 | f) RCC M20 Grade Sunshades 600mm wide and 75mm thick'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33114 | 1379 | m2 | 3723.3
12 | 15.224 | g) RCC M20 Grade Roof Slab for Control Room 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33128 | 10912 | m3 | 166124.288
13 | 3 | Reinforcement steelSupplying, Cutting, bending, binding, placing in position and tying reinforcement steel in all heights including cost and conveyance of steel and binding wire etc,. With all leads and lifts, labour charges, etc., complete for finished item of work. | Civil | Labour | SWR33144 | 70687 | Ton | 212061
14 | 38.36 | Brick masonry in cement mortar CM (1:6) for superstructure using well burnt country made second class bricks of approved quality including cost and conveyance of all materials curing, scaffolding with all leads and lifts in all heights etc., complete for finished item of work | Civil | Labour | SWR33068 | 8291 | m3 | 318042.76
15 | 2.7 | Plain Cement concrete PCC (1:2:4) using 20mm size well graded HBG metal for foundations, including cost, conveyance of all materials,labour all leads and lifts,consolidation and all operations, formwork as required, curing,etc. complete for finished item of work | Civil | Labour | SWR33030 | 6155 | m3 | 16618.5
16 | 606.06 | Plastering with CM 2 coats, 20 mm thick, base coat in CM (1:6), 16 mm thick and top coat in CM (1:4), 4mm thick with Dubara sponze finishing including cost of all materials, seigniorage charges, excluding conveyance charges of materials and including all operational, incidental and labour charges for mixing mortar, laying rendering smooth and thread lining, curing, rounding off junctions of wall and slab etc., complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33163 | 565 | m2 | 342423.9
17 | 349.515 | Painting with two coats of Plastic Emulsn paint over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33356 | 210 | m2 | 73398.15
18 | 200.85 | Painting with two coats of Surya Cem paint over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33329 | 85 | m2 | 17072.25
19 | 3 | Supply and Fixng of MS Name Board including cost & conveyance of all materials,labour charges etc complete for finished item of work. | Civil | Labour | SWR33421 | 4326 | m2 | 12978
20 | 1 | Geophysical Investgation charges for water point by Geologist | Civil | Labour | SWR33608 | 5000 | EA | 5000
21 |  | Drilling of 165mm bore well with machine rig including deployment and hire charges of rig and other machinery and equipment labour charges , measuring the yeild of borewell including cost and conveyance etc complete
22 | 90 | Drill-165mm Bore Well 0 to 90 | Civil | Labour | SWR33609 | 336 | M | 30240
23 | 30 | Drill-165mm Bore Well 90M to 120M | Civil | Labour | SWR34830 | 369 | M | 11070
24 | 30 | Drill-165mm Bore Well 120M to 150M | Civil | Labour | SWR34831 | 394 | M | 11820
25 | 30 | Drill-165mm Bore Well 150M to 180M | Civil | Labour | SWR34832 | 492 | M | 14760
26 | 30 | Drill-165mm Bore Well 180M to 210M | Civil | Labour | SWR34833 | 623 | M | 18690
27 | 30 | Drill-165mm Bore Well 210M to 240M | Civil | Labour | SWR34834 | 754 | M | 22620
28 | 30 | Drill-165mm Bore Well 240M to 270M | Civil | Labour | SWR34835 | 918 | M | 27540
29 | 80 | Drill-165mm Bore Well 270M and above | Civil | Labour | SWR34836 | 1082 | M | 86560
30 | 40 | Supply and fixing of 160mm dia PVC casing of A class 6Kg point pressure including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR33611 | 883 | M | 35320
31 | 1 | Supply and erecting, ISI mark submersible 5.0 HP, Single Phase 30 stages pumpset suitable for 106/156mm dia borewell including cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33640 | 48007 | EA | 48007
32 | 300 | Supply and fixing of HDPE pipe 40mm dia of 16Kg/cm2 including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR34410 | 180 | M | 54000
33 | 1 | Supply and erecting D.O.L Starter 415V , Single phase,50Hz with SS enclouserincluding cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33645 | 7854 | EA | 7854
34 | 310 | Supply of 3 Core 2.5 Sqmm Flat Copper cable of ISI for Submersible Motors of makes Finolex / Polycab / Gold Medal / Million / Payal / Sun Light / Power Flex / Fortune Art | Civil | Labour | SWR33641 | 192 | m | 59520
35 | 71 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-28.60mm OD Pipe - SDR 11 | Civil | Labour | SWR34363 | 410 | m | 29110
36 | 35 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type - 25mm NB Size | Civil | Labour | SWR34346 | 466 | EA | 16310
37 | 839.38 | Supplying and filling the substation site with borrowed gravel, watering, ramming, thoroughly complying with the standard specification. | Civil | Labour | SWR33052 | 309 | m3 | 259368.42
38 | 16.56 | Providing Design R.C.M. drop wall of 25mm thickness with cm 1:3 and 6mm dia MS bars at 150mm both ways and chicken mesh in two coats 20mm thick each plastering including cost and conveyance of all materials with leads and lifts, scaffolding and curing, labo | Civil | Labour | SWR33203 | 3121 | m2 | 51683.76
39 | 12.24 | Supply and fixing of Ms ornamental safety grill of approved design including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33310 | 2990 | m2 | 36597.6
40 | 5.91 | Supply and fixing of doors with the MT Wood frames of the door shall be made well seasoned mt wood of cross section 100x75mm. The shutter shall be made isi mark flushed door with decolam sheets pasted on both sides with PVC beading 40mm width all round.Frame shall be painted with two coats of synthetic enamel paint of approved color over one coat of primer over luppum with spary with 3 no 150mm brass hinges 1 no brass door stoper, 1 no 250mm brass aldrops. 2 no 300 mm aluminium tower bolts, 2 no 150mm brass fancy door handlers, 1 no keyless lockset with cp handel. The quoted rate shall include cost and conveyance of the meterials, fixig, labour carges, tools, handles,locking arrangementts and other fixtures & fittings for finished item work as directed by the Engineer - in- charge. | Civil | Labour | SWR33264 | 7314 | m2 | 43225.74
41 | 128.25 | Raised pointing to the exposed surfaces of CRS masonry in cm 1:3 prop. including cost and conveyance of all materials, labour charges, all leads and lifts curing etc, complete for finished item of work. | Civil | Labour | SWR33184 | 125 | m2 | 16031.25
42 | 8.64 | Supplying and fixing Aluminium sliding windows with grill and fixed glass panels using anodised aluminium extruded sections of mat finish for frames and mullions made from approved aluminium sections 62x32x1.2mm at 0.73kg/Rm providing 5mm plain glass fix | Civil | Labour | SWR33277 | 3623 | m2 | 31302.72
43 | 16.56 | Supply and laying of Ceramic floor over of CM 1:3 20 mm thick including required materials and labour charges etc complete for item of work | Civil | Labour | SWR33224 | 914 | m2 | 15135.84
44 | 121.92 | Flooring with double machine polished and hand cut Tandur blue stone 20mm thick of approved colour, quality and of minimum of 300x300mm size over a bed of cement mortar 1:3 20mm thick including cost of all materials, with all leads and lifts jointing and | Civil | Labour | SWR33219 | 788 | m2 | 96072.96
45 | 6.74 | Supply and fixing of 4" high skirting of shabad stone to the walls including cost and conveyance of all materials, labour etc for finished item of work. | Civil | Labour | SWR33236 | 878 | m2 | 5917.72
46 | 243.69 | Painting with two coats of OBD over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials labour charges etc., complete for finished item of work. | Civil | Labour | SWR33333 | 146 | m2 | 35578.74
47 | 101.17 | Providing impervious coat over RCC roof slab to requried slopes with 20mm thick in CM 1:3 mixed with approved brand of water proffing compound inclding cost and conveyance of all materials, labour charges, curing, rounding off junctions of wall and slab, all leads and lifts, etc . complete for finished item of work as directed by the Engineer - in - charge. | Civil | Labour | SWR33156 | 587 | m2 | 59386.79
48 | 60 | Supply & fixing of 25mm dia 2mm thick suSupply & fixing of 25mm dia 2mm thick surface P.V.C. pipe (ISI MARK) Concealed in wall with all required accessories including masonary work and labour charges etc.complete. | Civil | Labour | SWR33441 | 108 | m | 6480
49 | 1 | Supply & fixing TPN Distribution board w Supply & fixing TPN Distribution board with IP-42 protection (Metal Door)suitable for 3 phase ELCB/RCCB/FP Isolator as incomer and 10kA SP MCBs as out going including internal connection and labour charges for surface / flush mounting etc Complete. | Civil | Labour | SWR33526 | 11353 | EA | 11353
50 | 10 | Supply & fixing of 6A 3 pin wall plug socket with 6A switch control on a common switch board with earth continuity including wire leads,earth connection along with all labour charges etc., complete | Civil | Labour | SWR33468 | 166 | EA | 1660
51 | 6 | Supply & fixing of 16A 3 pin and 6A 3pin plug Flush type socket with indicator lamp and 16Amps fuse unit and 16Amps switch control (5 in one )duly recessed in wall with wooden deep box of 6'' x 8'' x 2 1/2'' size covered with hylam sheet earth connection and all labour charges etc., complete on wall. | Civil | Labour | SWR33470 | 449 | EA | 2694
52 | 24 | Supply and Fixing of modular switch, LP,FP,EFP Wiring with 2 runs of 14/0.3mm (1.0 sq.mm)Fire Retardant (FR) P.V.C. insulated flexible copper cable (ISI MARK) in existing pipe with 6A Flush type Switch,ceiling rose and 3mm thick hylam sheet covering to switch control box including all labour charges etc., complete for light points, bell , fan and exhaust fan points in Non-Residential Buildings. | Civil | Labour | SWR33457 | 676 | EA | 16224
53 | 12 | Supply & Fixing of 28W T5 fluorescent tube. | Civil | Labour | SWR33558 | 148 | EA | 1776
54 | 1 | Supply of 12" (300mm)ISI, 900 RPM Heavy duty exhaust fan with metallic blades with Mark of makes Crompton / Bajaj / Havells / Orient. | Civil | Labour | SWR33571 | 2192 | EA | 2192
55 | 180 | Supply and run of 2 of 22/0.3mm (1.5 sq.mm) (FR) P.V.C. insulated flexible copper cable in existing pipe for mains including all labour charges complete. | Civil | Labour | SWR33496 | 75 | m | 13500
56 | 180 | Supply and run of 2 of 36/0.3mm (2.5 sq.mm) FR P.V.C. insulated flexible copper cable in existing pipe for mains including all labour charges complete. | Civil | Labour | SWR33497 | 103 | m | 18540
57 | 12 | Supply & fixing of batten holder /slanting holder in lieu of ceiling rose of light point complete with all connection and all labour charges with 40W bulb (for new installation). | Civil | Labour | SWR33484 | 141 | EA | 1692
58 | 4 | Supply & fixing of 1200mm (48'') sweep 230v,A.C 50 Hz.Ceiling fan with 3 Blades and double ball bearings with all standared accessories. | Civil | Labour | SWR33563 | 2277 | EA | 9108
59 | 4 | Supply & fixing of Electronic Regulator for ceiling fans 900/1200/1400mm sweep including cost of material, Electrical charges complete for finished item of work | Civil | Labour | SWR33564 | 589 | EA | 2356
60 | 1 | Providing independent EARTHING by excavating a trench to a depth of 2.1M in all solid,as per size specified in the Data,using 40mm dia 'B' class GI pipe of 2.5 Mtrs length with necessary accessories with hume pipe ring duly providing staggered holes including filling with equal proportion of salt and Charcoal in layers and all labour charges etc., compiete for small quarters. | Civil | Labour | SWR33596 | 5345 | EA | 5345
61 | 35 | Supplying, laying, jointing and testing 101.6 mm SWG SP-1 pipes of ISI make conforming to ISI 651 & 4127 with airtight cement joints in CM 1.5:1 prop. Including excavation of trenches and socket pits in any soil (except rock requiring blasting) up to 1524 mm(5'0") depth and refilling with watering and tamping. | Civil | Labour | SWR34281 | 755 | m | 26425
62 | 3 | Constructing 904.0 mm (3#0#) dia brick masonry inspection chamber as per IS - 4111: Part-1:1986 with cement mortar (1:6) prop using 2nd Class Clay Bricks of 225 mm thick from approved source having a minimum crushing strength of 5 N/sq.mm including plastering with cement mortar 1:3 prop; ½# thick both inside and outside fitted with 20# dia RCC manhole covers and frames including excavating pits up to a depth of 904 mm (3'-0") in all sorts of soils (excluding rock) and laying cement concrete (1:4:8) 150 mm thick using 40 mm HBG Metal and P.C.C. 1:2:4 benching and channel 100 mm thick as per Standard specification and including cost and conveyance of all materials like cement, sand, bricks, water etc., to site, cost of seigniorage charges on all materials and all incidental and operational, labour charges like mixing cement mortar, constructing masonry, lift charges, curing etc., complete for finished item of work as per Standard specification. | Civil | Labour | SWR34296 | 8766 | EA | 26298
63 | 4 | Supply & fixing of 110 mm dia - Door Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34381 | 128 | EA | 512
64 | 4 | Supply & fixing of 110 mm dia - Plain Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34380 | 100 | EA | 400
65 | 12 | Supply & fixing of 110 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand | Civil | Labour | SWR34377 | 462 | m | 5544
66 | 18 | Supply & fixing of 90 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand | Civil | Labour | SWR34378 | 410 | m | 7380
67 | 3 | Supplying & fixing 150 mm x 100 mm SWG gully traps conforming to ISI 651 & 4127 with C.I Grating & Cost. Brick masonry in CM 1:6 prop. Intermediate chamber and fitted with 304.8 mm x 288.6mm (12"x9") C.I Frame and hinged cover | Civil | Labour | SWR34286 | 767 | EA | 2301
68 | 1 | Supplying and Fixing of European Water Closet of 1st Quality | Civil | Labour | SWR34312 | 2228 | EA | 2228
69 | 6 | Supply & fixing 15 mm angle stop cock Indian make 400 grams Seiko/ Senior/ Nice/ Senior/ Nice or equivalent | Civil | Labour | SWR34328 | 721 | EA | 4326
70 | 4 | S&F 15 mm N.P bib tap Indian make 400 grams full turn Seiko/ Senior/ Nice or equivalent | Civil | Labour | SWR34329 | 296 | EA | 1184
71 | 1 | Supplying & Fixing Indian make Flat Back Wash Hand Basin (HSW/Parryware/ Neycer) 1st quality conforming to IS:2556-Part-4:1972 with waste fittings like rubber plug, chain, 32 mm nominal size C.P. Fitting with parallel pipe thread conforming to IS:2963-1979 and fitted with 15 mm nominal bore Chromium Plated Pillar Tap of 1st quality Indian make 400 grams Seiko/ Senior/ Nice/ Esso or equivalent complete with standard CI brackets including wooden block: 550 x 400 mm - Single C.P. Pillar cock | Civil | Labour | SWR34316 | 1717 | EA | 1717
72 | 2 | Supply & fixing 38.1 mm C.P waste coupling Half or Full Thread 1st Quality Indian make Parryware or equivalent | Civil | Labour | SWR34428 | 309 | EA | 618
73 | 2 | Supply & fixing of 4" (101.6 mm ) Nahany Trap ( Without Jali with inlet)UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34387 | 134 | EA | 268
74 | 1000 | Providing & Placing on Terrace (at all floor levels) polyethylene water storage tank with Double layer approved brand & manufacture with cover and suitable locking arrangement & making necessary holes for inlet & outlets and over flow pipes but with NECESSARY fittings & base support for tanks | Civil | Labour | SWR34375 | 10 | L | 10000
75 | 2 | Supply & fixing 31.75 mm dia PVC flexible waste pipe of 914.4 mm length of Ist quality | Civil | Labour | SWR34426 | 33 | EA | 66
76 | 45 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)- 15.90mm OD Pipe - SDR 11 | Civil | Labour | SWR34361 | 239 | m | 10755
77 | 200 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-22.20mm OD Pipe - SDR 11 | Civil | Labour | SWR34362 | 313 | m | 62600
78 | 4 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type -20mm NB Size | Civil | Labour | SWR34345 | 331 | EA | 1324
79 | 1 | Supply & fixing 25.4 mm dia & 609.6 mm long aluminium anodized towel rod with brackets and aluminium screws | Civil | Labour | SWR34430 | 489 | EA | 489
80 | 36 | Plain Cement concrete PCC (1:3:6) using 40mm HBG metal for foundations and leveling course, including cost and conveyance of all materials, labour all leads and lifts, consolidation and all operations, formwork as required, curing, etc. complete for finished item w | Civil | Labour | SWR33029 | 5076 | m3 | 182736
81 | 120 | Supply&Fabrication and fixing of Welded wire mesh ( 2" x 2") of 3mm dia. with ISMC (75x40x4.4mm) and Pheriperal frame of ISA(35x35x3mm) incldg cost& conveyance painting with synthetic enamil paint two coats over a coat of red oxide primer etc complete for finished item of work.. | Civil | Labour | SWR33403 | 2310 | m2 | 277200
82 | 1 | Providing Consultancy services for arranging contour surveying with total station incuding preparation of boundary and contour levels with 2 Nos. Hard copies and soft copies complete for finished items of work | Civil | Labour | SWR33427 | 5665 | EA | 5665
83 | 222.2468 | Seigniorage Charges - Sand | Civil | Labour | SWR34470 | 40 | m3 | 8889.873
84 | 725.7496 | Seigniorage Charges - Metal | Civil | Labour | SWR34471 | 97.5 | m3 | 70760.585
85 | 839.38 | Seigniorage Charges - Gravel | Civil | Labour | SWR34472 | 30 | m3 | 25181.4
86 | 60 | Supply and fixing of RCC fencing poles of size 0.1mx0.1mx1.8m (security fencing of sub station), including cost and conveyance of all labour, materials,and hire chareges etc complete for finished item of work. | Civil | Labour | Swr33405 | 1444 | EA | 86640
87 | 1200 | Supply and fixing of galvanised barded wire (1 horizantal & 2 cross strands. including cost and conveyance of all labour, materials,and hire chareges etc complete for finished item of work. | Civil | Labour | Swr33408 | 16 | m | 19200
Civil total | [7 empty] | 4232006.774
Total elec+civil | [7 empty] | 21343495.593

## 3. Kings Colony
Name of the work: Erection of 33/11 kV SS Kings Colony outdoor sub-station in Rajendranagar (M) with 2x8 MVA PTRs and connected 33kV and 11kV Lines at kings colony, kattedan in Rajendranagar (M) of ECGH Division /Masterplan/RR Circle
WBS No. S-1787-13-03-02-01-001
Sl No | Estimate Quantity | Description of item | Work Type | Item Short Description | APSS / Month Cl.NumberSSR 11 & 12 | Rate (INR) | UOM | AMOUNT
1 | 16 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | ELEC | Labour | SWR11039 | 928 | EA | 14848
2 | 5.76 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ELEC | Labour | SWR10868 | 6852 | TO | 39467.52
3 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELEC | supply | SMR40009 | 2181 | TO | 12562.56
4 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELEC | labour | SWR10877 | 851 | TO | 4901.76
5 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELEC | supply | SMR40010 | 1293 | TO | 7447.68
6 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELEC | labour | SWR10879 | 482 | TO | 2776.32
7 | 5.76 | Fabrication & erection of Channels-Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ELEC | labour | SWR10867 | 1470 | TO | 8467.2
8 | 16 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-R.S. Joists 150 x 150 mm | ELEC | labour | SWR10348 | 1952.61 | EA | 31241.76
9 | 17.758 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 116829.882
10 | 9.24 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ELEC | labour | SWR10862 | 373 | M2 | 3446.52
11 | 16 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | ELEC | labour | SWR11089 | 48 | EA | 768
12 | 4 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-8.0Mtrs PSCC Poles 0.76 M x 0.76M x 1.52M (2.6" x 2.6" x 5.0') 0.88 cum | ELEC | labour | SWR11037 | 793 | EA | 3172
13 | 1 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ELEC | Labour | SWR10868 | 6852 | TO | 6852
14 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELEC | supply | SMR40009 | 2181 | TO | 2181
15 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELEC | labour | SWR10877 | 851 | TO | 851
16 | 1 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELEC | supply | SMR40010 | 1293 | TO | 1293
17 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELEC | labour | SWR10879 | 482 | TO | 482
18 | 1 | Fabrication & erection of Channels-Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ELEC | labour | SWR10867 | 1470 | TO | 1470
19 | 4 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Box pole 12 Mtr | ELEC | labour | SWR11267 | 3901.37 | EA | 15605.48
20 | 2.65 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 17434.35
21 | 2.31 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ELEC | labour | SWR10862 | 373 | M2 | 861.63
22 | 4 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | ELEC | labour | SWR11089 | 48 | EA | 192
23 | 5.063 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ELEC | labour | SWR10868 | 6852 | TO | 34691.676
24 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELEC | supply | SMR40009 | 2181 | TO | 11042.403
25 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELEC | labour | SWR10877 | 851 | TO | 4308.613
26 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELEC | labour | SMR40010 | 1293 | TO | 6546.459
27 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELEC | labour | SWR10879 | 482 | TO | 2440.366
28 | 5.063 | Fabrication & erection of Channels-Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ELEC | labour | SWR10867 | 1470 | TO | 7442.61
29 | 13 | Erection of AB Switch and aligment complete Erection of 33 KV AB Switch including alignment and earthing | ELEC | labour | SWR10392 | 4500 | EA | 58500
30 | 34 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Note:-The requirement of 2nd coat is to be justified by the concerned Divisional Engineer /Executive Engineer before execution of this work Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | ELEC | labour | SWR10881 | 142 | EA | 4828
31 | 34 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | ELEC | labour | SWR12331 | 146.63 | EA | 4985.42
32 | 6 | Loading of 33 KV CTs/ PTs | ELEC | labour | SWR10200 | 165 | EA | 990
33 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
34 | 6 | Un loading of 33 KV CTs/ PTs | ELEC | labour | SWR10518 | 128 | EA | 768
35 | 2 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33kv single phase PT s | ELEC | labour | SWR10401 | 1079 | SET | 2158
36 | 12 | Loading of 33 KV, 10 KA LAs Station typ | ELEC | labour | SWR10266 | 41 | EA | 492
37 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
38 | 12 | Un loading of 33 KV, 10 KA LAs Station type | ELEC | labour | SWR10584 | 35 | EA | 420
39 | 4 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33 KV LAS station/Line type including earthing | ELEC | labour | SWR10396 | 880 | SET | 3520
40 | 2 | Loading of 33 KV VCBs along with Panel boards | ELEC | labour | SWR10198 | 1024 | EA | 2048
41 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
42 | 2 | Un loading of 33 KV VCBs along with Panel boards | ELEC | labour | SWR10516 | 1044.48 | EA | 2088.96
43 | 12.584 | Excavate-Pit for 33KV VCB | ELEC | labour | SWR23224 | 331 | M3 | 4165.304
44 | 14.52 | Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x 1.8 x 0.75 cum for VCB Plinth | ELEC | labour | SWR20685 | 5160 | M3 | 74923.2
45 | 2 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33 KV VCB with Control Panel | ELEC | labour | SWR10460 | 12500 | EA | 25000
46 | 2 | Loading and unloading of PTR on constructed plinth-Loading of 8MVA PTR | ELEC | labour | SWR10613 | 5805.84 | EA | 11611.68
47 | 2 | Transport of Power transformers (0 to 100 KM) from one place to another place in GHMC Area.(excluding of loading & unloading )-8MVA power transformer | ELEC | labour | SWR10854 | 21945 | EA | 43890
48 | 2 | Loading and unloading of PTR on constructed plinth-Unloading of 8MVA PTR | ELEC | labour | SWR10627 | 5805.84 | EA | 11611.68
49 | 700 | S/o rail poles 90/105lb (250x2N) | ELEC | supply | SMR22718 | 47.27 | KG | 33089
50 | 14 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Rail pole 90 lbs | ELEC | labour | SWR10344 | 3510 | EA | 49140
51 | 2 | Erection of PTR on constructed plinth-Erection of 8 MVA PTR. | ELEC | labour | SWR21321 | 49480.2 | EA | 98960.4
52 | 0.436 | Extention of 33KV Bay at 132/33KV Sub-station-Zebra condutor | ELEC | supply | SMR24910 | 299369 | KM | 130524.884
53 | 30 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing | ELEC | supply | SMR11915 | 2055 | SET | 61650
54 | 30 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of I-Bolts | ELEC | supply | SMR22473 | 294 | EA | 8820
55 | 45 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 "to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating . Sup T clamp LM6 Al alloy of 12 mm, 800 A | ELEC | labour | SMR40011 | 299 | EA | 13455
56 | 6 | Bus stringing Hoisting of Insulators and hardware, stretching the conductor and stringing of 33 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bussection of 4.5mt) Hoisting post ins&hrd wr 1panther 33kv | ELEC | labour | SWR21240 | 781 | EA | 4686
57 | 84 | Stringing of bus with panther conductor including jumpering etc., complete to all the equipment in SS fixing to all clamps and equipment.(3 Conductors) | ELEC | labour | SWR10404 | 327.68 | M | 27525.12
58 | 30 | Bus stringing Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | ELEC | labour | SWR10884 | 224 | EA | 6720
59 | 75 | Labour for Fixing of all types of clamps | ELEC | labour | SWR10917 | 65 | EA | 4875
60 | 25 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | ELEC | labour | SWR11039 | 928 | EA | 23200
61 | 8.68 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ELEC | labour | SWR10868 | 6852 | TO | 59475.36
62 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELEC | supply | SMR40009 | 2181 | TO | 18931.08
63 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELEC | labour | SWR10877 | 851 | TO | 7386.68
64 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELEC | supply | SMR40010 | 1293 | TO | 11223.24
65 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELEC | labour | SWR10879 | 482 | TO | 4183.76
66 | 8.68 | Fabrication & erection of Channels-Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ELEC | labour | SWR10867 | 1470 | TO | 12759.6
67 | 25 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-R.S. Joists 150 x 150 mm | ELEC | labour | SWR10348 | 1952.61 | EA | 48815.25
68 | 27.75 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 182567.25
69 | 17.91 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ELEC | labour | SWR10862 | 373 | M2 | 6680.43
70 | 25 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | ELEC | labour | SWR11089 | 48 | EA | 1200
71 | 4.642 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ELEC | labour | SWR10868 | 6852 | TO | 31806.984
72 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELEC | supply | SMR40009 | 2181 | TO | 10124.202
73 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELEC | labour | SWR10877 | 851 | TO | 3950.342
74 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELEC | supply | SMR40010 | 1293 | TO | 6002.106
75 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELEC | labour | SWR10879 | 482 | TO | 2237.444
76 | 4.642 | Fabrication & erection of Channels-Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ELEC | labour | SWR10867 | 1470 | TO | 6823.74
77 | 17 | Erection of AB Switch and aligment complete-Erection of 11KV 800A double throw AB Switches | ELEC | labour | SWR21277 | 3500 | EA | 59500
78 | 3 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | ELEC | labour | SWR10393 | 3200 | EA | 9600
79 | 2 | Loading of 11 KV CT - PT Sets | ELEC | labour | SWR10201 | 190 | EA | 380
80 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
81 | 2 | Un loading of 11 KV CT - PT Sets | ELEC | labour | SWR10519 | 101 | EA | 202
82 | 2 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc-Erection of 11 KV three phase PTs | ELEC | labour | SWR10402 | 800 | SET | 1600
83 | 24 | Loading of 11 KV, 10 KA LAs Station type | ELEC | labour | SWR10264 | 32 | EA | 768
84 | 2 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 6599.4
85 | 24 | Un loading of 11 KV, 10 KA LAs Station type | ELEC | labour | SWR10582 | 32 | EA | 768
86 | 2 | Erection of 11 KV LAS station type including earthing | ELEC | labour | SWR10397 | 559 | SET | 1118
87 | 6 | Erection of 11 KV LAS line type including earthing | ELEC | labour | SWR10398 | 505 | SET | 3030
88 | 8 | Loading of 11 KV VCBs along with Panel boards | ELEC | labour | SWR10199 | 1024 | EA | 8192
89 | 4 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 13198.8
90 | 8 | Un Loading of 11 KV VCBs along with Panel boards | ELEC | labour | SWR10517 | 1044.48 | EA | 8355.84
91 | 41.6 | Excavate-Pit for 33KV VCB | ELEC | labour | SWR23224 | 331 | M3 | 13769.6
92 | 48 | Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x 1.8 x 0.75 cum for VCB Plinth | ELEC | labour | SWR20685 | 5160 | M3 | 247680
93 | 8 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc-Erection of 11 KV VCB with Control Panel | ELEC | labour | SWR10461 | 12000 | EA | 96000
94 | 12 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing | ELEC | supply | SMR11915 | 2055 | SET | 24660
95 | 12 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of I-Bolts | ELEC | supply | SMR22473 | 294 | EA | 3528
96 | 45 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 "to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating . Sup T clamp LM6 Al alloy of 12 mm, 800 A | ELEC | supply | SMR40011 | 299 | EA | 13455
97 | 2 | Bus Stringing -Hoisting of Insulators and hardware, stretching the conductor and stringing of 11 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 3.5mt) Hoisting post ins&hrd wr 1panther 11kv | ELEC | labour | SWR21241 | 507 | EA | 1014
98 | 63 | Stringing of bus with panther conductor including jumpering etc., complete to all the equipment in SS fixing to all clamps and equipment.(3 Conductors) | ELEC | labour | SWR10404 | 327.68 | M | 20643.84
99 | 45 | Bus stringing Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | ELEC | labour | SWR10884 | 224 | EA | 10080
100 | 57 | Labour for Fixing of all types of clamps | ELEC | labour | SWR10917 | 65 | EA | 3705
101 | 584 | Laying of earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication 75x 8mm MS Flat / GI Flat. Laying of earth mat,excavation 75x 8mm | ELEC | labour | SWR10920 | 65 | RMT | 37960
102 | 1010 | Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) Earthing for raisers of SS Flat 50x6 mm. | ELEC | labour | SWR10919 | 41 | RMT | 41410
103 | 36 | Supply of earthing pipe with materials -Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | ELEC | supply | SMR11482 | 3486 | EA | 125496
104 | 36 | Providing of Earthing-Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | ELEC | labour | SWR10357 | 1234.2 | EA | 44431.2
105 | 36 | Providing of RCC collar to earth pit-Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINES-Providing of RCC collar | ELEC | labour | SWR10359 | 386 | EA | 13896
106 | 2 | Supply of Copper Flexible jumper with 75 X 8 of length 250 mm at neutral of Power tranformer end and 50 X 6 of length 50mm two Nos at double neutral end duly brasing with flexible jumper of capacity of 5kA/3 sec for power transformer neutral. SupCU Flexi jumper for Power T/F Neutral | ELEC | supply | SMR40033 | 4725 | EA | 9450
107 | 2 | Providing of earthing with various types of earth electrodes-Providing of double earthing for neutral with flexible copper jumpers including arrangement by fixing M.S.Channel 100x50mm. | ELEC | labour | SWR11892 | 1323 | EA | 2646
108 | 4 | Loading of LT AB Cable 3X16+25 Sqmm | ELEC | labour | SWR11702 | 200 | DR | 800
109 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
110 | 4 | Un loading of LT AB Cable 3X16+25 Sqmm | ELEC | labour | SWR11713 | 204 | DR | 816
111 | 80 | Providing of control cable trench as per DATA-XII | ELEC | labour | SWR22093 | 3148 | RMT | 251840
112 | 3074 | Control Cable-Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends . Lay-4C/10C 2.5Sqmm Control Cable | ELEC | labour | SWR11879 | 27 | M | 82998
113 | 270 | Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per specification (including cost of ferrules, lugs and glands) | ELEC | labour | SWR12510 | 27 | EA | 7290
114 | 4 | Marshalling Box Supply of FRP PT Marshalling Box | ELEC | supply | SMR40048 | 4463 | EA | 17852
115 | 4 | Marshalling Box Erection of Marshalling boxes | ELEC | labour | SWR10940 | 374.85 | EA | 1499.4
116 | 1 | Loading of 220 V Batterry with charger | ELEC | labour | SWR11166 | 1612 | SET | 1612
117 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
118 | 1 | Un loading of 220 V Batterry with charger | ELEC | labour | SWR11147 | 1024 | SET | 1024
119 | 1 | Batteries-Erection of 220 V, 200 AH battery in complete shape fit for charging . Conventional lead acid | ELEC | labour | SWR12350 | 7666 | EA | 7666
120 | 1 | Control Panels -Supply of DC Annunciation & relay panel for 10 feeder panel including the cost of LED Indiacation lamps, VAA auxilairy relays, Electronic Hooters complete as per specification. | ELEC | supply | SMR40044 | 42500 | EA | 42500
121 | 1 | Control Panels -Supply of AC Supply panel inluding providing of changeover switch, SFU, metering unit, 32 A three phase MCB, 16 A Single phase MCB complete as per specification. Supply of AC Supply panel complete | ELEC | supply | SMR40045 | 42000 | EA | 42000
122 | 2 | Fixing of AC/DC Panel and giving Connections to the protection equipment and Metering circuits as per the specification and standards. The 3 1/2 core 25 Sqmm power cable required from distribution box to AC/DC panel in the control room is also to be supply | ELEC | labour | SWR20025 | 7871.85 | SET | 15743.7
123 | 8 | Yard lightning-Supply of stepped tubular poles single way made of steel of length 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9 mm, 2.1 mtrs with outer dia 76.1 mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79 kgf as per IS 2713 | ELEC | supply | SMR40051 | 13913 | EA | 111304
124 | 8 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE/CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA /OSRAM /SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty S-90W LED fixture set | ELEC | labour | SMR11594 | 8200 | EA | 65600
125 | 8 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | ELEC | labour | SWR11039 | 928 | EA | 7424
126 | 8 | Erection of tubular poles | ELEC | labour | SWR10955 | 1379 | EA | 11032
127 | 5.27 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 34671.33
128 | 8 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE/CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA /OSRAM /SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty. Fixing of Metal halide lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5 GI pipe complete Fixing of LED/Metal halide complete. | ELEC | labour | SWR10956 | 1268 | EA | 10144
129 | 45 | Supply of HBG metal-Supply & spreading of 20mm machine crushed metal (HBG) including cost of conveneyance of all materials, labour charges etc complete for finished item of work and directed by the engineer incharge | ELEC | labour | SWR10860 | 2113 | M3 | 95085
130 | 2 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M Ex of Hard pit w/o blast 0.75X0.9X1.95M | ELEC | labour | SWR11040 | 990.68 | EA | 1981.36
131 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELEC | Supply | SMR40009 | 2181 | TO | 1635.75
132 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELEC | labour | SWR10877 | 851 | TO | 638.25
133 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELEC | Supply | SMR40010 | 1293 | TO | 969.75
134 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELEC | labour | SWR10879 | 482 | TO | 361.5
135 | 1 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Box pole 12 Mtr | ELEC | labour | SWR11267 | 3901.37 | EA | 3901.37
136 | 2.22 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 14605.38
137 | 1.16 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ELEC | labour | SWR10862 | 373 | M2 | 432.68
138 | 2 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | ELEC | labour | SWR11089 | 48 | EA | 96
139 | 1 | Construction of DTR Plinth-RCC Column type DTR Plinth of size 1'X1'X10',topslab 4'x4'x6" & beam size 4'X8'X8" upto 160KVA | ELEC | labour | SWR21843 | 25967.57 | EA | 25967.57
140 | 1 | Loading of 50,63, 75 & 100 KVA DTR | ELEC | labour | SWR10195 | 350 | EA | 350
141 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
142 | 1 | Un loading of 50,63, 75 & 100 KVA DTR | ELEC | labour | SWR10513 | 280 | EA | 280
143 | 1 | Erection of DTR's including loading and Unloading DTR on the Structure/Plinth etc-Erection of 3 Phase DTRs 63,75 & 100 KVA | ELEC | labour | SWR20905 | 1650 | EA | 1650
144 | 1 | Erection of AB Switch and aligment complete Erection of 11KV 200A TT type AB Switch including fixing of cross angles and alignment complete | ELEC | labour | SWR20102 | 1813.49 | EA | 1813.49
145 | 1 | Erect. of 11kv HG Fuseset incl earthing | ELEC | labour | SWR10395 | 740.52 | SET | 740.52
146 | 40 | Excavation & laying of UG Cable in Single Run Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.-In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road-11KV 3x185 Sqmm Cable | ELEC | labour | SWR11920 | 465.46 | M | 18618.4
147 | 20 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-11 KV 3x185 Sqmm Cable | ELEC | labour | SWR11956 | 126.23 | M | 2524.6
148 | 2 | Making of Outdoor/Indoor End Termination Making 11 KV 3x185 Sqmm Cable Out Door/Indoor end termination | ELEC | labour | SWR10390 | 2370.63 | EA | 4741.26
149 | 1 | Erection of LT distribution box including laying of LT cable from distribution box to LT OH line and DTR to distribution box including earthing of distribution box and crimping of lugs connecting of jumpers etc | ELEC | labour | SWR10674 | 1594.67 | EA | 1594.67
150 | 85 | LAYING OF 33KV, 11KV UG CABLE Excavation & laying of UG Cable in Single Run Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road-LT 3 1/2 x 185 Sqmm Cable | ELEC | labour | SWR11923 | 377.63 | M | 32098.55
151 | 15 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-LT 3 1/2 x 185 Sqmm Cable | ELEC | labour | SWR11959 | 85.43 | M | 1281.45
152 | 2 | UG Cables Joints :-Making of Outdoor/Indoor End Termination -Supply & fixing of Oout Door/Indoor end termination LT 3 1/2 x 185 Sqmm Cable | ELEC | labour | SWR10765 | 968.9 | EA | 1937.8
153 | 1 | Supply and fixing of Substation board of size 3'x2.5' indicating the layout of switchyard Sup &fix of board ind Switchyard layout | ELEC | labour | SWR20032 | 1654 | EA | 1654
154 | 1 | Supply and fixing of safety instructions/Substation operation instruction board. Sup& fix safety inst/SS Op. inst board | ELEC | labour | SWR22090 | 2205 | EA | 2205
155 | 750 | Control Panels Supplying & fabrication erection of 6mm Checkerd plates as per the field conditions Supply,fabricati of 6mm Checkerd plates | ELEC | Labour | SWR10873 | 83 | KG | 62250
156 | 1 | T & P Supply of Wall clock standard make | ELEC | Supply | SMR40059 | 578 | EA | 578
157 | 1 | S-10ft Aluminium Ladder | ELEC | Supply | SMR12378 | 1654 | EA | 1654
158 | 1 | Sup Alluminium Ladder for indoor works | ELEC | Supply | SMR40062 | 4410 | EA | 4410
159 | 30 | T & P Painting of Name Plates for any equipmen | ELEC | labour | SWR10963 | 122 | EA | 3660
160 | 1 | T & P Supply of Taparia Tool kit of Size 20”x10”x15” with tier arrangements Tool box with locking arrangement & key containing (1) Double Ended fix Spanner sets, (Ribbed) 6 x 7, 8 x 9, 10 x 11, 12 x 13, 14 x 15, 16 x 17, 18 x19, 20 x 22, 21 x 23, 24 x 27, 25 x28, 30 x 32, (2) Double Ended Ring Spanners sets, 6 x 7 , 8 x 9, 10 x 11, 12 x 13, 14 x 15. 16 x 17 , 18+ x 19, 20 x 22 , 21 x 23, 24 x 27, 25 x28, 30 x 32 mm, (3) Adjustable Spanner 305 mm length least maximum opening 35mm chrome, (4) Pipe Wrench Length 350 mm 14”, (5) Soft faced Hammer with suitable handle 2 lb, (6) Hacksaw frame with metal handle heavy duty for 12" hacksaw blade with High Speed blade, (7) Insulated Screw drivers Transparent Green Handle Set Length 6”, 8” & 12”, (8) Star Screw Driver Transparent Green Handle Length 6”, (9) Insulated Wire Cutter, (10) Insulated Cutting Plier Length 8” with cable stripper insulated with thick C. A. sleeve confirming to IS: 4378 - 1990, (11) Long Nose Plier insulated with thick C.A. sleeve generally confirming to IS:3552-1989, (12) Tester type screw driver (special with neon bulb) generally confirm to IS: 5579- 1985 Grade:II handle yellow/ green colour overall length 130 mm, (13) Insulated Crimping Plier of all Taparia make. SupTaparia Tool kit complete as per Spec | ELEC | Supply | SMR40063 | 4925 | SET | 4925
161 | 1 | T & P Sup Rechargeable LED torch light of Standard make | ELEC | Supply | SMR40064 | 1733 | EA | 1733
162 | 1 | T & P-Steel almarah(61/2 X 3ft) Godrej | ELEC | Supply | SMR40061 | 9818 | EA | 9818
163 | 1 | T & P-Table (3x6ft) Godrej | ELEC | Supply | SMR40057 | 6050 | EA | 6050
164 | 4 | T & P-S type chairs (Godrej) | ELEC | Supply | SMR40058 | 924 | EA | 3696
165 | 1 | T & P Sup Angle racks(18x36.6inches) Godrej | ELEC | Supply | SMR40060 | 1733 | EA | 1733
166 | 1 | T & P Supply of Hack saw (12 inches) | ELEC | Supply | SMR40065 | 289 | EA | 289
167 | 4 | Sup Earth Rods (8ft) Screw & clamp type | ELEC | Supply | SMR40066 | 578 | EA | 2312
168 | 2 | Supply of Hand Gloves | ELEC | Supply | SMR40067 | 289 | SET | 578
169 | 12 | SupRubber mats( 6'x3')size fo indoorSS | ELEC | Supply | SMR40068 | 1386 | EA | 16632
170 | 1 | Biometric Time attendence System & Telecom Sup Stand basic cell phone with charger | ELEC | Supply | SMR40069 | 1386 | EA | 1386
171 | 14 | Supply of Danger boards with clamps | ELEC | Supply | SMR40070 | 116 | EA | 1624
172 | 2 | Supply of Materials -Fire bucket stand with 3 buckets (8 -10 ltr capacity) | ELEC | Supply | SMR40088 | 1386 | SET | 2772
173 | 2 | Room fire extinguisher (2 ltrs capacity) for control room | ELEC | Supply | SMR40089 | 4620 | EA | 9240
174 | 4 | Sup TrollyMounted Co2 (6.5Kgs) Cylinders(IS-2878) | ELEC | Supply | SMR40087 | 9240 | EA | 36960
175 | 6 | Supply of Safety Helmet of standard make | ELEC | Supply | SMR40071 | 231 | EA | 1386
176 | 8 | Supply of LC Boards | ELEC | Supply | SMR40072 | 116 | EA | 928
177 | 4 | Supply of Gum Boots(Pairs) | ELEC | Supply | SMR40073 | 693 | EA | 2772
178 | 1 | Supply of 5000v megger | ELEC | Supply | SMR40074 | 13860 | EA | 13860
179 | 1 | Supply of Earth megger (1000v) | ELEC | Supply | SMR40075 | 8085 | EA | 8085
180 | 1 | Supply of Digital clamp meter. | ELEC | Supply | SMR40076 | 2888 | EA | 2888
181 | 1 | Name board of the 33/11kV Sub-Station(As per Standard Specification) Sup 33/11kv S.S Permanent name board | ELEC | Supply | SMR40086 | 10238 | EA | 10238
182 | 800 | Supply of Hot dip galvanized/zinc coated bolts & nuts including spring washers, pack washers and flat washers etc. | ELEC | Supply | SMR12488 | 90 | KG | 72000
183 | 2 | Fabrication of poles-Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | ELEC | labour | SWR10642 | 512.55 | EA | 1025.1
184 | 1 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-RS Joists 150x75/175 x 85 mm | ELEC | labour | SWR10346 | 1934 | EA | 1934
185 | 5760 | S-Supply of RS Joist Grider Pole (150x150mm) | ELEC | Supply | SMR12302 | 59.25 | KG | 341280
186 | 1000 | S-Supply of RS Joist Pole (175x85mm) | ELEC | Supply | SMR12303 | 60.75 | KG | 60750
187 | 5063 | S- Supply of MS Channel 100x50mm | ELEC | Supply | SMR22745 | 57.45 | KGS | 290869.35
188 | 13 | S-Supply of 33KV 800A DB Break AB Switch | ELEC | Supply | SMR12315 | 40658.78 | EA | 528564.14
189 | 8680 | S-Supply of RS Joist Grider Pole (150x150mm) | ELEC | Supply | SMR12302 | 59.25 | KG | 514290
190 | 4642 | S- Supply of MS Channel 100x50mm | ELEC | Supply | SMR22745 | 57.45 | KGS | 266682.9
191 | 17 | S-Supply of 11KV 800A DB Break AB Switch | ELEC | Supply | SMR12316 | 30847.46 | EA | 524406.82
192 | 3 | S-Supply of 11KV 400A DB Break AB Switch | ELEC | Supply | SMR12317 | 18150 | EA | 54450
193 | 3045 | S-Supply of MS Flat 75x8mm | ELEC | Supply | SMR12321 | 56.42 | KG | 171798.9
194 | 2666 | S-Supply of MS Flat 50x6mm | ELEC | Supply | SMR12322 | 56.5 | KG | 150629
195 | 750 | S-Supply of RS Joist Pole (175x85mm) | ELEC | Supply | SMR12303 | 60.75 | KG | 45562.5
196 | 1 | S-Supply of 11KV 200A Tilting Type AB Switch | ELEC | Supply | SMR12318 | 8991 | EA | 8991
197 | 1 | S-Supply of 11KV HG FuseSet for StationTransformer | ELEC | Supply | SMR12324 | 1974 | EA | 1974
198 | 1 | S-Supply of LT Distribution Box (SMC) | ELEC | Supply | SMR25200 | 7797 | EA | 7797
199 | 2 | S-Supply of 11KV 3x185 Heat Shble O/d End Term Kit | ELEC | Supply | SMR25201 | 1182.97 | EA | 2365.94
200 | 40 | S-Supply of LT XLPE Cable 1C 150 sqmm | ELEC | Supply | SMR25203 | 114.83 | M | 4593.2
201 | 100 | Supply of LT XLPE Cable 31/2C185sqmm. | ELEC | Supply | SMR25204 | 547 | M | 54700
202 | 9 | survey line&cabl inc peg mark&tree clear |  | Labour | SWR22092 | 765 |  | 6885
203 | 9 | Paving out and stringing of conductor by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location-100 Sqmm Single Circuit (3 Conductors) |  | Labour | SWR10366 | 13856.7 |  | 124710.3
204 | 180 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M Ex of Hard pit w/o blast 0.75X0.9X1.95M | ELEC | labour | SWR11040 | 990.68 | EA | 178322.4
205 | 180 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Errection of 11 M long PSCC pole | ELEC | labour | SWR10978 | 4336.85 | EA | 780633
206 | 62.88 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 413687.52
207 | 180 | Painting of poles-Numbering of poles incl. cost of paint | ELEC | labour | SWR10378 | 32 | EA | 5760
208 | 50 | Excavation of pits in all soils except hard rock requiring blasting-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") 1.05 cum | ELEC | labour | SWR10107 | 700 | EA | 35000
209 | 50 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Erec of 9.1 Mts PSCC poles for stuts | ELEC | labour | SWR11083 | 2400 | EA | 120000
210 | 26.25 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 172698.75
211 | 30 | Formation of Cut points - Formation of Cut point for 11 KV Single Circuit line excluding pole erection and stays Formatn of Horiz Cut point for 11KV line | ELEC | labour | SWR10653 | 1435.81 | EA | 43074.3
212 | 300 | Supply of earthing pipe with materials S-GI Bolts & Nuts,Washers etc., | ELEC | supply | SMR11488 | 117.5 | KG | 35250
213 | 5 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 50 Km and upto 80 Km with Lorry for each trip | ELEC | labour | SWR11864 | 5290.74 | EA | 26453.7
214 | 9 | LOADING of Conductor drums | ELEC | labour | SWR10191 | 202 | EA | 1818
215 | 9 | UNLOADING of Conductor drums | ELEC | labour | SWR10509 | 100 | EA | 900
216 | 60 | Loading of 33 KV Pin insulators | ELEC | labour | SWR10211 | 3 | CRT | 180
217 | 60 | Un loading of 33 KV Pin insulators | ELEC | labour | SWR10529 | 3 | CRT | 180
218 | 30 | Loading of 33 KV Metal parts | ELEC | labour | SWR10618 | 65 | BAG | 1950
219 | 30 | Un loading of 33 KV Metal parts | ELEC | labour | SWR10632 | 65 | BAG | 1950
220 | 440 | Excavation & laying of UG Cable (Double Run) Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, Along the CC / BT multi layer road requiring compressor-33 KV 3x400 Sqmm Cable | ELEC | labour | SWR11980 | 1388.84 | M | 611089.6
221 | 440 | Laying of 2nd cable in excavated trench | ELEC | labour | SWR10988 | 204.1 | M | 89804
222 | 60 | Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-33 KV 3x400 Sqmm Cable | ELEC | labour | SWR12004 | 323.85 | M | 19431
223 | 12 | Cost of Pipes and slabs-Supply of 6" B class GI pipe | ELEC | supply | SMR40081 | 1044 | M | 12528
224 | 30 | Cost of Pipes and slabs-Supply of 250 mm Hume pipe of class NP3 with compresive strength of 35N/mm2 for 28 days curing,barewall thickness of 30mm,1.25kG linear/meter and withstanding capability of 22.50KN/linear meter as per IS 458-1993. | ELEC | supply | SMR40077 | 363 | M | 10890
225 | 4 | Cost of Pipes and slabs-Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters , CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | ELEC | supply | SMR40085 | 484 | EA | 1936
226 | 4 | Load-11/33KV XLPE UG Cable for all sizes | ELEC | labour | SWR11230 | 1024 | DR | 4096
227 | 4 | Unload-11/33KV XLPE UG Cable for all sizes | ELEC | labour | SWR11231 | 1024 | DR | 4096
228 | 8 | Making of Outdoor/Indoor End Making 33 KV 3x400 Sqmm Cable Out Door/Indoor end termination TerminationOD/Idoor end termination 33kv 3x400 xlpe | ELEC | labour | SWR10387 | 2764.76 | EA | 22118.08
229 | 2 | UG Cables Joints 33 KV 3x400 Sqmm Cable Straight through joint 33kv 3x400 xlpe | ELEC | labour | SWR10382 | 5700.78 | EA | 11401.56
230 | 2 | Fabrication & erection of Channels -Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to theRS-Joist poles excluding cost of Mild Steel and transportcharges to substation site, including erection. Fabrication of struc.with welding. | ELEC | labour | SWR10869 | 3426 | TO | 6852
231 | 50 | Supply of earthing pipe with materials-Supply of GI wire No 8 | ELEC | supply | SMR11486 | 105 | KG | 5250
232 | 2 | Supply of earthing pipe with materials-Supply of CI eath pipe with 80mm dia,2.0 M Length | ELEC | labour | SMR11483 | 2789 | EA | 5578
233 | 2 | Providing of Earthing-Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | ELEC | labour | SWR10357 | 1234.2 | EA | 2468.4
234 | 2 | Providing of RCC collar to earth pit-Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINES-Providing of RCC collar | ELEC | labour | SWR10359 | 386 | EA | 772
235 | 40 | Supply of earthing pipe with materials-Supply of GI Flat 25X3 mm | ELEC | supply | SMR11485 | 105 | KG | 4200
236 | 20 | Supply of Danger boards with clamps | ELEC | supply | SMR40070 | 116 | EA | 2320
237 | 4 | S&E-Smart RFID marker | ELEC | labour | SWR25089 | 2745 | EA | 10980
238 | 50 | Supply of PSCC Pole 9.1Mtr 280KG | ELEC | supply | SMR25233 | 3109.41 | EA | 155470.5
239 | 1200 | Supply of Materials -- Supply of MS Channel 100X50mm | ELEC | supply | SMR22745 | 57.45 | KGS | 68940
240 | 600 | Supply of MS Angle 65x65x6 | ELEC | supply | SMR25207 | 57.25 | KG | 34350
241 | 200 | Supply of Materials -- Supply of MS Flat 75x8 mm | ELEC | supply | SMR12321 | 56.42 | KG | 11284
242 | 8 | UG Cables Joints : Making of Outdoor/Indoor End Termination -- Supply 33KV 3x400Sqmm Outdoor | ELEC | supply | SMR22222 | 4554 | EA | 36432
243 | 2 | UG Cables Joints : Making of Straight through joints -- Supply of 33KV 3x400SQmm Straight Through Joint Kit | ELEC | supply | SMR22223 | 24151 | EA | 48302
244 | 180 | Supply of PSCC Pole 11Mtr 365KG | ELEC | supply | SMR25236 | 5399 | EA | 971820
245 | 150 | Supply of 33KV V-Cross Arm without Clamps | ELEC | supply | SMR25229 | 1678 | EA | 251700
246 | 9 | survey line&cabl inc peg mark&tree clear | ELEC | labour | SWR22092 | 765 | KM | 6885
247 | 9 | Paving out and stringing of conductor by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location-55 Sqmm Single Circuit (3 Conductors) | ELEC | labour | SWR10365 | 9454.81 | KM | 85093.29
248 | 175 | Excavation of pits in all soils except hard rock requiring blasting-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") 1.05 cum | ELEC | labour | SWR10107 | 700 | EA | 122500
249 | 50 | Excavation of pits in hard rock requiring blasting. (other than SS)-9.1Mtrs PSCC Pole 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | ELEC | labour | SWR10112 | 1770 | EA | 88500
250 | 213 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Erec of 9.1 Mts PSCC poles for stuts | ELEC | labour | SWR11083 | 2400 | EA | 511200
251 | 37.8 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 248686.2
252 | 225 | Painting of poles-Numbering of poles incl. cost of paint | ELEC | labour | SWR10378 | 32 | EA | 7200
253 | 80 | Excavation of pits in all soils except hard rock requiring blasting-Stud Poles 0.6 M x 0.9 M x 1.5 M | ELEC | labour | SWR10106 | 645 | EA | 51600
254 | 80 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-8.0 m long PSCC poles for Strut | ELEC | labour | SWR21590 | 1500 | EA | 120000
255 | 32 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 210528
256 | 40 | Formation of Cut points - Formation of Cut point for 11 KV Single Circuit line excluding pole erection and stays Formatn of Horiz Cut point for 11KV line | ELEC | labour | SWR10653 | 1435.81 | EA | 57432.4
257 | 350 | Supply of earthing pipe with materials S-GI Bolts & Nuts,Washers etc., | ELEC | supply | SMR11488 | 117.5 | KG | 41125
258 | 4 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 50 Km and upto 80 Km with Lorry for each trip | ELEC | labour | SWR11864 | 5290.74 | EA | 21162.96
259 | 4 | LOADING of Conductor drums | ELEC | labour | SWR10191 | 202 | EA | 808
260 | 4 | UNLOADING of Conductor drums | ELEC | labour | SWR10509 | 100 | EA | 400
261 | 6 | Supply of earthing pipe with materials-Supply of CI eath pipe with 50mm dia,2.0 M Length | ELEC | supply | SMR11484 | 2441 | EA | 14646
262 | 6 | Providing of Earthing-Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | ELEC | labour | SWR10357 | 1234.2 | EA | 7405.2
263 | 6 | Providing of RCC collar to earth pit-Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINES-Providing of RCC collar | ELEC | labour | SWR10359 | 386 | EA | 2316
264 | 6 | Assembly and erection of Structure as per specification which includes fixing of top channels and cross bracings, transport of all materials from road side to the location, earthing, back filling with earth ramming etc excluding pit excavation and concreting.-11KV DP Structure with 9.1 Mtrs PSCC Poles | ELEC | labour | SWR21130 | 3363.96 | SET | 20183.76
265 | 6 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | ELEC | labour | SWR10393 | 3200 | EA | 19200
266 | 6 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | ELEC | labour | SWR10881 | 142 | EA | 852
267 | 50 | Supply of earthing pipe with materials-Supply of GI wire No 8 | ELEC | supply | SMR11486 | 105 | KG | 5250
268 | 675 | Loading of 11KV Polymer Pin Insulators with GI pins | ELEC | labour | SWR11248 | 1 | EA | 675
269 | 675 | Un loading of 11KV Polymer Pin Insulators with GI pins | ELEC | labour | SWR11249 | 1 | EA | 675
270 | 240 | Loading of 11KV Polymer Pin Insulators with GI pins | ELEC | labour | SWR11248 | 1 | EA | 240
271 | 240 | Un loading of 11KV Polymer Pin Insulators with GI pins | ELEC | labour | SWR11249 | 1 | EA | 240
272 | 6 | Loading of 11 KV Metal parts | ELEC | labour | SWR12402 | 48 | BAG | 288
273 | 6 | Un loading of 11 KV Metal parts | ELEC | labour | SWR12421 | 48 | BAG | 288
274 | 960 | Laying of 2nd cable in excavated trench | ELEC | labour | SWR10988 | 204.1 | M | 195936
275 | 72 | Cost of Pipes and slabs-Supply of 6" B class GI pipe | ELEC | supply | SMR40081 | 1044 | M | 75168
276 | 200 | Cost of Pipes and slabs-Supply of 250 mm Hume pipe of class NP3 with compresive strength of 35N/mm2 for 28 days curing,barewall thickness of 30mm,1.25kG linear/meter and withstanding capability of 22.50KN/linear meter as per IS 458-1993. | ELEC | supply | SMR40077 | 363 | M | 72600
277 | 6 | Cost of Pipes and slabs-Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters , CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | ELEC | supply | SMR40085 | 484 | EA | 2904
278 | 5 | Load-11/33KV XLPE UG Cable for all sizes | ELEC | labour | SWR11230 | 1024 | DR | 5120
279 | 5 | Unload-11/33KV XLPE UG Cable for all sizes | ELEC | labour | SWR11231 | 1024 | DR | 5120
280 | 1.1 | Fabrication & erection of Channels -Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to theRS-Joist poles excluding cost of Mild Steel and transportcharges to substation site, including erection. Fabrication of struc.with welding. | ELEC | labour | SWR10869 | 3426 | TO | 3768.6
281 | 50 | Supply of Danger boards with clamps | ELEC | supply | SMR40070 | 116 | EA | 5800
282 | 6 | S&E-Smart RFID marker | ELEC | labour | SWR25089 | 2745 | EA | 16470
283 | 960 | Excavation & laying of UG Cable (Double Run)-Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts,-In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil/CC-11 KV 3x300 Sqmm Cable | ELEC | labour | SWR11973 | 631.06 | M | 605817.6
284 | 240 | Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-11 KV 3x300 Sqmm Cable | ELEC | labour | SWR12005 | 275.4 | M | 66096
285 | 24 | Making of Outdoor/Indoor End Termination-Making 11 KV 3x300 Sqmm Cable Out Door/Indoor end termination | ELEC | labour. | SWR10391 | 2370.63 | EA | 56895.12
286 | 6 | UG Cables Joints Making of Straight through joints-11 KV 3x300 Sqmm Cable | ELEC | labour. | SWR10386 | 3725.45 | EA | 22352.7
287 | 225 | Supply of PSCC Pole 9.1Mtr 280KG | ELEC | supply | SMR25233 | 3109.41 | EA | 699617.25
288 | 80 | Supply of PSCC Pole 8Mtr 140KG | ELEC | supply | SMR25232 | 1580 | EA | 126400
289 | 185 | supply of V X-Arm with MS Angle 65x65x6 | ELEC | supply | SMR25218 | 743 | EA | 137455
290 | 185 | Supply of 11KV Top Cleant for 9.1M(Vertical) | ELEC | supply | SMR25226 | 256 | EA | 47360
291 | 80 | Supply of 11KV Horizontal Cross Arm | ELEC | supply | SMR25223 | 528 | EA | 42240
292 | 6 | Supply of Materials -- Supply of 11 kV 400 A Double break AB switch | ELEC | supply | SMR12317 | 18150 | EA | 108900
293 | 200 | Supply of Materials -- Supply of MS Flat 50x6 mm | ELEC | supply | SMR12322 | 56.5 | KG | 11300
294 | 400 | Supply of MS Angle 50x50x6 | ELEC | supply | SMR25206 | 58.15 | KG | 23260
295 | 500 | Supply of MS Channel 75x40 mm | ELEC | supply | SMR25205 | 58.45 | KG | 29225
296 | 24 | Supply of 11KV 3x300 Heat Shble O/d End Term Kit | ELEC | supply | SMR25208 | 1372.88 | EA | 32949.12
297 | 6 | Supply of 11KV 3x300 Heat Shble stright through joint Kit | ELEC | supply | SMR25210 | 4110.17 | EA | 24661.02
Sub Total: | [7 empty] | 14999130.445
Civil labour - WBS. No. S-1787-13-07-01-01-001
Sl No | Estimate Quantity | Description of item | Work Type | Item Short Description | APSS / Month Cl.NumberSSR 11 & 12 | Rate (INR) | UOM | AMOUNT
1 | 32 | Leveliing the site by cutting and levelling with the help of JCB including cost,conveyance of all materials,hire chareges etc complete for finished item of work as directed by Engineer-in-charge. | Civil | Labour | SWR34179 | 2165 | Hrs | 69280
2 | 135.61 | Earth work excavation in all type of ordinary soils red earth, Hard gravelly soils, earth mixed with sand and sandy soils etc., in all conditions such as slushy and dry with initial leads and lifts for foundations. | Civil | Labour | SWR33015 | 486 | m3 | 65906.46
3 | 32.45 | Plain Cement concrete PCC (1:4:8) using 40mm HBG metal for foundations and leveling course, including cost and conveyance of all materials, labour all leads and lifts, consolidation and all operations, formwork as required, curing, etc. complete for finished item w | Civil | Labour | SWR33028 | 4679 | m3 | 151833.55
4 | 117.88 | Coursed Rubble stone (CRS) masonry 2nd sort with hard granite stones in cement mortar (1:6) for basement, including cost and conveyance of all materials, labour charges, curing, all leads and lifts, etc, complete for finished item of work. | Civil | Labour | SWR33041 | 4826 | m3 | 568888.88
5 |  | 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge
6 | 3.564 | RCC M20 Grade footing 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33098 | 9431 | m3 | 33612.084
7 | 2.28 | RCC M20 Grade Coloumn . 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33100 | 13180 | m3 | 30050.4
8 | 2.25 | RCC M20 Grade Plinth beams 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33099 | 12302 | m3 | 27679.5
9 | 3.17 | D) RCC M20 Grade Roof Beams landing beam 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33121 | 12218 | m3 | 38731.06
10 | 0.58 | e)RCC M20 Grade Lintels 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33107 | 13009 | m3 | 7545.22
11 | 2.7 | f) RCC M20 Grade Sunshades 600mm wide and 75mm thick'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33114 | 1371 | m2 | 3701.7
12 | 15.224 | g) RCC M20 Grade Roof Slab for Control Room 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33128 | 10806 | m3 | 164510.544
13 | 3 | Reinforcement steelSupplying, Cutting, bending, binding, placing in position and tying reinforcement steel in all heights including cost and conveyance of steel and binding wire etc,. With all leads and lifts, labour charges, etc., complete for finished item of work. | Civil | Labour | SWR33144 | 70687 | Ton | 212061
14 | 38.36 | Brick masonry in cement mortar CM (1:6) for superstructure using well burnt country made second class bricks of approved quality including cost and conveyance of all materials curing, scaffolding with all leads and lifts in all heights etc., complete for fin | Civil | Labour | SWR33068 | 8244 | m3 | 316239.84
15 | 2.7 | Plain Cement concrete PCC (1:2:4) using 20mm size well graded HBG metal for foundations, including cost, conveyance of all materials,labour all leads and lifts,consolidation and all operations, formwork as required, curing,etc. complete for finished item of work | Civil | Labour | SWR33030 | 6048 | m3 | 16329.6
16 | 606.06 | Plastering with CM 2 coats, 20 mm thick, base coat in CM (1:6), 16 mm thick and top coat in CM (1:4), 4mm thick with Dubara sponze finishing including cost of all materials, seigniorage charges, excluding conveyance charges of materials and including all operational, incidental and labour charges for mixing mortar, laying rendering smooth and thread lining, curing, rounding off junctions of wall and slab etc., complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33163 | 559 | m2 | 338787.54
17 | 349.515 | Painting with two coats of Plastic Emulsn paint over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33356 | 210 | m2 | 73398.15
18 | 200.85 | Painting with two coats of Surya Cem paint over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33329 | 85 | m2 | 17072.25
19 | 3 | Supply and Fixng of MS Name Board including cost & conveyance of all materials,labour charges etc complete for finished item of work. | Civil | Labour | SWR33421 | 4326 | m2 | 12978
20 | 1 | Geophysical Investgation charges for water point by Geologist | Civil | Labour | SWR33608 | 5000 | EA | 5000
21 |  | Drilling of 165mm bore well with machine rig including deployment and hire charges of rig and other machinery and equipment labour charges , measuring the yeild of borewell including cost and conveyance etc complete
22 | 90 | Drill-165mm Bore Well 0 to 90 | Civil | Labour | SWR33609 | 336 | M | 30240
23 | 30 | Drill-165mm Bore Well 90M to 120M | Civil | Labour | SWR34830 | 369 | M | 11070
24 | 30 | Drill-165mm Bore Well 120M to 150M | Civil | Labour | SWR34831 | 394 | M | 11820
25 | 30 | Drill-165mm Bore Well 150M to 180M | Civil | Labour | SWR34832 | 492 | M | 14760
26 | 30 | Drill-165mm Bore Well 180M to 210M | Civil | Labour | SWR34833 | 623 | M | 18690
27 | 30 | Drill-165mm Bore Well 210M to 240M | Civil | Labour | SWR34834 | 754 | M | 22620
28 | 30 | Drill-165mm Bore Well 240M to 270M | Civil | Labour | SWR34835 | 918 | M | 27540
29 | 92 | Drill-165mm Bore Well 270M and above | Civil | Labour | SWR34836 | 1082 | M | 99544
30 | 40 | Supply and fixing of 160mm dia PVC casing of A class 6Kg point pressure including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR33611 | 883 | M | 35320
31 | 1 | Supply and erecting, ISI mark submersible 5.0 HP, Single Phase 30 stages pumpset suitable for 106/156mm dia borewell including cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33640 | 48007 | EA | 48007
32 | 325 | Supply and fixing of HDPE pipe 40mm dia of 16Kg/cm2 including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR34410 | 180 | M | 58500
33 | 1 | Supply and erecting D.O.L Starter 415V , Single phase,50Hz with SS enclouserincluding cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33645 | 7854 | EA | 7854
34 | 360 | Supply of 3 Core 2.5 Sqmm Flat Copper cable of ISI for Submersible Motors of makes Finolex / Polycab / Gold Medal / Million / Payal / Sun Light / Power Flex / Fortune Art | Civil | Labour | SWR33641 | 192 | m | 69120
35 | 71 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-28.60mm OD Pipe - SDR 11 | Civil | Labour | SWR34363 | 410 | m | 29110
36 | 35 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type - 25mm NB Size | Civil | Labour | SWR34346 | 466 | EA | 16310
37 | 839.38 | Supplying and filling the substation site with borrowed gravel, watering, ramming, thoroughly complying with the standard specification. | Civil | Labour | SWR33052 | 309 | m3 | 259368.42
38 | 16.56 | Providing Design R.C.M. drop wall of 25mm thickness with cm 1:3 and 6mm dia MS bars at 150mm both ways and chicken mesh in two coats 20mm thick each plastering including cost and conveyance of all materials with leads and lifts, scaffolding and curing, labo | Civil | Labour | SWR33203 | 3037 | m2 | 50292.72
39 | 12.24 | Supply and fixing of Ms ornamental safety grill of approved design including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33310 | 2990 | m2 | 36597.6
40 | 5.91 | Supply and fixing of doors with the MT Wood frames of the door shall be made well seasoned mt wood of cross section 100x75mm. The shutter shall be made isi mark flushed door with decolam sheets pasted on both sides with PVC beading 40mm width all round.Frame shall be painted with two coats of synthetic enamel paint of approved color over one coat of primer over luppum with spary with 3 no 150mm brass hinges 1 no brass door stoper, 1 no 250mm brass aldrops. 2 no 300 mm aluminium tower bolts, 2 no 150mm brass fancy door handlers, 1 no keyless lockset with cp handel. The quoted rate shall include cost and conveyance of the meterials, fixig, labour carges, tools, handles,locking arrangementts and other fixtures & fittings for finished item work as directed by the Engineer - in- charge. | Civil | Labour | SWR33264 | 7314 | m2 | 43225.74
41 | 128.25 | Raised pointing to the exposed surfaces of CRS masonry in cm 1:3 prop. including cost and conveyance of all materials, labour charges, all leads and lifts curing etc, complete for finished item of work. | Civil | Labour | SWR33184 | 124 | m2 | 15903
42 | 8.64 | Supplying and fixing Aluminium sliding windows with grill and fixed glass panels using anodised aluminium extruded sections of mat finish for frames and mullions made from approved aluminium sections 62x32x1.2mm at 0.73kg/Rm providing 5mm plain glass fix | Civil | Labour | SWR33277 | 3623 | m2 | 31302.72
43 | 16.56 | Supply and laying of Ceramic floor over of CM 1:3 20 mm thick including required materials and labour charges etc complete for item of work | Civil | Labour | SWR33224 | 914 | m2 | 15135.84
44 | 121.92 | Flooring with double machine polished and hand cut Tandur blue stone 20mm thick of approved colour, quality and of minimum of 300x300mm size over a bed of cement mortar 1:3 20mm thick including cost of all materials, with all leads and lifts jointing and | Civil | Labour | SWR33219 | 785 | m2 | 95707.2
45 | 6.74 | Supply and fixing of 4" high skirting of shabad stone to the walls including cost and conveyance of all materials, labour etc for finished item of work. | Civil | Labour | SWR33236 | 875 | m2 | 5897.5
46 | 243.69 | Painting with two coats of OBD over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials labour charges etc., complete for finished item of work. | Civil | Labour | SWR33333 | 146 | m2 | 35578.74
47 | 101.17 | Providing impervious coat over RCC roof slab to requried slopes with 20mm thick in CM 1:3 mixed with approved brand of water proffing compound inclding cost and conveyance of all materials, labour charges, curing, rounding off junctions of wall and slab, all leads and lifts, etc . complete for finished item of work as directed by the Engineer - in - charge. | Civil | Labour | SWR33156 | 582 | m2 | 58880.94
48 | 60 | Supply & fixing of 25mm dia 2mm thick suSupply & fixing of 25mm dia 2mm thick surface P.V.C. pipe (ISI MARK) Concealed in wall with all required accessories including masonary work and labour charges etc.complete. | Civil | Labour | SWR33441 | 108 | m | 6480
49 | 1 | Supply & fixing TPN Distribution board w Supply & fixing TPN Distribution board with IP-42 protection (Metal Door)suitable for 3 phase ELCB/RCCB/FP Isolator as incomer and 10kA SP MCBs as out going including internal connection and labour charges for surface / flush mounting etc Complete. | Civil | Labour | SWR33526 | 11353 | EA | 11353
50 | 10 | Supply & fixing of 6A 3 pin wall plug socket with 6A switch control on a common switch board with earth continuity including wire leads,earth connection along with all labour charges etc., complete | Civil | Labour | SWR33468 | 166 | EA | 1660
51 | 6 | Supply & fixing of 16A 3 pin and 6A 3pin plug Flush type socket with indicator lamp and 16Amps fuse unit and 16Amps switch control (5 in one )duly recessed in wall with wooden deep box of 6'' x 8'' x 2 1/2'' size covered with hylam sheet earth connection and all labour charges etc., complete on wall. | Civil | Labour | SWR33470 | 449 | EA | 2694
52 | 24 | Supply and Fixing of modular switch, LP,FP,EFP Wiring with 2 runs of 14/0.3mm (1.0 sq.mm)Fire Retardant (FR) P.V.C. insulated flexible copper cable (ISI MARK) in existing pipe with 6A Flush type Switch,ceiling rose and 3mm thick hylam sheet covering to switch control box including all labour charges etc., complete for light points, bell , fan and exhaust fan points in Non-Residential Buildings. | Civil | Labour | SWR33457 | 676 | EA | 16224
53 | 12 | Supply & Fixing of 28W T5 fluorescent tube. | Civil | Labour | SWR33558 | 148 | EA | 1776
54 | 1 | Supply of 12" (300mm)ISI, 900 RPM Heavy duty exhaust fan with metallic blades with Mark of makes Crompton / Bajaj / Havells / Orient. | Civil | Labour | SWR33571 | 2192 | EA | 2192
55 | 180 | Supply and run of 2 of 22/0.3mm (1.5 sq.mm) (FR) P.V.C. insulated flexible copper cable in existing pipe for mains including all labour charges complete. | Civil | Labour | SWR33496 | 75 | m | 13500
56 | 180 | Supply and run of 2 of 36/0.3mm (2.5 sq.mm) FR P.V.C. insulated flexible copper cable in existing pipe for mains including all labour charges complete. | Civil | Labour | SWR33497 | 103 | m | 18540
57 | 12 | Supply & fixing of batten holder /slanting holder in lieu of ceiling rose of light point complete with all connection and all labour charges with 40W bulb (for new installation). | Civil | Labour | SWR33484 | 141 | EA | 1692
58 | 4 | Supply & fixing of 1200mm (48'') sweep 230v,A.C 50 Hz.Ceiling fan with 3 Blades and double ball bearings with all standared accessories. | Civil | Labour | SWR33563 | 2277 | EA | 9108
59 | 4 | Supply & fixing of Electronic Regulator for ceiling fans 900/1200/1400mm sweep including cost of material, Electrical charges complete for finished item of work | Civil | Labour | SWR33564 | 589 | EA | 2356
60 | 1 | Providing independent EARTHING by excavating a trench to a depth of 2.1M in all solid,as per size specified in the Data,using 40mm dia 'B' class GI pipe of 2.5 Mtrs length with necessary accessories with hume pipe ring duly providing staggered holes including filling with equal proportion of salt and Charcoal in layers and all labour charges etc., compiete for small quarters. | Civil | Labour | SWR33596 | 5345 | EA | 5345
61 | 35 | Supplying, laying, jointing and testing 101.6 mm SWG SP-1 pipes of ISI make conforming to ISI 651 & 4127 with airtight cement joints in CM 1.5:1 prop. Including excavation of trenches and socket pits in any soil (except rock requiring blasting) up to 1524 mm(5'0") depth and refilling with watering and tamping. | Civil | Labour | SWR34281 | 755 | m | 26425
62 | 3 | Constructing 904.0 mm (3#0#) dia brick masonry inspection chamber as per IS - 4111: Part-1:1986 with cement mortar (1:6) prop using 2nd Class Clay Bricks of 225 mm thick from approved source having a minimum crushing strength of 5 N/sq.mm including plastering with cement mortar 1:3 prop; ½# thick both inside and outside fitted with 20# dia RCC manhole covers and frames including excavating pits up to a depth of 904 mm (3'-0") in all sorts of soils (excluding rock) and laying cement concrete (1:4:8) 150 mm thick using 40 mm HBG Metal and P.C.C. 1:2:4 benching and channel 100 mm thick as per Standard specification and including cost and conveyance of all materials like cement, sand, bricks, water etc., to site, cost of seigniorage charges on all materials and all incidental and operational, labour charges like mixing cement mortar, constructing masonry, lift charges, curing etc., complete for finished item of work as per Standard specification. | Civil | Labour | SWR34296 | 8766 | EA | 26298
63 | 4 | Supply & fixing of 110 mm dia - Door Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34381 | 128 | EA | 512
64 | 4 | Supply & fixing of 110 mm dia - Plain Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34380 | 100 | EA | 400
65 | 12 | Supply & fixing of 110 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand | Civil | Labour | SWR34377 | 462 | m | 5544
66 | 18 | Supply & fixing of 90 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand | Civil | Labour | SWR34378 | 410 | m | 7380
67 | 3 | Supplying & fixing 150 mm x 100 mm SWG gully traps conforming to ISI 651 & 4127 with C.I Grating & Cost. Brick masonry in CM 1:6 prop. Intermediate chamber and fitted with 304.8 mm x 288.6mm (12"x9") C.I Frame and hinged cover | Civil | Labour | SWR34286 | 767 | EA | 2301
68 | 1 | Supplying and Fixing of European Water Closet of 1st Quality | Civil | Labour | SWR34312 | 2228 | EA | 2228
69 | 6 | Supply & fixing 15 mm angle stop cock Indian make 400 grams Seiko/ Senior/ Nice/ Senior/ Nice or equivalent | Civil | Labour | SWR34328 | 721 | EA | 4326
70 | 4 | S&F 15 mm N.P bib tap Indian make 400 grams full turn Seiko/ Senior/ Nice or equivalent | Civil | Labour | SWR34329 | 296 | EA | 1184
71 | 1 | Supplying & Fixing Indian make Flat Back Wash Hand Basin (HSW/Parryware/ Neycer) 1st quality conforming to IS:2556-Part-4:1972 with waste fittings like rubber plug, chain, 32 mm nominal size C.P. Fitting with parallel pipe thread conforming to IS:2963-1979 and fitted with 15 mm nominal bore Chromium Plated Pillar Tap of 1st quality Indian make 400 grams Seiko/ Senior/ Nice/ Esso or equivalent complete with standard CI brackets including wooden block: 550 x 400 mm - Single C.P. Pillar cock | Civil | Labour | SWR34316 | 1717 | EA | 1717
72 | 2 | Supply & fixing 38.1 mm C.P waste coupling Half or Full Thread 1st Quality Indian make Parryware or equivalent | Civil | Labour | SWR34428 | 309 | EA | 618
73 | 2 | Supply & fixing of 4" (101.6 mm ) Nahany Trap ( Without Jali with inlet)UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34387 | 134 | EA | 268
74 | 1000 | Providing & Placing on Terrace (at all floor levels) polyethylene water storage tank with Double layer approved brand & manufacture with cover and suitable locking arrangement & making necessary holes for inlet & outlets and over flow pipes but with NECESSARY fittings & base support for tanks | Civil | Labour | SWR34375 | 10 | L | 10000
75 | 2 | Supply & fixing 31.75 mm dia PVC flexible waste pipe of 914.4 mm length of Ist quality | Civil | Labour | SWR34426 | 33 | EA | 66
76 | 45 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)- 15.90mm OD Pipe - SDR 11 | Civil | Labour | SWR34361 | 239 | m | 10755
77 | 200 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-22.20mm OD Pipe - SDR 11 | Civil | Labour | SWR34362 | 313 | m | 62600
78 | 4 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type -20mm NB Size | Civil | Labour | SWR34345 | 331 | EA | 1324
79 | 1 | Supply & fixing 25.4 mm dia & 609.6 mm long aluminium anodized towel rod with brackets and aluminium screws | Civil | Labour | SWR34430 | 489 | EA | 489
80 | 36 | Plain Cement concrete PCC (1:3:6) using 40mm HBG metal for foundations and leveling course, including cost and conveyance of all materials, labour all leads and lifts, consolidation and all operations, formwork as required, curing, etc. complete for finished item w | Civil | Labour | SWR33029 | 4969 | m3 | 178884
81 | 120 | Supply&Fabrication and fixing of Welded wire mesh ( 2" x 2") of 3mm dia. with ISMC (75x40x4.4mm) and Pheriperal frame of ISA(35x35x3mm) incldg cost& conveyance painting with synthetic enamil paint two coats over a coat of red oxide primer etc complete for finished item of work.. | Civil | Labour | SWR33403 | 2310 | m2 | 277200
82 | 1 | Providing Consultancy services for arranging contour surveying with total station incuding preparation of boundary and contour levels with 2 Nos. Hard copies and soft copies complete for finished items of work | Civil | Labour | SWR33427 | 5665 | EA | 5665
83 | 222.2468 | Seigniorage Charges - Sand | Civil | Labour | SWR34470 | 40 | m3 | 8889.873
84 | 725.7496 | Seigniorage Charges - Metal | Civil | Labour | SWR34471 | 97.5 | m3 | 70760.585
85 | 839.38 | Seigniorage Charges - Gravel | Civil | Labour | SWR34472 | 30 | m3 | 25181.4
86 | 60 | Supply and fixing of RCC fencing poles of size 0.1mx0.1mx1.8m (security fencing of sub station), including cost and conveyance of all labour, materials,and hire chareges etc complete for finished item of work. | Civil | Labour | Swr33405 | 1444 | EA | 86640
87 | 1200 | Supply and fixing of galvanised barded wire (1 horizantal & 2 cross strands. including cost and conveyance of all labour, materials,and hire chareges etc complete for finished item of work. | Civil | Labour | Swr33408 | 16 | m | 19200
Civil total | [7 empty] | 4231777.056
Total elec+civil | [7 empty] | 19230907.501

## 4. Noori Nagar
Name of the work: Estimate for erection of new 33/11kV Outdoor Sub-Station at Noorinagar with 2x8 MVA PTRs and connected 33kV and 11kV Lines at Noorinagar in Pahadishareef (M) of ECGH Division/Masterplan/RR Circle
WBS No. S-1788-13-03-02-01-001
Sl No | Estimate Quantity | Description of item | Work Type | Item Short Description | APSS / Month Cl.NumberSSR 11 & 12 | Rate (INR) | UOM | AMOUNT
1 | 16 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | ELEC | Labour | SWR11039 | 928 | EA | 14848
2 | 5.76 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ELEC | Labour | SWR10868 | 6852 | TO | 39467.52
3 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELEC | supply | SMR40009 | 2181 | TO | 12562.56
4 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELEC | labour | SWR10877 | 851 | TO | 4901.76
5 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELEC | supply | SMR40010 | 1293 | TO | 7447.68
6 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELEC | labour | SWR10879 | 482 | TO | 2776.32
7 | 5.76 | Fabrication & erection of Channels-Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ELEC | labour | SWR10867 | 1470 | TO | 8467.2
8 | 16 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-R.S. Joists 150 x 150 mm | ELEC | labour | SWR10348 | 1952.61 | EA | 31241.76
9 | 17.758 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 116829.882
10 | 9.24 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ELEC | labour | SWR10862 | 373 | M2 | 3446.52
11 | 16 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | ELEC | labour | SWR11089 | 48 | EA | 768
12 | 4 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-8.0Mtrs PSCC Poles 0.76 M x 0.76M x 1.52M (2.6" x 2.6" x 5.0') 0.88 cum | ELEC | labour | SWR11037 | 793 | EA | 3172
13 | 1 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ELEC | Labour | SWR10868 | 6852 | TO | 6852
14 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELEC | supply | SMR40009 | 2181 | TO | 2181
15 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELEC | labour | SWR10877 | 851 | TO | 851
16 | 1 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELEC | supply | SMR40010 | 1293 | TO | 1293
17 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELEC | labour | SWR10879 | 482 | TO | 482
18 | 1 | Fabrication & erection of Channels-Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ELEC | labour | SWR10867 | 1470 | TO | 1470
19 | 4 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Box pole 12 Mtr | ELEC | labour | SWR11267 | 3901.37 | EA | 15605.48
20 | 2.65 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 17434.35
21 | 2.31 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ELEC | labour | SWR10862 | 373 | M2 | 861.63
22 | 4 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | ELEC | labour | SWR11089 | 48 | EA | 192
23 | 5.063 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ELEC | labour | SWR10868 | 6852 | TO | 34691.676
24 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELEC | supply | SMR40009 | 2181 | TO | 11042.403
25 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELEC | labour | SWR10877 | 851 | TO | 4308.613
26 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELEC | labour | SMR40010 | 1293 | TO | 6546.459
27 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELEC | labour | SWR10879 | 482 | TO | 2440.366
28 | 5.063 | Fabrication & erection of Channels-Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ELEC | labour | SWR10867 | 1470 | TO | 7442.61
29 | 13 | Erection of AB Switch and aligment complete Erection of 33 KV AB Switch including alignment and earthing | ELEC | labour | SWR10392 | 4500 | EA | 58500
30 | 34 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Note:-The requirement of 2nd coat is to be justified by the concerned Divisional Engineer /Executive Engineer before execution of this work Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | ELEC | labour | SWR10881 | 142 | EA | 4828
31 | 34 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | ELEC | labour | SWR12331 | 146.63 | EA | 4985.42
32 | 6 | Loading of 33 KV CTs/ PTs | ELEC | labour | SWR10200 | 165 | EA | 990
33 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
34 | 6 | Un loading of 33 KV CTs/ PTs | ELEC | labour | SWR10518 | 128 | EA | 768
35 | 2 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33kv single phase PT s | ELEC | labour | SWR10401 | 1079 | SET | 2158
36 | 12 | Loading of 33 KV, 10 KA LAs Station typ | ELEC | labour | SWR10266 | 41 | EA | 492
37 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
38 | 12 | Un loading of 33 KV, 10 KA LAs Station type | ELEC | labour | SWR10584 | 35 | EA | 420
39 | 4 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33 KV LAS station/Line type including earthing | ELEC | labour | SWR10396 | 880 | SET | 3520
40 | 2 | Loading of 33 KV VCBs along with Panel boards | ELEC | labour | SWR10198 | 1024 | EA | 2048
41 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
42 | 2 | Un loading of 33 KV VCBs along with Panel boards | ELEC | labour | SWR10516 | 1044.48 | EA | 2088.96
43 | 12.584 | Excavate-Pit for 33KV VCB | ELEC | labour | SWR23224 | 331 | M3 | 4165.304
44 | 14.52 | Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x 1.8 x 0.75 cum for VCB Plinth | ELEC | labour | SWR20685 | 5160 | M3 | 74923.2
45 | 2 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33 KV VCB with Control Panel | ELEC | labour | SWR10460 | 12500 | EA | 25000
46 | 2 | Loading and unloading of PTR on constructed plinth-Loading of 8MVA PTR | ELEC | labour | SWR10613 | 5805.84 | EA | 11611.68
47 | 2 | Transport of Power transformers (0 to 100 KM) from one place to another place in GHMC Area.(excluding of loading & unloading )-8MVA power transformer | ELEC | labour | SWR10854 | 21945 | EA | 43890
48 | 2 | Loading and unloading of PTR on constructed plinth-Unloading of 8MVA PTR | ELEC | labour | SWR10627 | 5805.84 | EA | 11611.68
49 | 700 | S/o rail poles 90/105lb (250x2N) | ELEC | supply | SMR22718 | 47.27 | KG | 33089
50 | 14 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Rail pole 90 lbs | ELEC | labour | SWR10344 | 3510 | EA | 49140
51 | 2 | Erection of PTR on constructed plinth-Erection of 8 MVA PTR. | ELEC | labour | SWR21321 | 49480.2 | 49480.2 | 98960.4
52 | 0.436 | Extention of 33KV Bay at 132/33KV Sub-station-Zebra condutor | ELEC | supply | SMR24910 | 299369 | 299369 | 130524.884
53 | 30 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing | ELEC | supply | SMR11915 | 2055 | 2055 | 61650
54 | 30 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of I-Bolts | ELEC | supply | SMR22473 | 294 | 294 | 8820
55 | 45 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 "to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating . Sup T clamp LM6 Al alloy of 12 mm, 800 A | ELEC | labour | SMR40011 | 299 | 299 | 13455
56 | 6 | Bus stringing Hoisting of Insulators and hardware, stretching the conductor and stringing of 33 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bussection of 4.5mt) Hoisting post ins&hrd wr 1panther 33kv | ELEC | labour | SWR21240 | 781 | 781 | 4686
57 | 84 | Stringing of bus with panther conductor including jumpering etc., complete to all the equipment in SS fixing to all clamps and equipment.(3 Conductors) | ELEC | labour | SWR10404 | 327.68 | 327.68 | 27525.12
58 | 30 | Bus stringing Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | ELEC | labour | SWR10884 | 224 | 224 | 6720
59 | 75 | Labour for Fixing of all types of clamps | ELEC | labour | SWR10917 | 65 | 65 | 4875
60 | 25 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | ELEC | labour | SWR11039 | 928 | 928 | 23200
61 | 8.68 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ELEC | labour | SWR10868 | 6852 | 6852 | 59475.36
62 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELEC | supply | SMR40009 | 2181 | 2181 | 18931.08
63 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELEC | labour | SWR10877 | 851 | 851 | 7386.68
64 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELEC | supply | SMR40010 | 1293 | 1293 | 11223.24
65 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELEC | labour | SWR10879 | 482 | 482 | 4183.76
66 | 8.68 | Fabrication & erection of Channels-Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ELEC | labour | SWR10867 | 1470 | 1470 | 12759.6
67 | 25 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-R.S. Joists 150 x 150 mm | ELEC | labour | SWR10348 | 1952.61 | 1952.61 | 48815.25
68 | 27.75 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | 6579 | 182567.25
69 | 17.91 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ELEC | labour | SWR10862 | 373 | 373 | 6680.43
70 | 25 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | ELEC | labour | SWR11089 | 48 | 48 | 1200
71 | 4.642 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ELEC | labour | SWR10868 | 6852 | 6852 | 31806.984
72 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELEC | supply | SMR40009 | 2181 | 2181 | 10124.202
73 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELEC | labour | SWR10877 | 851 | 851 | 3950.342
74 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELEC | supply | SMR40010 | 1293 | 1293 | 6002.106
75 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELEC | labour | SWR10879 | 482 | TO | 2237.444
76 | 4.642 | Fabrication & erection of Channels-Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ELEC | labour | SWR10867 | 1470 | TO | 6823.74
77 | 17 | Erection of AB Switch and aligment complete-Erection of 11KV 800A double throw AB Switches | ELEC | labour | SWR21277 | 3500 | EA | 59500
78 | 3 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | ELEC | labour | SWR10393 | 3200 | EA | 9600
79 | 2 | Loading of 11 KV CT - PT Sets | ELEC | labour | SWR10201 | 190 | EA | 380
80 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
81 | 2 | Un loading of 11 KV CT - PT Sets | ELEC | labour | SWR10519 | 101 | EA | 202
82 | 2 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc-Erection of 11 KV three phase PTs | ELEC | labour | SWR10402 | 800 | SET | 1600
83 | 24 | Loading of 11 KV, 10 KA LAs Station type | ELEC | labour | SWR10264 | 32 | EA | 768
84 | 2 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 6599.4
85 | 24 | Un loading of 11 KV, 10 KA LAs Station type | ELEC | labour | SWR10582 | 32 | EA | 768
86 | 2 | Erection of 11 KV LAS station type including earthing | ELEC | labour | SWR10397 | 559 | SET | 1118
87 | 6 | Erection of 11 KV LAS line type including earthing | ELEC | labour | SWR10398 | 505 | SET | 3030
88 | 8 | Loading of 11 KV VCBs along with Panel boards | ELEC | labour | SWR10199 | 1024 | EA | 8192
89 | 4 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 13198.8
90 | 8 | Un Loading of 11 KV VCBs along with Panel boards | ELEC | labour | SWR10517 | 1044.48 | EA | 8355.84
91 | 41.6 | Excavate-Pit for 33KV VCB | ELEC | labour | SWR23224 | 331 | M3 | 13769.6
92 | 48 | Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x 1.8 x 0.75 cum for VCB Plinth | ELEC | labour | SWR20685 | 5160 | M3 | 247680
93 | 8 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc-Erection of 11 KV VCB with Control Panel | ELEC | labour | SWR10461 | 12000 | EA | 96000
94 | 12 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing | ELEC | supply | SMR11915 | 2055 | SET | 24660
95 | 12 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of I-Bolts | ELEC | supply | SMR22473 | 294 | EA | 3528
96 | 45 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 "to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating . Sup T clamp LM6 Al alloy of 12 mm, 800 A | ELEC | supply | SMR40011 | 299 | EA | 13455
97 | 2 | Bus Stringing -Hoisting of Insulators and hardware, stretching the conductor and stringing of 11 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 3.5mt) Hoisting post ins&hrd wr 1panther 11kv | ELEC | labour | SWR21241 | 507 | EA | 1014
98 | 63 | Stringing of bus with panther conductor including jumpering etc., complete to all the equipment in SS fixing to all clamps and equipment.(3 Conductors) | ELEC | labour | SWR10404 | 327.68 | M | 20643.84
99 | 45 | Bus stringing Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | ELEC | labour | SWR10884 | 224 | EA | 10080
100 | 57 | Labour for Fixing of all types of clamps | ELEC | labour | SWR10917 | 65 | EA | 3705
101 | 584 | Laying of earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication 75x 8mm MS Flat / GI Flat. Laying of earth mat,excavation 75x 8mm | ELEC | labour | SWR10920 | 65 | RMT | 37960
102 | 1010 | Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) Earthing for raisers of SS Flat 50x6 mm. | ELEC | labour | SWR10919 | 41 | RMT | 41410
103 | 36 | Supply of earthing pipe with materials -Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | ELEC | supply | SMR11482 | 3486 | EA | 125496
104 | 36 | Providing of Earthing-Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | ELEC | labour | SWR10357 | 1234.2 | EA | 44431.2
105 | 36 | Providing of RCC collar to earth pit-Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINES-Providing of RCC collar | ELEC | labour | SWR10359 | 386 | EA | 13896
106 | 2 | Supply of Copper Flexible jumper with 75 X 8 of length 250 mm at neutral of Power tranformer end and 50 X 6 of length 50mm two Nos at double neutral end duly brasing with flexible jumper of capacity of 5kA/3 sec for power transformer neutral. SupCU Flexi jumper for Power T/F Neutral | ELEC | supply | SMR40033 | 4725 | EA | 9450
107 | 2 | Providing of earthing with various types of earth electrodes-Providing of double earthing for neutral with flexible copper jumpers including arrangement by fixing M.S.Channel 100x50mm. | ELEC | labour | SWR11892 | 1323 | EA | 2646
108 | 80 | Providing of control cable trench as per DATA-XII | ELEC | labour | SWR22093 | 3148 | RMT | 251840
109 | 3074 | Control Cable-Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends . Lay-4C/10C 2.5Sqmm Control Cable | ELEC | labour | SWR11879 | 27 | M | 82998
110 | 270 | Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per specification (including cost of ferrules, lugs and glands) | ELEC | labour | SWR12510 | 27 | EA | 7290
111 | 4 | Marshalling Box Supply of FRP PT Marshalling Box | ELEC | supply | SMR40048 | 4463 | EA | 17852
112 | 4 | Marshalling Box Erection of Marshalling boxes | ELEC | labour | SWR10940 | 374.85 | EA | 1499.4
113 | 1 | Loading of 220 V Batterry with charger | ELEC | labour | SWR11166 | 1612 | SET | 1612
114 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
115 | 1 | Un loading of 220 V Batterry with charger | ELEC | labour | SWR11147 | 1024 | SET | 1024
116 | 1 | Batteries-Erection of 220 V, 200 AH battery in complete shape fit for charging . Conventional lead acid | ELEC | labour | SWR12350 | 7666 | EA | 7666
117 | 1 | Control Panels -Supply of DC Annunciation & relay panel for 10 feeder panel including the cost of LED Indiacation lamps, VAA auxilairy relays, Electronic Hooters complete as per specification. | ELEC | supply | SMR40044 | 42500 | EA | 42500
118 | 1 | Control Panels -Supply of AC Supply panel inluding providing of changeover switch, SFU, metering unit, 32 A three phase MCB, 16 A Single phase MCB complete as per specification. Supply of AC Supply panel complete | ELEC | supply | SMR40045 | 42000 | EA | 42000
119 | 2 | Fixing of AC/DC Panel and giving Connections to the protection equipment and Metering circuits as per the specification and standards. The 3 1/2 core 25 Sqmm power cable required from distribution box to AC/DC panel in the control room is also to be supply | ELEC | labour | SWR20025 | 7871.85 | SET | 15743.7
120 | 8 | Yard lightning-Supply of stepped tubular poles single way made of steel of length 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9 mm, 2.1 mtrs with outer dia 76.1 mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79 kgf as per IS 2713 | ELEC | supply | SMR40051 | 13913 | EA | 111304
121 | 8 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE/CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA /OSRAM /SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty S-90W LED fixture set | ELEC | labour | SMR11594 | 8200 | EA | 65600
122 | 8 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | ELEC | labour | SWR11039 | 928 | EA | 7424
123 | 8 | Erection of tubular poles | ELEC | labour | SWR10955 | 1379 | EA | 11032
124 | 5.27 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 34671.33
125 | 8 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE/CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA /OSRAM /SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty. Fixing of Metal halide lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5 GI pipe complete Fixing of LED/Metal halide complete. | ELEC | labour | SWR10956 | 1268 | EA | 10144
126 | 45 | Supply of HBG metal-Supply & spreading of 20mm machine crushed metal (HBG) including cost of conveneyance of all materials, labour charges etc complete for finished item of work and directed by the engineer incharge | ELEC | labour | SWR10860 | 2113 | M3 | 95085
127 | 2 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M Ex of Hard pit w/o blast 0.75X0.9X1.95M | ELEC | labour | SWR11040 | 990.68 | EA | 1981.36
128 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELEC | Supply | SMR40009 | 2181 | TO | 1635.75
129 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELEC | labour | SWR10877 | 851 | TO | 638.25
130 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELEC | Supply | SMR40010 | 1293 | TO | 969.75
131 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELEC | labour | SWR10879 | 482 | TO | 361.5
132 | 1 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Box pole 12 Mtr | ELEC | labour | SWR11267 | 3901.37 | EA | 3901.37
133 | 2.22 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 14605.38
134 | 1.16 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ELEC | labour | SWR10862 | 373 | M2 | 432.68
135 | 2 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | ELEC | labour | SWR11089 | 48 | EA | 96
136 | 1 | Construction of DTR Plinth-RCC Column type DTR Plinth of size 1'X1'X10',topslab 4'x4'x6" & beam size 4'X8'X8" upto 160KVA | ELEC | labour | SWR21843 | 25967.57 | EA | 25967.57
137 | 1 | Loading of 50,63, 75 & 100 KVA DTR | ELEC | labour | SWR10195 | 350 | EA | 350
138 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
139 | 1 | Un loading of 50,63, 75 & 100 KVA DTR | ELEC | labour | SWR10513 | 280 | EA | 280
140 | 1 | Erection of DTR's including loading and Unloading DTR on the Structure/Plinth etc-Erection of 3 Phase DTRs 63,75 & 100 KVA | ELEC | labour | SWR20905 | 1650 | EA | 1650
141 | 1 | Erection of AB Switch and aligment complete Erection of 11KV 200A TT type AB Switch including fixing of cross angles and alignment complete | ELEC | labour | SWR20102 | 1813.49 | EA | 1813.49
142 | 1 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erect. of 11kv HG Fuseset incl earthing | ELEC | labour | SWR10395 | 740.52 | SET | 740.52
143 | 40 | Excavation & laying of UG Cable in Single Run Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.-In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road-11KV 3x185 Sqmm Cable | ELEC | labour | SWR11920 | 465.46 | M | 18618.4
144 | 20 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-11 KV 3x185 Sqmm Cable | ELEC | labour | SWR11956 | 126.23 | M | 2524.6
145 | 2 | Making of Outdoor/Indoor End Termination Making 11 KV 3x185 Sqmm Cable Out Door/Indoor end termination | ELEC | labour | SWR10390 | 2370.63 | EA | 4741.26
146 | 1 | Erection of LT distribution box including laying of LT cable from distribution box to LT OH line and DTR to distribution box including earthing of distribution box and crimping of lugs connecting of jumpers etc | ELEC | labour | SWR10674 | 1594.67 | EA | 1594.67
147 | 85 | LAYING OF 33KV, 11KV UG CABLE Excavation & laying of UG Cable in Single Run Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road-LT 3 1/2 x 185 Sqmm Cable | ELEC | labour | SWR11923 | 377.63 | M | 32098.55
148 | 15 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-LT 3 1/2 x 185 Sqmm Cable | ELEC | labour | SWR11959 | 85.43 | M | 1281.45
149 | 2 | UG Cables Joints :-Making of Outdoor/Indoor End Termination -Supply & fixing of Oout Door/Indoor end termination LT 3 1/2 x 185 Sqmm Cable | ELEC | labour | SWR10765 | 968.9 | EA | 1937.8
150 | 1 | Supply and fixing of Substation board of size 3'x2.5' indicating the layout of switchyard Sup &fix of board ind Switchyard layout | ELEC | labour | SWR20032 | 1654 | EA | 1654
151 | 1 | Supply and fixing of safety instructions/Substation operation instruction board. Sup& fix safety inst/SS Op. inst board | ELEC | labour | SWR22090 | 2205 | EA | 2205
152 | 750 | Control Panels Supplying & fabrication erection of 6mm Checkerd plates as per the field conditions Supply,fabricati of 6mm Checkerd plates | ELEC | Labour | SWR10873 | 83 | KG | 62250
153 | 1 | T & P Supply of Wall clock standard make | ELEC | Supply | SMR40059 | 578 | EA | 578
154 | 1 | S-10ft Aluminium Ladder | ELEC | Supply | SMR12378 | 1654 | EA | 1654
155 | 1 | Sup Alluminium Ladder for indoor works | ELEC | Supply | SMR40062 | 4410 | EA | 4410
156 | 30 | T & P Painting of Name Plates for any equipmen | ELEC | labour | SWR10963 | 122 | EA | 3660
157 | 1 | T & P Supply of Taparia Tool kit of Size 20”x10”x15” with tier arrangements Tool box with locking arrangement & key containing (1) Double Ended fix Spanner sets, (Ribbed) 6 x 7, 8 x 9, 10 x 11, 12 x 13, 14 x 15, 16 x 17, 18 x19, 20 x 22, 21 x 23, 24 x 27, 25 x28, 30 x 32, (2) Double Ended Ring Spanners sets, 6 x 7 , 8 x 9, 10 x 11, 12 x 13, 14 x 15. 16 x 17 , 18 x 19, 20 x 22 , 21 x 23, 24 x 27, 25 x28, 30 x 32 mm, (3) Adjustable Spanner 305 mm length least maximum opening 35mm chrome, (4) Pipe Wrench Length 350 mm 14”, (5) Soft faced Hammer with suitable handle 2 lb, (6) Hacksaw frame with metal handle heavy duty for 12" hacksaw blade with High Speed blade, (7) Insulated Screw drivers Transparent Green Handle Set Length 6”, 8” & 12”, (8) Star Screw Driver Transparent Green Handle Length 6”, (9) Insulated Wire Cutter, (10) Insulated Cutting Plier Length 8” with cable stripper insulated with thick C. A. sleeve confirming to IS: 4378 - 1990, (11) Long Nose Plier insulated with thick C.A. sleeve generally confirming to IS:3552-1989, (12) Tester type screw driver (special with neon bulb) generally confirm to IS: 5579- 1985 Grade:II handle yellow/ green colour overall length 130 mm, (13) Insulated Crimping Plier of all Taparia make. SupTaparia Tool kit complete as per Spec | ELEC | Supply | SMR40063 | 4925 | SET | 4925
158 | 1 | T & P Sup Rechargeable LED torch light of Standard make | ELEC | Supply | SMR40064 | 1733 | EA | 1733
159 | 1 | T & P-Steel almarah(61/2 X 3ft) Godrej | ELEC | Supply | SMR40061 | 9818 | EA | 9818
160 | 1 | T & P-Table (3x6ft) Godrej | ELEC | Supply | SMR40057 | 6050 | EA | 6050
161 | 4 | T & P-S type chairs (Godrej) | ELEC | Supply | SMR40058 | 924 | EA | 3696
162 | 1 | T & P Sup Angle racks(18x36.6inches) Godrej | ELEC | Supply | SMR40060 | 1733 | EA | 1733
163 | 1 | T & P Supply of Hack saw (12 inches) | ELEC | Supply | SMR40065 | 289 | EA | 289
164 | 4 | Sup Earth Rods (8ft) Screw & clamp type | ELEC | Supply | SMR40066 | 578 | EA | 2312
165 | 2 | Supply of Hand Gloves | ELEC | Supply | SMR40067 | 289 | SET | 578
166 | 12 | SupRubber mats( 6'x3')size fo indoorSS | ELEC | Supply | SMR40068 | 1386 | EA | 16632
167 | 1 | Biometric Time attendence System & Telecom Sup Stand basic cell phone with charger | ELEC | Supply | SMR40069 | 1386 | EA | 1386
168 | 14 | Supply of Danger boards with clamps | ELEC | Supply | SMR40070 | 116 | EA | 1624
169 | 2 | Supply of Materials -Fire bucket stand with 3 buckets (8 -10 ltr capacity) | ELEC | Supply | SMR40088 | 1386 | SET | 2772
170 | 2 | Room fire extinguisher (2 ltrs capacity) for control room | ELEC | Supply | SMR40089 | 4620 | EA | 9240
171 | 4 | Sup TrollyMounted Co2 (6.5Kgs) Cylinders(IS-2878) | ELEC | Supply | SMR40087 | 9240 | EA | 36960
172 | 6 | Supply of Safety Helmet of standard make | ELEC | Supply | SMR40071 | 231 | EA | 1386
173 | 8 | Supply of LC Boards | ELEC | Supply | SMR40072 | 116 | EA | 928
174 | 4 | Supply of Gum Boots(Pairs) | ELEC | Supply | SMR40073 | 693 | EA | 2772
175 | 1 | Supply of 5000v megger | ELEC | Supply | SMR40074 | 13860 | EA | 13860
176 | 1 | Supply of Earth megger (1000v) | ELEC | Supply | SMR40075 | 8085 | EA | 8085
177 | 1 | Supply of Digital clamp meter. | ELEC | Supply | SMR40076 | 2888 | EA | 2888
178 | 1 | Name board of the 33/11kV Sub-Station(As per Standard Specification) Sup 33/11kv S.S Permanent name board | ELEC | Supply | SMR40086 | 10238 | EA | 10238
179 | 800 | Supply of Hot dip galvanized/zinc coated bolts & nuts including spring washers, pack washers and flat washers etc. | ELEC | Supply | SMR12488 | 90 | KG | 72000
180 | 2 | Fabrication of poles-Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | ELEC | labour | SWR10642 | 512.55 | EA | 1025.1
181 | 1 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-RS Joists 150x75/175 x 85 mm | ELEC | labour | SWR10346 | 1934 | EA | 1934
182 | 5760 | S-Supply of RS Joist Grider Pole (150x150mm) | ELEC | Supply | SMR12302 | 59.25 | KG | 341280
183 | 1000 | S-Supply of RS Joist Pole (175x85mm) | ELEC | Supply | SMR12303 | 60.75 | KG | 60750
184 | 5063 | S- Supply of MS Channel 100x50mm | ELEC | Supply | SMR22745 | 57.45 | KGS | 290869.35
185 | 13 | S-Supply of 33KV 800A DB Break AB Switch | ELEC | Supply | SMR12315 | 40658.78 | EA | 528564.14
186 | 8680 | S-Supply of RS Joist Grider Pole (150x150mm) | ELEC | Supply | SMR12302 | 59.25 | KG | 514290
187 | 4642 | S- Supply of MS Channel 100x50mm | ELEC | Supply | SMR22745 | 57.45 | KGS | 266682.9
188 | 17 | S-Supply of 11KV 800A DB Break AB Switch | ELEC | Supply | SMR12316 | 30847.46 | EA | 524406.82
189 | 3 | S-Supply of 11KV 400A DB Break AB Switch | ELEC | Supply | SMR12317 | 18150 | EA | 54450
190 | 3045 | S-Supply of MS Flat 75x8mm | ELEC | Supply | SMR12321 | 56.42 | KG | 171798.9
191 | 2666 | S-Supply of MS Flat 50x6mm | ELEC | Supply | SMR12322 | 56.5 | KG | 150629
192 | 750 | S-Supply of RS Joist Pole (175x85mm) | ELEC | Supply | SMR12303 | 60.75 | KG | 45562.5
193 | 1 | S-Supply of 11KV 200A Tilting Type AB Switch | ELEC | Supply | SMR12318 | 8991 | EA | 8991
194 | 1 | S-Supply of 11KV HG FuseSet for StationTransformer | ELEC | Supply | SMR12324 | 1974 | EA | 1974
195 | 1 | S-Supply of LT Distribution Box (SMC) | ELEC | Supply | SMR25200 | 7797 | EA | 7797
196 | 2 | S-Supply of 11KV 3x185 Heat Shble O/d End Term Kit | ELEC | Supply | SMR25201 | 1182.97 | EA | 2365.94
197 | 40 | S-Supply of LT XLPE Cable 1C 150 sqmm | ELEC | Supply | SMR25203 | 114.83 | M | 4593.2
198 | 100 | Supply of LT XLPE Cable 31/2C185sqmm. | ELEC | supply | SMR25204 | 547 | M | 54700
199 | 4 | Loading of LT AB Cable 3X16+25 Sqmm | ELEC | labour | SWR11702 | 200 | DR | 800
200 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
201 | 4 | Un loading of LT AB Cable 3X16+25 Sqmm | ELEC | labour | SWR11713 | 204 | DR | 816
202 | 16.5 | survey line&cabl inc peg mark&tree clear | ELEC | labour | SWR22092 | 765 | KM | 12622.5
203 | 16.5 | Paving out and stringing of conductor by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location-100 Sqmm Single Circuit (3 Conductors) | ELEC | labour | SWR10366 | 13856.7 | KM | 228635.55
204 | 330 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M Ex of Hard pit w/o blast 0.75X0.9X1.95M | ELEC | labour | SWR11040 | 990.68 | EA | 326924.4
205 | 330 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Errection of 11 M long PSCC pole | ELEC | labour | SWR10978 | 4336.85 | EA | 1431160.5
206 | 115.28 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 758427.12
207 | 330 | Painting of poles-Numbering of poles incl. cost of paint | ELEC | labour | SWR10378 | 32 | EA | 10560
208 | 80 | Excavation of pits in all soils except hard rock requiring blasting-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") 1.05 cum | ELEC | labour | SWR10107 | 700 | EA | 56000
209 | 80 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Erec of 9.1 Mts PSCC poles for stuts | ELEC | labour | SWR11083 | 2400 | EA | 192000
210 | 42 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 276318
211 | 55 | Formation of Cut points - Formation of Cut point for 11 KV Single Circuit line excluding pole erection and stays Formatn of Horiz Cut point for 11KV line | ELEC | labour | SWR10653 | 1435.81 | EA | 78969.55
212 | 500 | Supply of earthing pipe with materials S-GI Bolts & Nuts,Washers etc., | ELEC | supply | SMR11488 | 117.5 | KG | 58750
213 | 8 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 50 Km and upto 80 Km with Lorry for each trip | ELEC | labour | SWR11864 | 5290.74 | EA | 42325.92
214 | 15 | LOADING of Conductor drums | ELEC | labour | SWR10191 | 202 | EA | 3030
215 | 15 | UNLOADING of Conductor drums | ELEC | labour | SWR10509 | 100 | EA | 1500
216 | 100 | Loading of 33 KV Pin insulators | ELEC | labour | SWR10211 | 3 | CRT | 300
217 | 100 | Un loading of 33 KV Pin insulators | ELEC | labour | SWR10529 | 3 | CRT | 300
218 | 15 | Loading of 33 KV Metal parts | ELEC | labour | SWR10618 | 65 | BAG | 975
219 | 15 | Un loading of 33 KV Metal parts | ELEC | labour | SWR10632 | 65 | BAG | 975
220 | 560 | Excavation & laying of UG Cable (Double Run) Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, Along the CC / BT multi layer road requiring compressor-33 KV 3x400 Sqmm Cable | ELEC | labour | SWR11980 | 1388.84 | M | 777750.4
221 | 560 | Laying of 2nd cable in excavated trench | ELEC | labour | SWR10988 | 204.1 | M | 114296
222 | 40 | Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-33 KV 3x400 Sqmm Cable | ELEC | labour | SWR12004 | 323.85 | M | 12954
223 | 12 | Cost of Pipes and slabs-Supply of 6" B class GI pipe | ELEC | supply | SMR40081 | 1044 | M | 12528
224 | 30 | Cost of Pipes and slabs-Supply of 250 mm Hume pipe of class NP3 with compresive strength of 35N/mm2 for 28 days curing,barewall thickness of 30mm,1.25kG linear/meter and withstanding capability of 22.50KN/linear meter as per IS 458-1993. | ELEC | supply | SMR40077 | 363 | M | 10890
225 | 6 | Cost of Pipes and slabs-Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters , CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | ELEC | supply | SMR40085 | 484 | EA | 2904
226 | 4 | Load-11/33KV XLPE UG Cable for all sizes | ELEC | labour | SWR11230 | 1024 | DR | 4096
227 | 4 | Unload-11/33KV XLPE UG Cable for all sizes | ELEC | labour | SWR11231 | 1024 | DR | 4096
228 | 8 | Making of Outdoor/Indoor End Making 33 KV 3x400 Sqmm Cable Out Door/Indoor end termination TerminationOD/Idoor end termination 33kv 3x400 xlpe | ELEC | labour | SWR10387 | 2764.76 | EA | 22118.08
229 | 2 | UG Cables Joints 33 KV 3x400 Sqmm Cable Straight through joint 33kv 3x400 xlpe | ELEC | labour | SWR10382 | 5700.78 | EA | 11401.56
230 | 4.5 | Fabrication & erection of Channels -Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to theRS-Joist poles excluding cost of Mild Steel and transportcharges to substation site, including erection. Fabrication of struc.with welding. | ELEC | labour | SWR10869 | 3426 | TO | 15417
231 | 50 | Supply of earthing pipe with materials-Supply of GI wire No 8 | ELEC | supply | SMR11486 | 105 | KG | 5250
232 | 2 | Supply of earthing pipe with materials-Supply of CI eath pipe with 80mm dia,2.0 M Length | ELEC | labour | SMR11483 | 2789 | EA | 5578
233 | 2 | Providing of Earthing-Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | ELEC | labour | SWR10357 | 1234.2 | EA | 2468.4
234 | 2 | Providing of RCC collar to earth pit-Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINES-Providing of RCC collar | ELEC | labour | SWR10359 | 386 | EA | 772
235 | 40 | Supply of earthing pipe with materials-Supply of GI Flat 25X3 mm | ELEC | supply | SMR11485 | 105 | KG | 4200
236 | 20 | Supply of Danger boards with clamps | ELEC | supply | SMR40070 | 116 | EA | 2320
237 | 6 | S&E-Smart RFID marker | ELEC | labour | SWR25089 | 2745 | EA | 16470
238 | 330 | Supply of PSCC Pole 11Mtr 365KG | ELEC | supply | SMR25236 | 5399 | EA | 1781670
239 | 80 | Supply of PSCC Pole 9.1Mtr 280KG | ELEC | supply | SMR25233 | 3109.41 | EA | 248752.8
240 | 2500 | Supply of Materials -- Supply of MS Channel 100X50mm | ELEC | supply | SMR22745 | 57.45 | KGS | 143625
241 | 1500 | Supply of MS Angle 65x65x6 | ELEC | supply | SMR25207 | 57.25 | KG | 85875
242 | 500 | Supply of Materials -- Supply of MS Flat 75x8 mm | ELEC | supply | SMR12321 | 56.42 | KG | 28210
243 | 8 | UG Cables Joints : Making of Outdoor/Indoor End Termination -- Supply 33KV 3x400Sqmm Outdoor | ELEC | supply | SMR22222 | 4554 | EA | 36432
244 | 2 | UG Cables Joints : Making of Straight through joints -- Supply of 33KV 3x400SQmm Straight Through Joint Kit | ELEC | supply | SMR22223 | 24151 | EA | 48302
245 | 275 | Supply of 33KV V-Cross Arm without Clamps | ELEC | supply | SMR25229 | 1678 | EA | 461450
246 | 9 | survey line&cabl inc peg mark&tree clear | ELEC | labour | SWR22092 | 765 | KM | 6885
247 | 9 | Paving out and stringing of conductor by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location-55 Sqmm Single Circuit (3 Conductors) | ELEC | labour | SWR10365 | 9454.81 | KM | 85093.29
248 | 175 | Excavation of pits in all soils except hard rock requiring blasting-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") 1.05 cum | ELEC | labour | SWR10107 | 700 | EA | 122500
249 | 50 | Excavation of pits in hard rock requiring blasting. (other than SS)-9.1Mtrs PSCC Pole 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | ELEC | labour | SWR10112 | 1770 | EA | 88500
250 | 213 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-9.1 M long PSCC pole | ELEC | labour | SWR10343 | 2400 | EA | 511200
251 | 37.8 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 248686.2
252 | 225 | Painting of poles-Numbering of poles incl. cost of paint | ELEC | labour | SWR10378 | 32 | EA | 7200
253 | 80 | Excavation of pits in all soils except hard rock requiring blasting-Stud Poles 0.6 M x 0.9 M x 1.5 M | ELEC | labour | SWR10106 | 645 | EA | 51600
254 | 80 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-8.0 m long PSCC poles for Strut | ELEC | labour | SWR21590 | 1500 | EA | 120000
255 | 32 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 210528
256 | 40 | Formation of Cut points - Formation of Cut point for 11 KV Single Circuit line excluding pole erection and stays Formatn of Horiz Cut point for 11KV line | ELEC | labour | SWR10653 | 1435.81 | EA | 57432.4
257 | 350 | Supply of earthing pipe with materials S-GI Bolts & Nuts,Washers etc., | ELEC | supply | SMR11488 | 117.5 | KG | 41125
258 | 4 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 13198.8
259 | 4 | LOADING of Conductor drums | ELEC | labour | SWR10191 | 202 | EA | 808
260 | 4 | UNLOADING of Conductor drums | ELEC | labour | SWR10509 | 100 | EA | 400
261 | 6 | Supply of earthing pipe with materials-Supply of CI eath pipe with 50mm dia,2.0 M Length | ELEC | supply | SMR11484 | 2441 | EA | 14646
262 | 6 | Providing of Earthing-Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | ELEC | labour | SWR10357 | 1234.2 | EA | 7405.2
263 | 6 | Providing of RCC collar to earth pit-Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINES-Providing of RCC collar | ELEC | labour | SWR10359 | 386 | EA | 2316
264 | 6 | Assembly and erection of Structure as per specification which includes fixing of top channels and cross bracings, transport of all materials from road side to the location, earthing, back filling with earth ramming etc excluding pit excavation and concreting.-11KV DP Structure with 9.1 Mtrs PSCC Poles | ELEC | labour | SWR21130 | 3363.96 | SET | 20183.76
265 | 6 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | ELEC | labour | SWR10393 | 3200 | EA | 19200
266 | 6 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | ELEC | labour | SWR10881 | 142 | EA | 852
267 | 50 | Supply of earthing pipe with materials-Supply of GI wire No 8 | ELEC | supply | SMR11486 | 105 | KG | 5250
268 | 675 | Loading of 11KV Polymer Pin Insulators with GI pins | ELEC | labour | SWR11248 | 1 | EA | 675
269 | 675 | Un loading of 11KV Polymer Pin Insulators with GI pins | ELEC | labour | SWR11249 | 1 | EA | 675
270 | 240 | Loading of 11KV Polymer Pin Insulators with GI pins | ELEC | labour | SWR11248 | 1 | EA | 240
271 | 240 | Un loading of 11KV Polymer Pin Insulators with GI pins | ELEC | labour | SWR11249 | 1 | EA | 240
272 | 6 | Loading of 11 KV Metal parts | ELEC | labour | SWR12402 | 48 | BAG | 288
273 | 6 | Un loading of 11 KV Metal parts | ELEC | labour | SWR12421 | 48 | BAG | 288
274 | 960 | Laying of 2nd cable in excavated trench | ELEC | labour | SWR10988 | 204.1 | M | 195936
275 | 72 | Cost of Pipes and slabs-Supply of 6" B class GI pipe | ELEC | supply | SMR40081 | 1044 | M | 75168
276 | 200 | Cost of Pipes and slabs-Supply of 250 mm Hume pipe of class NP3 with compresive strength of 35N/mm2 for 28 days curing,barewall thickness of 30mm,1.25kG linear/meter and withstanding capability of 22.50KN/linear meter as per IS 458-1993. | ELEC | supply | SMR40077 | 363 | M | 72600
277 | 6 | Cost of Pipes and slabs-Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters , CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | ELEC | supply | SMR40085 | 484 | EA | 2904
278 | 5 | Load-11/33KV XLPE UG Cable for all sizes | ELEC | labour | SWR11230 | 1024 | DR | 5120
279 | 5 | Unload-11/33KV XLPE UG Cable for all sizes | ELEC | labour | SWR11231 | 1024 | DR | 5120
280 | 1.1 | Fabrication & erection of Channels -Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to theRS-Joist poles excluding cost of Mild Steel and transportcharges to substation site, including erection. Fabrication of struc.with welding. | ELEC | labour | SWR10869 | 3426 | TO | 3768.6
281 | 50 | Supply of Danger boards with clamps | ELEC | supply | SMR40070 | 116 | EA | 5800
282 | 6 | S&E-Smart RFID marker | ELEC | labour | SWR25089 | 2745 | EA | 16470
283 | 960 | Excavation & laying of UG Cable (Double Run)-Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts,-In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil/CC-11 KV 3x300 Sqmm Cable | ELEC | labour | SWR11973 | 631.06 | M | 605817.6
284 | 240 | Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-11 KV 3x300 Sqmm Cable | ELEC | labour | SWR12005 | 275.4 | M | 66096
285 | 24 | Making of Outdoor/Indoor End Termination-Making 11 KV 3x300 Sqmm Cable Out Door/Indoor end termination | ELEC | labour. | SWR10391 | 2370.63 | EA | 56895.12
286 | 6 | UG Cables Joints Making of Straight through joints-11 KV 3x300 Sqmm Cable | ELEC | labour. | SWR10386 | 3725.45 | EA | 22352.7
287 | 225 | Supply of PSCC Pole 9.1Mtr 280KG | ELEC | supply | SMR25233 | 3109.41 | EA | 699617.25
288 | 80 | Supply of PSCC Pole 8Mtr 140KG | ELEC | supply | SMR25232 | 1580 | EA | 126400
289 | 185 | S-Supply of 11KV Top Cleat for 9.1M(Vertical) | ELEC | Supply | SMR25226 | 256 | EA | 47360
290 | 80 | Supply of 11KV Horizontal Cross Arm | ELEC | supply | SMR25223 | 528 | EA | 42240
291 | 6 | Supply of Materials -- Supply of 11 kV 400 A Double break AB switch | ELEC | supply | SMR12317 | 18150 | EA | 108900
292 | 200 | Supply of Materials -- Supply of MS Flat 50x6 mm | ELEC | supply | SMR12322 | 56.5 | KG | 11300
293 | 400 | Supply of MS Angle 50x50x6 | ELEC | supply | SMR25206 | 58.15 | KG | 23260
294 | 500 | Supply of MS Channel 75x40 mm | ELEC | supply | SMR25205 | 58.45 | KG | 29225
295 | 24 | Supply of 11KV 3x300 Heat Shble O/d End Term Kit | ELEC | supply | SMR25208 | 1372.88 | EA | 32949.12
296 | 6 | Supply of 11KV 3x300 Heat Shble stright through joint Kit | ELEC | supply | SMR25210 | 4110.17 | EA | 24661.02
297 | 185 | supply of V X-Arm with MS Angle 65x65x6 | ELEC | supply | SMR25218 | 743 | EA | 137455
298 | 6 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | ELEC | labour | SWR12331 | 146.63 | EA | 879.78
Sub Total: | [7 empty] | 17978083.735
Civil labour-WBS. No. S-1788-13-07-01-01-001
Sl.No. | Estimate Quantity (only Figures) | Item Detailed Specification Description | Work Type eg. Earth Work, Electrical works. etc (upto 200 Characters) | Item Short Description (upto 100 Characters) | APSS / Morth Cl. Number (upto 200 Characters) | Rate (INR) (Upto 2 Decimals ) | UOM (upto 50 Characters) | Amount
1 | 32 | Leveliing the site by cutting and levelling with the help of JCB including cost,conveyance of all materials,hire chareges etc complete for finished item of work as directed by Engineer-in-charge. | Civil | Labour | SWR34179 | 2165 | Hrs | 69280
2 | 135.61 | Earth work excavation in all type of ordinary soils red earth, Hard gravelly soils, earth mixed with sand and sandy soils etc., in all conditions such as slushy and dry with initial leads and lifts for foundations. | Civil | Labour | SWR33015 | 486 | m3 | 65906.46
3 | 32.45 | Plain Cement concrete PCC (1:4:8) using 40mm HBG metal for foundations and leveling course, including cost and conveyance of all materials, labour all leads and lifts, consolidation and all operations, formwork as required, curing, etc. complete for finished item w | Civil | Labour | SWR33028 | 4791 | m3 | 155467.95
4 | 117.88 | Coursed Rubble stone (CRS) masonry 2nd sort with hard granite stones in cement mortar (1:6) for basement, including cost and conveyance of all materials, labour charges, curing, all leads and lifts, etc, complete for finished item of work. | Civil | Labour | SWR33041 | 4906 | m3 | 578319.28
5 |  | 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge
6 | 3.564 | RCC M20 Grade footing 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33098 | 9543 | m3 | 34011.252
7 | 2.28 | RCC M20 Grade Coloumn . 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33100 | 13292 | m3 | 30305.76
8 | 2.25 | RCC M20 Grade Plinth beams 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33099 | 12414 | m3 | 27931.5
9 | 3.17 | D) RCC M20 Grade Roof Beams landing beam 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33121 | 12330 | m3 | 39086.1
10 | 0.58 | e)RCC M20 Grade Lintels 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33107 | 13121 | m3 | 7610.18
11 | 2.7 | f) RCC M20 Grade Sunshades 600mm wide and 75mm thick'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33114 | 1379 | m2 | 3723.3
12 | 15.224 | g) RCC M20 Grade Roof Slab for Control Room 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33128 | 10918 | m3 | 166215.632
13 | 3 | Reinforcement steelSupplying, Cutting, bending, binding, placing in position and tying reinforcement steel in all heights including cost and conveyance of steel and binding wire etc,. With all leads and lifts, labour charges, etc., complete for finished item of work. | Civil | Labour | SWR33144 | 70687 | Ton | 212061
14 | 38.36 | Brick masonry in cement mortar CM (1:6) for superstructure using well burnt country made second class bricks of approved quality including cost and conveyance of all materials curing, scaffolding with all leads and lifts in all heights etc., complete for fin | Civil | Labour | SWR33068 | 8293 | m3 | 318119.48
15 | 2.7 | Plain Cement concrete PCC (1:2:4) using 20mm size well graded HBG metal for foundations, including cost, conveyance of all materials,labour all leads and lifts,consolidation and all operations, formwork as required, curing,etc. complete for finished item of work | Civil | Labour | SWR33030 | 6160 | m3 | 16632
16 | 606.06 | Plastering with CM 2 coats, 20 mm thick, base coat in CM (1:6), 16 mm thick and top coat in CM (1:4), 4mm thick with Dubara sponze finishing including cost of all materials, seigniorage charges, excluding conveyance charges of materials and including all operational, incidental and labour charges for mixing mortar, laying rendering smooth and thread lining, curing, rounding off junctions of wall and slab etc., complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33163 | 565 | m2 | 342423.9
17 | 349.515 | Painting with two coats of Plastic Emulsn paint over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33356 | 210 | m2 | 73398.15
18 | 200.85 | Painting with two coats of Surya Cem paint over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33329 | 85 | m2 | 17072.25
19 | 3 | Supply and Fixng of MS Name Board including cost & conveyance of all materials,labour charges etc complete for finished item of work. | Civil | Labour | SWR33421 | 4326 | m2 | 12978
20 | 1 | Geophysical Investgation charges for water point by Geologist | Civil | Labour | SWR33608 | 5000 | EA | 5000
21 |  | Drilling of 165mm bore well with machine rig including deployment and hire charges of rig and other machinery and equipment labour charges , measuring the yeild of borewell including cost and conveyance etc complete
22 | 90 | Drill-165mm Bore Well 0 to 90 | Civil | Labour | SWR33609 | 336 | M | 30240
23 | 30 | Drill-165mm Bore Well 90M to 120M | Civil | Labour | SWR34830 | 369 | M | 11070
24 | 30 | Drill-165mm Bore Well 120M to 150M | Civil | Labour | SWR34831 | 394 | M | 11820
25 | 30 | Drill-165mm Bore Well 150M to 180M | Civil | Labour | SWR34832 | 492 | M | 14760
26 | 30 | Drill-165mm Bore Well 180M to 210M | Civil | Labour | SWR34833 | 623 | M | 18690
27 | 30 | Drill-165mm Bore Well 210M to 240M | Civil | Labour | SWR34834 | 754 | M | 22620
28 | 30 | Drill-165mm Bore Well 240M to 270M | Civil | Labour | SWR34835 | 918 | M | 27540
29 | 82 | Drill-165mm Bore Well 270M and above | Civil | Labour | SWR34836 | 1082 | M | 88724
30 | 40 | Supply and fixing of 160mm dia PVC casing of A class 6Kg point pressure including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR33611 | 883 | M | 35320
31 | 1 | Supply and erecting, ISI mark submersible 5.0 HP, Single Phase 30 stages pumpset suitable for 106/156mm dia borewell including cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33640 | 48007 | EA | 48007
32 | 290 | Supply and fixing of HDPE pipe 40mm dia of 16Kg/cm2 including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR34410 | 180 | M | 52200
33 | 1 | Supply and erecting D.O.L Starter 415V , Single phase,50Hz with SS enclouserincluding cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33645 | 7854 | EA | 7854
34 | 300 | Supply of 3 Core 2.5 Sqmm Flat Copper cable of ISI for Submersible Motors of makes Finolex / Polycab / Gold Medal / Million / Payal / Sun Light / Power Flex / Fortune Art | Civil | Labour | SWR33641 | 192 | m | 57600
35 | 71 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-28.60mm OD Pipe - SDR 11 | Civil | Labour | SWR34363 | 410 | m | 29110
36 | 35 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type - 25mm NB Size | Civil | Labour | SWR34346 | 466 | EA | 16310
37 | 839.38 | Supplying and filling the substation site with borrowed gravel, watering, ramming, thoroughly complying with the standard specification. | Civil | Labour | SWR33052 | 309 | m3 | 259368.42
38 | 16.56 | Providing Design R.C.M. drop wall of 25mm thickness with cm 1:3 and 6mm dia MS bars at 150mm both ways and chicken mesh in two coats 20mm thick each plastering including cost and conveyance of all materials with leads and lifts, scaffolding and curing, labo | Civil | Labour | SWR33203 | 3125 | m2 | 51750
39 | 12.24 | Supply and fixing of Ms ornamental safety grill of approved design including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33310 | 2990 | m2 | 36597.6
40 | 5.91 | Supply and fixing of doors with the MT Wood frames of the door shall be made well seasoned mt wood of cross section 100x75mm. The shutter shall be made isi mark flushed door with decolam sheets pasted on both sides with PVC beading 40mm width all round.Frame shall be painted with two coats of synthetic enamel paint of approved color over one coat of primer over luppum with spary with 3 no 150mm brass hinges 1 no brass door stoper, 1 no 250mm brass aldrops. 2 no 300 mm aluminium tower bolts, 2 no 150mm brass fancy door handlers, 1 no keyless lockset with cp handel. The quoted rate shall include cost and conveyance of the meterials, fixig, labour carges, tools, handles,locking arrangementts and other fixtures & fittings for finished item work as directed by the Engineer - in- charge. | Civil | Labour | SWR33264 | 7314 | m2 | 43225.74
41 | 128.25 | Raised pointing to the exposed surfaces of CRS masonry in cm 1:3 prop. including cost and conveyance of all materials, labour charges, all leads and lifts curing etc, complete for finished item of work. | Civil | Labour | SWR33184 | 126 | m2 | 16159.5
42 | 8.64 | Supplying and fixing Aluminium sliding windows with grill and fixed glass panels using anodised aluminium extruded sections of mat finish for frames and mullions made from approved aluminium sections 62x32x1.2mm at 0.73kg/Rm providing 5mm plain glass fix | Civil | Labour | SWR33277 | 3623 | m2 | 31302.72
43 | 16.56 | Supply and laying of Ceramic floor over of CM 1:3 20 mm thick including required materials and labour charges etc complete for item of work | Civil | Labour | SWR33224 | 914 | m2 | 15135.84
44 | 121.92 | Flooring with double machine polished and hand cut Tandur blue stone 20mm thick of approved colour, quality and of minimum of 300x300mm size over a bed of cement mortar 1:3 20mm thick including cost of all materials, with all leads and lifts jointing and | Civil | Labour | SWR33219 | 788 | m2 | 96072.96
45 | 6.74 | Supply and fixing of 4" high skirting of shabad stone to the walls including cost and conveyance of all materials, labour etc for finished item of work. | Civil | Labour | SWR33236 | 878 | m2 | 5917.72
46 | 243.69 | Painting with two coats of OBD over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials labour charges etc., complete for finished item of work. | Civil | Labour | SWR33333 | 146 | m2 | 35578.74
47 | 101.17 | Providing impervious coat over RCC roof slab to requried slopes with 20mm thick in CM 1:3 mixed with approved brand of water proffing compound inclding cost and conveyance of all materials, labour charges, curing, rounding off junctions of wall and slab, all leads and lifts, etc . complete for finished item of work as directed by the Engineer - in - charge. | Civil | Labour | SWR33156 | 587 | m2 | 59386.79
48 | 60 | Supply & fixing of 25mm dia 2mm thick suSupply & fixing of 25mm dia 2mm thick surface P.V.C. pipe (ISI MARK) Concealed in wall with all required accessories including masonary work and labour charges etc.complete. | Civil | Labour | SWR33441 | 108 | m | 6480
49 | 1 | Supply & fixing TPN Distribution board w Supply & fixing TPN Distribution board with IP-42 protection (Metal Door)suitable for 3 phase ELCB/RCCB/FP Isolator as incomer and 10kA SP MCBs as out going including internal connection and labour charges for surface / flush mounting etc Complete. | Civil | Labour | SWR33526 | 11353 | EA | 11353
50 | 10 | Supply & fixing of 6A 3 pin wall plug socket with 6A switch control on a common switch board with earth continuity including wire leads,earth connection along with all labour charges etc., complete | Civil | Labour | SWR33468 | 166 | EA | 1660
51 | 6 | Supply & fixing of 16A 3 pin and 6A 3pin plug Flush type socket with indicator lamp and 16Amps fuse unit and 16Amps switch control (5 in one )duly recessed in wall with wooden deep box of 6'' x 8'' x 2 1/2'' size covered with hylam sheet earth connection and all labour charges etc., complete on wall. | Civil | Labour | SWR33470 | 449 | EA | 2694
52 | 24 | Supply and Fixing of modular switch, LP,FP,EFP Wiring with 2 runs of 14/0.3mm (1.0 sq.mm)Fire Retardant (FR) P.V.C. insulated flexible copper cable (ISI MARK) in existing pipe with 6A Flush type Switch,ceiling rose and 3mm thick hylam sheet covering to switch control box including all labour charges etc., complete for light points, bell , fan and exhaust fan points in Non-Residential Buildings. | Civil | Labour | SWR33457 | 676 | EA | 16224
53 | 12 | Supply & Fixing of 28W T5 fluorescent tube. | Civil | Labour | SWR33558 | 148 | EA | 1776
54 | 1 | Supply of 12" (300mm)ISI, 900 RPM Heavy duty exhaust fan with metallic blades with Mark of makes Crompton / Bajaj / Havells / Orient. | Civil | Labour | SWR33571 | 2192 | EA | 2192
55 | 180 | Supply and run of 2 of 22/0.3mm (1.5 sq.mm) (FR) P.V.C. insulated flexible copper cable in existing pipe for mains including all labour charges complete. | Civil | Labour | SWR33496 | 75 | m | 13500
56 | 180 | Supply and run of 2 of 36/0.3mm (2.5 sq.mm) FR P.V.C. insulated flexible copper cable in existing pipe for mains including all labour charges complete. | Civil | Labour | SWR33497 | 103 | m | 18540
57 | 12 | Supply & fixing of batten holder /slanting holder in lieu of ceiling rose of light point complete with all connection and all labour charges with 40W bulb (for new installation). | Civil | Labour | SWR33484 | 141 | EA | 1692
58 | 4 | Supply & fixing of 1200mm (48'') sweep 230v,A.C 50 Hz.Ceiling fan with 3 Blades and double ball bearings with all standared accessories. | Civil | Labour | SWR33563 | 2277 | EA | 9108
59 | 4 | Supply & fixing of Electronic Regulator for ceiling fans 900/1200/1400mm sweep including cost of material, Electrical charges complete for finished item of work | Civil | Labour | SWR33564 | 589 | EA | 2356
60 | 1 | Providing independent EARTHING by excavating a trench to a depth of 2.1M in all solid,as per size specified in the Data,using 40mm dia 'B' class GI pipe of 2.5 Mtrs length with necessary accessories with hume pipe ring duly providing staggered holes including filling with equal proportion of salt and Charcoal in layers and all labour charges etc., compiete for small quarters. | Civil | Labour | SWR33596 | 5345 | EA | 5345
61 | 35 | Supplying, laying, jointing and testing 101.6 mm SWG SP-1 pipes of ISI make conforming to ISI 651 & 4127 with airtight cement joints in CM 1.5:1 prop. Including excavation of trenches and socket pits in any soil (except rock requiring blasting) up to 1524 mm(5'0") depth and refilling with watering and tamping. | Civil | Labour | SWR34281 | 755 | m | 26425
62 | 3 | Constructing 904.0 mm (3#0#) dia brick masonry inspection chamber as per IS - 4111: Part-1:1986 with cement mortar (1:6) prop using 2nd Class Clay Bricks of 225 mm thick from approved source having a minimum crushing strength of 5 N/sq.mm including plastering with cement mortar 1:3 prop; ½# thick both inside and outside fitted with 20# dia RCC manhole covers and frames including excavating pits up to a depth of 904 mm (3'-0") in all sorts of soils (excluding rock) and laying cement concrete (1:4:8) 150 mm thick using 40 mm HBG Metal and P.C.C. 1:2:4 benching and channel 100 mm thick as per Standard specification and including cost and conveyance of all materials like cement, sand, bricks, water etc., to site, cost of seigniorage charges on all materials and all incidental and operational, labour charges like mixing cement mortar, constructing masonry, lift charges, curing etc., complete for finished item of work as per Standard specification. | Civil | Labour | SWR34296 | 8766 | EA | 26298
63 | 4 | Supply & fixing of 110 mm dia - Door Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34381 | 128 | EA | 512
64 | 4 | Supply & fixing of 110 mm dia - Plain Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34380 | 100 | EA | 400
65 | 12 | Supply & fixing of 110 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand | Civil | Labour | SWR34377 | 462 | m | 5544
66 | 18 | Supply & fixing of 90 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand | Civil | Labour | SWR34378 | 410 | m | 7380
67 | 3 | Supplying & fixing 150 mm x 100 mm SWG gully traps conforming to ISI 651 & 4127 with C.I Grating & Cost. Brick masonry in CM 1:6 prop. Intermediate chamber and fitted with 304.8 mm x 288.6mm (12"x9") C.I Frame and hinged cover | Civil | Labour | SWR34286 | 767 | EA | 2301
68 | 1 | Supplying and Fixing of European Water Closet of 1st Quality | Civil | Labour | SWR34312 | 2228 | EA | 2228
69 | 6 | Supply & fixing 15 mm angle stop cock Indian make 400 grams Seiko/ Senior/ Nice/ Senior/ Nice or equivalent | Civil | Labour | SWR34328 | 721 | EA | 4326
70 | 4 | S&F 15 mm N.P bib tap Indian make 400 grams full turn Seiko/ Senior/ Nice or equivalent | Civil | Labour | SWR34329 | 296 | EA | 1184
71 | 1 | Supplying & Fixing Indian make Flat Back Wash Hand Basin (HSW/Parryware/ Neycer) 1st quality conforming to IS:2556-Part-4:1972 with waste fittings like rubber plug, chain, 32 mm nominal size C.P. Fitting with parallel pipe thread conforming to IS:2963-1979 and fitted with 15 mm nominal bore Chromium Plated Pillar Tap of 1st quality Indian make 400 grams Seiko/ Senior/ Nice/ Esso or equivalent complete with standard CI brackets including wooden block: 550 x 400 mm - Single C.P. Pillar cock | Civil | Labour | SWR34316 | 1717 | EA | 1717
72 | 2 | Supply & fixing 38.1 mm C.P waste coupling Half or Full Thread 1st Quality Indian make Parryware or equivalent | Civil | Labour | SWR34428 | 309 | EA | 618
73 | 2 | Supply & fixing of 4" (101.6 mm ) Nahany Trap ( Without Jali with inlet)UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34387 | 134 | EA | 268
74 | 1000 | Providing & Placing on Terrace (at all floor levels) polyethylene water storage tank with Double layer approved brand & manufacture with cover and suitable locking arrangement & making necessary holes for inlet & outlets and over flow pipes but with NECESSARY fittings & base support for tanks | Civil | Labour | SWR34375 | 10 | L | 10000
75 | 2 | Supply & fixing 31.75 mm dia PVC flexible waste pipe of 914.4 mm length of Ist quality | Civil | Labour | SWR34426 | 33 | EA | 66
76 | 45 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)- 15.90mm OD Pipe - SDR 11 | Civil | Labour | SWR34361 | 239 | m | 10755
77 | 200 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-22.20mm OD Pipe - SDR 11 | Civil | Labour | SWR34362 | 313 | m | 62600
78 | 4 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type -20mm NB Size | Civil | Labour | SWR34345 | 331 | EA | 1324
79 | 1 | Supply & fixing 25.4 mm dia & 609.6 mm long aluminium anodized towel rod with brackets and aluminium screws | Civil | Labour | SWR34430 | 489 | EA | 489
80 | 36 | Plain Cement concrete PCC (1:3:6) using 40mm HBG metal for foundations and leveling course, including cost and conveyance of all materials, labour all leads and lifts, consolidation and all operations, formwork as required, curing, etc. complete for finished item w | Civil | Labour | SWR33029 | 5081 | m3 | 182916
81 | 120 | Supply&Fabrication and fixing of Welded wire mesh ( 2" x 2") of 3mm dia. with ISMC (75x40x4.4mm) and Pheriperal frame of ISA(35x35x3mm) incldg cost& conveyance painting with synthetic enamil paint two coats over a coat of red oxide primer etc complete for finished item of work.. | Civil | Labour | SWR33403 | 2310 | m2 | 277200
82 | 1 | Providing Consultancy services for arranging contour surveying with total station incuding preparation of boundary and contour levels with 2 Nos. Hard copies and soft copies complete for finished items of work | Civil | Labour | SWR33427 | 5665 | EA | 5665
83 | 222.2468 | Seigniorage Charges - Sand | Civil | Labour | SWR34470 | 40 | m3 | 8889.873
84 | 725.7496 | Seigniorage Charges - Metal | Civil | Labour | SWR34471 | 97.5 | m3 | 70760.585
85 | 839.38 | Seigniorage Charges - Gravel | Civil | Labour | SWR34472 | 30 | m3 | 25181.4
86 | 60 | Supply and fixing of RCC fencing poles of size 0.1mx0.1mx1.8m (security fencing of sub station), including cost and conveyance of all labour, materials,and hire chareges etc complete for finished item of work. | Civil | Labour | Swr33405 | 1444 | EA | 86640
87 | 1200 | Supply and fixing of galvanised barded wire (1 horizantal & 2 cross strands. including cost and conveyance of all labour, materials,and hire chareges etc complete for finished item of work. | Civil | Labour | Swr33408 | 16 | m | 19200
Total Rs. | [7 empty] | 4231711.082
Total elec+civil |  |  | 18% GST Rs. |  |  |  |  | 22209794.817

## 5. Meeralam Park
Name of the work: Estimate for erection of new 33/11kV outdoor SS at Miralam Park with 2x8 MVA PTRs and connected 33kV, 11kV Lines at Miralam Park(9 Number) in Rajendranagar (M) in ECGH Division/Masterplan/RRCircle
WBS No. S-1789-13-03-02-01-001
Sl No | Estimate Quantity | Description of item | Work Type | Item Short Description | APSS / Month Cl.NumberSSR 11 & 12 | Rate (INR) | UOM | AMOUNT
1 | 16 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | ELEC | Labour | SWR11039 | 928 | EA | 14848
2 | 5.76 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ELEC | Labour | SWR10868 | 6852 | TO | 39467.52
3 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELEC | supply | SMR40009 | 2181 | TO | 12562.56
4 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELEC | labour | SWR10877 | 851 | TO | 4901.76
5 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELEC | supply | SMR40010 | 1293 | TO | 7447.68
6 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELEC | labour | SWR10879 | 482 | TO | 2776.32
7 | 5.76 | Fabrication & erection of Channels-Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ELEC | labour | SWR10867 | 1470 | TO | 8467.2
8 | 16 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-R.S. Joists 150 x 150 mm | ELEC | labour | SWR10348 | 1952.61 | EA | 31241.76
9 | 17.758 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 116829.882
10 | 9.24 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ELEC | labour | SWR10862 | 373 | M2 | 3446.52
11 | 16 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | ELEC | labour | SWR11089 | 48 | EA | 768
12 | 4 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-8.0Mtrs PSCC Poles 0.76 M x 0.76M x 1.52M (2.6" x 2.6" x 5.0') 0.88 cum | ELEC | labour | SWR11037 | 793 | EA | 3172
13 | 1 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ELEC | Labour | SWR10868 | 6852 | TO | 6852
14 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELEC | supply | SMR40009 | 2181 | TO | 2181
15 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELEC | labour | SWR10877 | 851 | TO | 851
16 | 1 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELEC | supply | SMR40010 | 1293 | TO | 1293
17 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELEC | labour | SWR10879 | 482 | TO | 482
18 | 1 | Fabrication & erection of Channels-Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ELEC | labour | SWR10867 | 1470 | TO | 1470
19 | 4 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Box pole 12 Mtr | ELEC | labour | SWR11267 | 3901.37 | EA | 15605.48
20 | 2.65 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 17434.35
21 | 2.31 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ELEC | labour | SWR10862 | 373 | M2 | 861.63
22 | 4 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | ELEC | labour | SWR11089 | 48 | EA | 192
23 | 5.063 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ELEC | labour | SWR10868 | 6852 | TO | 34691.676
24 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELEC | supply | SMR40009 | 2181 | TO | 11042.403
25 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELEC | labour | SWR10877 | 851 | TO | 4308.613
26 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELEC | labour | SMR40010 | 1293 | TO | 6546.459
27 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELEC | labour | SWR10879 | 482 | TO | 2440.366
28 | 5.063 | Fabrication & erection of Channels-Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ELEC | labour | SWR10867 | 1470 | TO | 7442.61
29 | 13 | Erection of AB Switch and aligment complete Erection of 33 KV AB Switch including alignment and earthing | ELEC | labour | SWR10392 | 4500 | EA | 58500
30 | 34 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Note:-The requirement of 2nd coat is to be justified by the concerned Divisional Engineer /Executive Engineer before execution of this work Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | ELEC | labour | SWR10881 | 142 | EA | 4828
31 | 34 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | ELEC | labour | SWR12331 | 146.63 | EA | 4985.42
32 | 6 | Loading of 33 KV CTs/ PTs | ELEC | labour | SWR10200 | 165 | EA | 990
33 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
34 | 6 | Un loading of 33 KV CTs/ PTs | ELEC | labour | SWR10518 | 128 | EA | 768
35 | 2 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33kv single phase PT s | ELEC | labour | SWR10401 | 1079 | SET | 2158
36 | 12 | Loading of 33 KV, 10 KA LAs Station typ | ELEC | labour | SWR10266 | 41 | EA | 492
37 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
38 | 12 | Un loading of 33 KV, 10 KA LAs Station type | ELEC | labour | SWR10584 | 35 | EA | 420
39 | 4 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33 KV LAS station/Line type including earthing | ELEC | labour | SWR10396 | 880 | SET | 3520
40 | 2 | Loading of 33 KV VCBs along with Panel boards | ELEC | labour | SWR10198 | 1024 | EA | 2048
41 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
42 | 2 | Un loading of 33 KV VCBs along with Panel boards | ELEC | labour | SWR10516 | 1044.48 | EA | 2088.96
43 | 12.584 | Excavate-Pit for 33KV VCB | ELEC | labour | SWR23224 | 331 | M3 | 4165.304
44 | 14.52 | Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x 1.8 x 0.75 cum for VCB Plinth | ELEC | labour | SWR20685 | 5160 | M3 | 74923.2
45 | 2 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33 KV VCB with Control Panel | ELEC | labour | SWR10460 | 12500 | EA | 25000
46 | 2 | Loading and unloading of PTR on constructed plinth-Loading of 8MVA PTR | ELEC | labour | SWR10613 | 5805.84 | EA | 11611.68
47 | 2 | Transport of Power transformers (0 to 100 KM) from one place to another place in GHMC Area.(excluding of loading & unloading )-8MVA power transformer | ELEC | labour | SWR10854 | 21945 | EA | 43890
48 | 2 | Loading and unloading of PTR on constructed plinth-Unloading of 8MVA PTR | ELEC | labour | SWR10627 | 5805.84 | EA | 11611.68
49 | 700 | S/o rail poles 90/105lb (250x2N) | ELEC | supply | SMR22718 | 47.27 | KG | 33089
50 | 14 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Rail pole 90 lbs | ELEC | labour | SWR10344 | 3510 | EA | 49140
51 | 2 | Erection of PTR on constructed plinth-Erection of 8 MVA PTR. | ELEC | labour | SWR21321 | 49480.2 | 49480.2 | 98960.4
52 | 0.436 | Extention of 33KV Bay at 132/33KV Sub-station-Zebra condutor | ELEC | supply | SMR24910 | 299369 | 299369 | 130524.884
53 | 30 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing | ELEC | supply | SMR11915 | 2055 | 2055 | 61650
54 | 30 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of I-Bolts | ELEC | supply | SMR22473 | 294 | 294 | 8820
55 | 45 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 "to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating . Sup T clamp LM6 Al alloy of 12 mm, 800 A | ELEC | labour | SMR40011 | 299 | 299 | 13455
56 | 6 | Bus stringing Hoisting of Insulators and hardware, stretching the conductor and stringing of 33 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bussection of 4.5mt) Hoisting post ins&hrd wr 1panther 33kv | ELEC | labour | SWR21240 | 781 | 781 | 4686
57 | 84 | Stringing of bus with panther conductor including jumpering etc., complete to all the equipment in SS fixing to all clamps and equipment.(3 Conductors) | ELEC | labour | SWR10404 | 327.68 | 327.68 | 27525.12
58 | 30 | Bus stringing Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | ELEC | labour | SWR10884 | 224 | 224 | 6720
59 | 75 | Labour for Fixing of all types of clamps | ELEC | labour | SWR10917 | 65 | 65 | 4875
60 | 25 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | ELEC | labour | SWR11039 | 928 | 928 | 23200
61 | 8.68 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ELEC | labour | SWR10868 | 6852 | 6852 | 59475.36
62 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELEC | supply | SMR40009 | 2181 | 2181 | 18931.08
63 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELEC | labour | SWR10877 | 851 | 851 | 7386.68
64 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELEC | supply | SMR40010 | 1293 | 1293 | 11223.24
65 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELEC | labour | SWR10879 | 482 | 482 | 4183.76
66 | 8.68 | Fabrication & erection of Channels-Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ELEC | labour | SWR10867 | 1470 | 1470 | 12759.6
67 | 25 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-R.S. Joists 150 x 150 mm | ELEC | labour | SWR10348 | 1952.61 | 1952.61 | 48815.25
68 | 27.75 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | 6579 | 182567.25
69 | 17.91 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ELEC | labour | SWR10862 | 373 | 373 | 6680.43
70 | 25 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | ELEC | labour | SWR11089 | 48 | 48 | 1200
71 | 4.642 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ELEC | labour | SWR10868 | 6852 | 6852 | 31806.984
72 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELEC | supply | SMR40009 | 2181 | 2181 | 10124.202
73 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELEC | labour | SWR10877 | 851 | 851 | 3950.342
74 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELEC | supply | SMR40010 | 1293 | 1293 | 6002.106
75 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELEC | labour | SWR10879 | 482 | TO | 2237.444
76 | 4.642 | Fabrication & erection of Channels-Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ELEC | labour | SWR10867 | 1470 | TO | 6823.74
77 | 17 | Erection of AB Switch and aligment complete-Erection of 11KV 800A double throw AB Switches | ELEC | labour | SWR21277 | 3500 | EA | 59500
78 | 3 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | ELEC | labour | SWR10393 | 3200 | EA | 9600
79 | 2 | Loading of 11 KV CT - PT Sets | ELEC | labour | SWR10201 | 190 | EA | 380
80 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
81 | 2 | Un loading of 11 KV CT - PT Sets | ELEC | labour | SWR10519 | 101 | EA | 202
82 | 2 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc-Erection of 11 KV three phase PTs | ELEC | labour | SWR10402 | 800 | SET | 1600
83 | 24 | Loading of 11 KV, 10 KA LAs Station type | ELEC | labour | SWR10264 | 32 | EA | 768
84 | 2 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 6599.4
85 | 24 | Un loading of 11 KV, 10 KA LAs Station type | ELEC | labour | SWR10582 | 32 | EA | 768
86 | 2 | Erection of 11 KV LAS station type including earthing | ELEC | labour | SWR10397 | 559 | SET | 1118
87 | 6 | Erection of 11 KV LAS line type including earthing | ELEC | labour | SWR10398 | 505 | SET | 3030
88 | 8 | Loading of 11 KV VCBs along with Panel boards | ELEC | labour | SWR10199 | 1024 | EA | 8192
89 | 4 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 13198.8
90 | 8 | Un Loading of 11 KV VCBs along with Panel boards | ELEC | labour | SWR10517 | 1044.48 | EA | 8355.84
91 | 41.6 | Excavate-Pit for 33KV VCB | ELEC | labour | SWR23224 | 331 | M3 | 13769.6
92 | 48 | Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x 1.8 x 0.75 cum for VCB Plinth | ELEC | labour | SWR20685 | 5160 | M3 | 247680
93 | 8 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc-Erection of 11 KV VCB with Control Panel | ELEC | labour | SWR10461 | 12000 | EA | 96000
94 | 12 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing | ELEC | supply | SMR11915 | 2055 | SET | 24660
95 | 12 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of I-Bolts | ELEC | supply | SMR22473 | 294 | EA | 3528
96 | 45 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 "to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating . Sup T clamp LM6 Al alloy of 12 mm, 800 A | ELEC | supply | SMR40011 | 299 | EA | 13455
97 | 2 | Bus Stringing -Hoisting of Insulators and hardware, stretching the conductor and stringing of 11 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 3.5mt) Hoisting post ins&hrd wr 1panther 11kv | ELEC | labour | SWR21241 | 507 | EA | 1014
98 | 63 | Stringing of bus with panther conductor including jumpering etc., complete to all the equipment in SS fixing to all clamps and equipment.(3 Conductors) | ELEC | labour | SWR10404 | 327.68 | M | 20643.84
99 | 45 | Bus stringing Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | ELEC | labour | SWR10884 | 224 | EA | 10080
100 | 57 | Labour for Fixing of all types of clamps | ELEC | labour | SWR10917 | 65 | EA | 3705
101 | 584 | Laying of earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication 75x 8mm MS Flat / GI Flat. Laying of earth mat,excavation 75x 8mm | ELEC | labour | SWR10920 | 65 | RMT | 37960
102 | 1010 | Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) Earthing for raisers of SS Flat 50x6 mm. | ELEC | labour | SWR10919 | 41 | RMT | 41410
103 | 36 | Supply of earthing pipe with materials -Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | ELEC | supply | SMR11482 | 3486 | EA | 125496
104 | 36 | Providing of Earthing-Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | ELEC | labour | SWR10357 | 1234.2 | EA | 44431.2
105 | 36 | Providing of RCC collar to earth pit-Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINES-Providing of RCC collar | ELEC | labour | SWR10359 | 386 | EA | 13896
106 | 2 | Supply of Copper Flexible jumper with 75 X 8 of length 250 mm at neutral of Power tranformer end and 50 X 6 of length 50mm two Nos at double neutral end duly brasing with flexible jumper of capacity of 5kA/3 sec for power transformer neutral. SupCU Flexi jumper for Power T/F Neutral | ELEC | supply | SMR40033 | 4725 | EA | 9450
107 | 2 | Providing of earthing with various types of earth electrodes-Providing of double earthing for neutral with flexible copper jumpers including arrangement by fixing M.S.Channel 100x50mm. | ELEC | labour | SWR11892 | 1323 | EA | 2646
108 | 80 | Providing of control cable trench as per DATA-XII | ELEC | labour | SWR22093 | 3148 | RMT | 251840
109 | 3074 | Control Cable-Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends . Lay-4C/10C 2.5Sqmm Control Cable | ELEC | labour | SWR11879 | 27 | M | 82998
110 | 270 | Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per specification (including cost of ferrules, lugs and glands) | ELEC | labour | SWR12510 | 27 | EA | 7290
111 | 4 | Marshalling Box Supply of FRP PT Marshalling Box | ELEC | supply | SMR40048 | 4463 | EA | 17852
112 | 4 | Marshalling Box Erection of Marshalling boxes | ELEC | labour | SWR10940 | 374.85 | EA | 1499.4
113 | 1 | Loading of 220 V Batterry with charger | ELEC | labour | SWR11166 | 1612 | SET | 1612
114 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
115 | 1 | Un loading of 220 V Batterry with charger | ELEC | labour | SWR11147 | 1024 | SET | 1024
116 | 1 | Batteries-Erection of 220 V, 200 AH battery in complete shape fit for charging . Conventional lead acid | ELEC | labour | SWR12350 | 7666 | EA | 7666
117 | 1 | Control Panels -Supply of DC Annunciation & relay panel for 10 feeder panel including the cost of LED Indiacation lamps, VAA auxilairy relays, Electronic Hooters complete as per specification. | ELEC | supply | SMR40044 | 42500 | EA | 42500
118 | 1 | Control Panels -Supply of AC Supply panel inluding providing of changeover switch, SFU, metering unit, 32 A three phase MCB, 16 A Single phase MCB complete as per specification. Supply of AC Supply panel complete | ELEC | supply | SMR40045 | 42000 | EA | 42000
119 | 2 | Fixing of AC/DC Panel and giving Connections to the protection equipment and Metering circuits as per the specification and standards. The 3 1/2 core 25 Sqmm power cable required from distribution box to AC/DC panel in the control room is also to be supply | ELEC | labour | SWR20025 | 7871.85 | SET | 15743.7
120 | 8 | Yard lightning-Supply of stepped tubular poles single way made of steel of length 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9 mm, 2.1 mtrs with outer dia 76.1 mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79 kgf as per IS 2713 | ELEC | supply | SMR40051 | 13913 | EA | 111304
121 | 8 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE/CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA /OSRAM /SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty S-90W LED fixture set | ELEC | labour | SMR11594 | 8200 | EA | 65600
122 | 8 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | ELEC | labour | SWR11039 | 928 | EA | 7424
123 | 8 | Erection of tubular poles | ELEC | labour | SWR10955 | 1379 | EA | 11032
124 | 5.27 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 34671.33
125 | 8 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE/CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA /OSRAM /SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty. Fixing of Metal halide lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5 GI pipe complete Fixing of LED/Metal halide complete. | ELEC | labour | SWR10956 | 1268 | EA | 10144
126 | 45 | Supply of HBG metal-Supply & spreading of 20mm machine crushed metal (HBG) including cost of conveneyance of all materials, labour charges etc complete for finished item of work and directed by the engineer incharge | ELEC | labour | SWR10860 | 2113 | M3 | 95085
127 | 2 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M Ex of Hard pit w/o blast 0.75X0.9X1.95M | ELEC | labour | SWR11040 | 990.68 | EA | 1981.36
128 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELEC | Supply | SMR40009 | 2181 | TO | 1635.75
129 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELEC | labour | SWR10877 | 851 | TO | 638.25
130 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELEC | Supply | SMR40010 | 1293 | TO | 969.75
131 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELEC | labour | SWR10879 | 482 | TO | 361.5
132 | 1 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Box pole 12 Mtr | ELEC | labour | SWR11267 | 3901.37 | EA | 3901.37
133 | 2.22 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 14605.38
134 | 1.16 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ELEC | labour | SWR10862 | 373 | M2 | 432.68
135 | 2 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | ELEC | labour | SWR11089 | 48 | EA | 96
136 | 1 | Construction of DTR Plinth-RCC Column type DTR Plinth of size 1'X1'X10',topslab 4'x4'x6" & beam size 4'X8'X8" upto 160KVA | ELEC | labour | SWR21843 | 25967.57 | EA | 25967.57
137 | 1 | Loading of 50,63, 75 & 100 KVA DTR | ELEC | labour | SWR10195 | 350 | EA | 350
138 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
139 | 1 | Un loading of 50,63, 75 & 100 KVA DTR | ELEC | labour | SWR10513 | 280 | EA | 280
140 | 1 | Erection of DTR's including loading and Unloading DTR on the Structure/Plinth etc-Erection of 3 Phase DTRs 63,75 & 100 KVA | ELEC | labour | SWR20905 | 1650 | EA | 1650
141 | 1 | Erection of AB Switch and aligment complete Erection of 11KV 200A TT type AB Switch including fixing of cross angles and alignment complete | ELEC | labour | SWR20102 | 1813.49 | EA | 1813.49
142 | 1 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erect. of 11kv HG Fuseset incl earthing | ELEC | labour | SWR10395 | 740.52 | SET | 740.52
143 | 40 | Excavation & laying of UG Cable in Single Run Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.-In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road-11KV 3x185 Sqmm Cable | ELEC | labour | SWR11920 | 465.46 | M | 18618.4
144 | 20 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-11 KV 3x185 Sqmm Cable | ELEC | labour | SWR11956 | 126.23 | M | 2524.6
145 | 2 | Making of Outdoor/Indoor End Termination Making 11 KV 3x185 Sqmm Cable Out Door/Indoor end termination | ELEC | labour | SWR10390 | 2370.63 | EA | 4741.26
146 | 1 | Erection of LT distribution box including laying of LT cable from distribution box to LT OH line and DTR to distribution box including earthing of distribution box and crimping of lugs connecting of jumpers etc | ELEC | labour | SWR10674 | 1594.67 | EA | 1594.67
147 | 85 | LAYING OF 33KV, 11KV UG CABLE Excavation & laying of UG Cable in Single Run Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road-LT 3 1/2 x 185 Sqmm Cable | ELEC | labour | SWR11923 | 377.63 | M | 32098.55
148 | 15 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-LT 3 1/2 x 185 Sqmm Cable | ELEC | labour | SWR11959 | 85.43 | M | 1281.45
149 | 2 | UG Cables Joints :-Making of Outdoor/Indoor End Termination -Supply & fixing of Oout Door/Indoor end termination LT 3 1/2 x 185 Sqmm Cable | ELEC | labour | SWR10765 | 968.9 | EA | 1937.8
150 | 1 | Supply and fixing of Substation board of size 3'x2.5' indicating the layout of switchyard Sup &fix of board ind Switchyard layout | ELEC | labour | SWR20032 | 1654 | EA | 1654
151 | 1 | Supply and fixing of safety instructions/Substation operation instruction board. Sup& fix safety inst/SS Op. inst board | ELEC | labour | SWR22090 | 2205 | EA | 2205
152 | 750 | Control Panels Supplying & fabrication erection of 6mm Checkerd plates as per the field conditions Supply,fabricati of 6mm Checkerd plates | ELEC | Labour | SWR10873 | 83 | KG | 62250
153 | 1 | T & P Supply of Wall clock standard make | ELEC | Supply | SMR40059 | 578 | EA | 578
154 | 1 | S-10ft Aluminium Ladder | ELEC | Supply | SMR12378 | 1654 | EA | 1654
155 | 1 | Sup Alluminium Ladder for indoor works | ELEC | Supply | SMR40062 | 4410 | EA | 4410
156 | 30 | T & P Painting of Name Plates for any equipmen | ELEC | labour | SWR10963 | 122 | EA | 3660
157 | 1 | T & P Supply of Taparia Tool kit of Size 20”x10”x15” with tier arrangements Tool box with locking arrangement & key containing (1) Double Ended fix Spanner sets, (Ribbed) 6 x 7, 8 x 9, 10 x 11, 12 x 13, 14 x 15, 16 x 17, 18 x19, 20 x 22, 21 x 23, 24 x 27, 25 x28, 30 x 32, (2) Double Ended Ring Spanners sets, 6 x 7 , 8 x 9, 10 x 11, 12 x 13, 14 x 15. 16 x 17 , 18 x 19, 20 x 22 , 21 x 23, 24 x 27, 25 x28, 30 x 32 mm, (3) Adjustable Spanner 305 mm length least maximum opening 35mm chrome, (4) Pipe Wrench Length 350 mm 14”, (5) Soft faced Hammer with suitable handle 2 lb, (6) Hacksaw frame with metal handle heavy duty for 12" hacksaw blade with High Speed blade, (7) Insulated Screw drivers Transparent Green Handle Set Length 6”, 8” & 12”, (8) Star Screw Driver Transparent Green Handle Length 6”, (9) Insulated Wire Cutter, (10) Insulated Cutting Plier Length 8” with cable stripper insulated with thick C. A. sleeve confirming to IS: 4378 - 1990, (11) Long Nose Plier insulated with thick C.A. sleeve generally confirming to IS:3552-1989, (12) Tester type screw driver (special with neon bulb) generally confirm to IS: 5579- 1985 Grade:II handle yellow/ green colour overall length 130 mm, (13) Insulated Crimping Plier of all Taparia make. SupTaparia Tool kit complete as per Spec | ELEC | Supply | SMR40063 | 4925 | SET | 4925
158 | 1 | T & P Sup Rechargeable LED torch light of Standard make | ELEC | Supply | SMR40064 | 1733 | EA | 1733
159 | 1 | T & P-Steel almarah(61/2 X 3ft) Godrej | ELEC | Supply | SMR40061 | 9818 | EA | 9818
160 | 1 | T & P-Table (3x6ft) Godrej | ELEC | Supply | SMR40057 | 6050 | EA | 6050
161 | 4 | T & P-S type chairs (Godrej) | ELEC | Supply | SMR40058 | 924 | EA | 3696
162 | 1 | T & P Sup Angle racks(18x36.6inches) Godrej | ELEC | Supply | SMR40060 | 1733 | EA | 1733
163 | 1 | T & P Supply of Hack saw (12 inches) | ELEC | Supply | SMR40065 | 289 | EA | 289
164 | 4 | Sup Earth Rods (8ft) Screw & clamp type | ELEC | Supply | SMR40066 | 578 | EA | 2312
165 | 2 | Supply of Hand Gloves | ELEC | Supply | SMR40067 | 289 | SET | 578
166 | 12 | SupRubber mats( 6'x3')size fo indoorSS | ELEC | Supply | SMR40068 | 1386 | EA | 16632
167 | 1 | Biometric Time attendence System & Telecom Sup Stand basic cell phone with charger | ELEC | Supply | SMR40069 | 1386 | EA | 1386
168 | 14 | Supply of Danger boards with clamps | ELEC | Supply | SMR40070 | 116 | EA | 1624
169 | 2 | Supply of Materials -Fire bucket stand with 3 buckets (8 -10 ltr capacity) | ELEC | Supply | SMR40088 | 1386 | SET | 2772
170 | 2 | Room fire extinguisher (2 ltrs capacity) for control room | ELEC | Supply | SMR40089 | 4620 | EA | 9240
171 | 4 | Sup TrollyMounted Co2 (6.5Kgs) Cylinders(IS-2878) | ELEC | Supply | SMR40087 | 9240 | EA | 36960
172 | 6 | Supply of Safety Helmet of standard make | ELEC | Supply | SMR40071 | 231 | EA | 1386
173 | 8 | Supply of LC Boards | ELEC | Supply | SMR40072 | 116 | EA | 928
174 | 4 | Supply of Gum Boots(Pairs) | ELEC | Supply | SMR40073 | 693 | EA | 2772
175 | 1 | Supply of 5000v megger | ELEC | Supply | SMR40074 | 13860 | EA | 13860
176 | 1 | Supply of Earth megger (1000v) | ELEC | Supply | SMR40075 | 8085 | EA | 8085
177 | 1 | Supply of Digital clamp meter. | ELEC | Supply | SMR40076 | 2888 | EA | 2888
178 | 1 | Name board of the 33/11kV Sub-Station(As per Standard Specification) Sup 33/11kv S.S Permanent name board | ELEC | Supply | SMR40086 | 10238 | EA | 10238
179 | 800 | Supply of Hot dip galvanized/zinc coated bolts & nuts including spring washers, pack washers and flat washers etc. | ELEC | Supply | SMR12488 | 90 | KG | 72000
180 | 2 | Fabrication of poles-Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | ELEC | labour | SWR10642 | 512.55 | EA | 1025.1
181 | 1 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-RS Joists 150x75/175 x 85 mm | ELEC | labour | SWR10346 | 1934 | EA | 1934
182 | 5760 | S-Supply of RS Joist Grider Pole (150x150mm) | ELEC | Supply | SMR12302 | 59.25 | KG | 341280
183 | 1000 | S-Supply of RS Joist Pole (175x85mm) | ELEC | Supply | SMR12303 | 60.75 | KG | 60750
184 | 5063 | S- Supply of MS Channel 100x50mm | ELEC | Supply | SMR22745 | 57.45 | KGS | 290869.35
185 | 13 | S-Supply of 33KV 800A DB Break AB Switch | ELEC | Supply | SMR12315 | 40658.78 | EA | 528564.14
186 | 8680 | S-Supply of RS Joist Grider Pole (150x150mm) | ELEC | Supply | SMR12302 | 59.25 | KG | 514290
187 | 4642 | S- Supply of MS Channel 100x50mm | ELEC | Supply | SMR22745 | 57.45 | KGS | 266682.9
188 | 17 | S-Supply of 11KV 800A DB Break AB Switch | ELEC | Supply | SMR12316 | 30847.46 | EA | 524406.82
189 | 3 | S-Supply of 11KV 400A DB Break AB Switch | ELEC | Supply | SMR12317 | 18150 | EA | 54450
190 | 3045 | S-Supply of MS Flat 75x8mm | ELEC | Supply | SMR12321 | 56.42 | KG | 171798.9
191 | 2666 | S-Supply of MS Flat 50x6mm | ELEC | Supply | SMR12322 | 56.5 | KG | 150629
192 | 750 | S-Supply of RS Joist Pole (175x85mm) | ELEC | Supply | SMR12303 | 60.75 | KG | 45562.5
193 | 1 | S-Supply of 11KV 200A Tilting Type AB Switch | ELEC | Supply | SMR12318 | 8991 | EA | 8991
194 | 1 | S-Supply of 11KV HG FuseSet for StationTransformer | ELEC | Supply | SMR12324 | 1974 | EA | 1974
195 | 1 | S-Supply of LT Distribution Box (SMC) | ELEC | Supply | SMR25200 | 7797 | EA | 7797
196 | 2 | S-Supply of 11KV 3x185 Heat Shble O/d End Term Kit | ELEC | Supply | SMR25201 | 1182.97 | EA | 2365.94
197 | 40 | S-Supply of LT XLPE Cable 1C 150 sqmm | ELEC | Supply | SMR25203 | 114.83 | M | 4593.2
198 | 100 | Supply of LT XLPE Cable 31/2C185sqmm. | ELEC |  | SMR25204 | 547 | M | 54700
199 | 4 | Loading of LT AB Cable 3X16+25 Sqmm | ELEC | labour | SWR11702 | 200 | DR | 800
200 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
201 | 4 | Un loading of LT AB Cable 3X16+25 Sqmm | ELEC | labour | SWR11713 | 204 | DR | 816
202 | 4 | survey line&cabl inc peg mark&tree clear | ELEC | labour | SWR22092 | 765 | KM | 3060
203 | 4 | Paving out and stringing of conductor by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location-100 Sqmm Single Circuit (3 Conductors) | ELEC | labour | SWR10366 | 13856.7 | KM | 55426.8
204 | 80 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M Ex of Hard pit w/o blast 0.75X0.9X1.95M | ELEC | labour | SWR11040 | 990.68 | EA | 79254.4
205 | 80 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Errection of 11 M long PSCC pole | ELEC | labour | SWR10978 | 4336.85 | EA | 346948
206 | 28.296 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 186159.384
207 | 80 | Painting of poles-Numbering of poles incl. cost of paint | ELEC | labour | SWR10378 | 32 | EA | 2560
208 | 30 | Excavation of pits in all soils except hard rock requiring blasting-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") 1.05 cum | ELEC | labour | SWR10107 | 700 | EA | 21000
209 | 30 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Erec of 9.1 Mts PSCC poles for stuts | ELEC | labour | SWR11083 | 2400 | EA | 72000
210 | 15.75 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 103619.25
211 | 16 | Formation of Cut points - Formation of Cut point for 11 KV Single Circuit line excluding pole erection and stays Formatn of Horiz Cut point for 11KV line | ELEC | labour | SWR10653 | 1435.81 | EA | 22972.96
212 | 200 | Supply of earthing pipe with materials S-GI Bolts & Nuts,Washers etc., | ELEC | supply | SMR11488 | 117.5 | KG | 23500
213 | 4 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 50 Km and upto 80 Km with Lorry for each trip | ELEC | labour | SWR11864 | 5290.74 | EA | 21162.96
214 | 4 | LOADING of Conductor drums | ELEC | labour | SWR10191 | 202 | EA | 808
215 | 4 | UNLOADING of Conductor drums | ELEC | labour | SWR10509 | 100 | EA | 400
216 | 25 | Loading of 33 KV Pin insulators | ELEC | labour | SWR10211 | 3 | CRT | 75
217 | 25 | Un loading of 33 KV Pin insulators | ELEC | labour | SWR10529 | 3 | CRT | 75
218 | 5 | Loading of 33 KV Metal parts | ELEC | labour | SWR10618 | 65 | BAG | 325
219 | 5 | Un loading of 33 KV Metal parts | ELEC | labour | SWR10632 | 65 | BAG | 325
220 | 210 | Excavation & laying of UG Cable (Double Run) Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, Along the CC / BT multi layer road requiring compressor-33 KV 3x400 Sqmm Cable | ELEC | labour | SWR11980 | 1388.84 | M | 291656.4
221 | 210 | Laying of 2nd cable in excavated trench | ELEC | labour | SWR10988 | 204.1 | M | 42861
222 | 40 | Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-33 KV 3x400 Sqmm Cable | ELEC | labour | SWR12004 | 323.85 | M | 12954
223 | 12 | Cost of Pipes and slabs-Supply of 6" B class GI pipe | ELEC | supply | SMR40081 | 1044 | M | 12528
224 | 30 | Cost of Pipes and slabs-Supply of 250 mm Hume pipe of class NP3 with compresive strength of 35N/mm2 for 28 days curing,barewall thickness of 30mm,1.25kG linear/meter and withstanding capability of 22.50KN/linear meter as per IS 458-1993. | ELEC | supply | SMR40077 | 363 | M | 10890
225 | 6 | Cost of Pipes and slabs-Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters , CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | ELEC | supply | SMR40085 | 484 | EA | 2904
226 | 2 | Load-11/33KV XLPE UG Cable for all sizes | ELEC | labour | SWR11230 | 1024 | DR | 2048
227 | 2 | Unload-11/33KV XLPE UG Cable for all sizes | ELEC | labour | SWR11231 | 1024 | DR | 2048
228 | 8 | Making of Outdoor/Indoor End Making 33 KV 3x400 Sqmm Cable Out Door/Indoor end termination TerminationOD/Idoor end termination 33kv 3x400 xlpe | ELEC | labour | SWR10387 | 2764.76 | EA | 22118.08
229 | 2 | UG Cables Joints 33 KV 3x400 Sqmm Cable Straight through joint 33kv 3x400 xlpe | ELEC | labour | SWR10382 | 5700.78 | EA | 11401.56
230 | 1.35 | Fabrication & erection of Channels -Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to theRS-Joist poles excluding cost of Mild Steel and transportcharges to substation site, including erection. Fabrication of struc.with welding. | ELEC | labour | SWR10869 | 3426 | TO | 4625.1
231 | 50 | Supply of earthing pipe with materials-Supply of GI wire No 8 | ELEC | supply | SMR11486 | 105 | KG | 5250
232 | 2 | Supply of earthing pipe with materials-Supply of CI eath pipe with 80mm dia,2.0 M Length | ELEC | labour | SMR11483 | 2789 | EA | 5578
233 | 2 | Providing of Earthing-Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | ELEC | labour | SWR10357 | 1234.2 | EA | 2468.4
234 | 2 | Providing of RCC collar to earth pit-Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINES-Providing of RCC collar | ELEC | labour | SWR10359 | 386 | EA | 772
235 | 40 | Supply of earthing pipe with materials-Supply of GI Flat 25X3 mm | ELEC | supply | SMR11485 | 105 | KG | 4200
236 | 20 | Supply of Danger boards with clamps | ELEC | supply | SMR40070 | 116 | EA | 2320
237 | 6 | S&E-Smart RFID marker | ELEC | labour | SWR25089 | 2745 | EA | 16470
238 | 80 | Supply of PSCC Pole 11Mtr 365KG | ELEC | supply | SMR25236 | 5399 | EA | 431920
239 | 30 | Supply of PSCC Pole 9.1Mtr 280KG | ELEC | supply | SMR25233 | 3109.41 | EA | 93282.3
240 | 800 | Supply of Materials -- Supply of MS Channel 100X50mm | ELEC | supply | SMR22745 | 57.45 | KGS | 45960
241 | 400 | Supply of MS Angle 65x65x6 | ELEC | supply | SMR25207 | 57.25 | KG | 22900
242 | 150 | Supply of Materials -- Supply of MS Flat 75x8 mm | ELEC | supply | SMR12321 | 56.42 | KG | 8463
243 | 8 | UG Cables Joints : Making of Outdoor/Indoor End Termination -- Supply 33KV 3x400Sqmm Outdoor | ELEC | supply | SMR22222 | 4554 | EA | 36432
244 | 2 | UG Cables Joints : Making of Straight through joints -- Supply of 33KV 3x400SQmm Straight Through Joint Kit | ELEC | supply | SMR22223 | 24151 | EA | 48302
245 | 64 | Supply of 33KV V-Cross Arm without Clamps | ELEC | supply | SMR25229 | 1678 | EA | 107392
246 | 9 | survey line&cabl inc peg mark&tree clear | ELEC | labour | SWR22092 | 765 | KM | 6885
247 | 9 | Paving out and stringing of conductor by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location-55 Sqmm Single Circuit (3 Conductors) | ELEC | labour | SWR10365 | 9454.81 | KM | 85093.29
248 | 175 | Excavation of pits in all soils except hard rock requiring blasting-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") 1.05 cum | ELEC | labour | SWR10107 | 700 | EA | 122500
249 | 50 | Excavation of pits in hard rock requiring blasting. (other than SS)-9.1Mtrs PSCC Pole 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | ELEC | labour | SWR10112 | 1770 | EA | 88500
250 | 213 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-9.1 M long PSCC pole | ELEC | labour | SWR10343 | 2400 | EA | 511200
251 | 37.8 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 248686.2
252 | 225 | Painting of poles-Numbering of poles incl. cost of paint | ELEC | labour | SWR10378 | 32 | EA | 7200
253 | 80 | Excavation of pits in all soils except hard rock requiring blasting-Stud Poles 0.6 M x 0.9 M x 1.5 M | ELEC | labour | SWR10106 | 645 | EA | 51600
254 | 80 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-8.0 m long PSCC poles for Strut | ELEC | labour | SWR21590 | 1500 | EA | 120000
255 | 32 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 210528
256 | 40 | Formation of Cut points - Formation of Cut point for 11 KV Single Circuit line excluding pole erection and stays Formatn of Horiz Cut point for 11KV line | ELEC | labour | SWR10653 | 1435.81 | EA | 57432.4
257 | 350 | Supply of earthing pipe with materials S-GI Bolts & Nuts,Washers etc., | ELEC | supply | SMR11488 | 117.5 | KG | 41125
258 | 4 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 50 Km and upto 80 Km with Lorry for each trip | ELEC | labour | SWR11864 | 5290.74 | EA | 21162.96
259 | 4 | LOADING of Conductor drums | ELEC | labour | SWR10191 | 202 | EA | 808
260 | 4 | UNLOADING of Conductor drums | ELEC | labour | SWR10509 | 100 | EA | 400
261 | 6 | Supply of earthing pipe with materials-Supply of CI eath pipe with 50mm dia,2.0 M Length | ELEC | supply | SMR11484 | 2441 | EA | 14646
262 | 6 | Providing of Earthing-Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | ELEC | labour | SWR10357 | 1234.2 | EA | 7405.2
263 | 6 | Providing of RCC collar to earth pit-Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINES-Providing of RCC collar | ELEC | labour | SWR10359 | 386 | EA | 2316
264 | 6 | Assembly and erection of Structure as per specification which includes fixing of top channels and cross bracings, transport of all materials from road side to the location, earthing, back filling with earth ramming etc excluding pit excavation and concreting.-11KV DP Structure with 9.1 Mtrs PSCC Poles | ELEC | labour | SWR21130 | 3363.96 | SET | 20183.76
265 | 6 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | ELEC | labour | SWR10393 | 3200 | EA | 19200
266 | 6 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | ELEC | labour | SWR10881 | 142 | EA | 852
267 | 50 | Supply of earthing pipe with materials-Supply of GI wire No 8 | ELEC | supply | SMR11486 | 105 | KG | 5250
268 | 675 | Loading of 11KV Polymer Pin Insulators with GI pins | ELEC | labour | SWR11248 | 1 | EA | 675
269 | 675 | Un loading of 11KV Polymer Pin Insulators with GI pins | ELEC | labour | SWR11249 | 1 | EA | 675
270 | 240 | Loading of 11KV Polymer Pin Insulators with GI pins | ELEC | labour | SWR11248 | 1 | EA | 240
271 | 240 | Un loading of 11KV Polymer Pin Insulators with GI pins | ELEC | labour | SWR11249 | 1 | EA | 240
272 | 6 | Loading of 11 KV Metal parts | ELEC | labour | SWR12402 | 48 | BAG | 288
273 | 6 | Un loading of 11 KV Metal parts | ELEC | labour | SWR12421 | 48 | BAG | 288
274 | 960 | Laying of 2nd cable in excavated trench | ELEC | labour | SWR10988 | 204.1 | M | 195936
275 | 72 | Cost of Pipes and slabs-Supply of 6" B class GI pipe | ELEC | supply | SMR40081 | 1044 | M | 75168
276 | 200 | Cost of Pipes and slabs-Supply of 250 mm Hume pipe of class NP3 with compresive strength of 35N/mm2 for 28 days curing,barewall thickness of 30mm,1.25kG linear/meter and withstanding capability of 22.50KN/linear meter as per IS 458-1993. | ELEC | supply | SMR40077 | 363 | M | 72600
277 | 6 | Cost of Pipes and slabs-Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters , CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | ELEC | supply | SMR40085 | 484 | EA | 2904
278 | 5 | Load-11/33KV XLPE UG Cable for all sizes | ELEC | labour | SWR11230 | 1024 | DR | 5120
279 | 5 | Unload-11/33KV XLPE UG Cable for all sizes | ELEC | labour | SWR11231 | 1024 | DR | 5120
280 | 1.1 | Fabrication & erection of Channels -Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to theRS-Joist poles excluding cost of Mild Steel and transportcharges to substation site, including erection. Fabrication of struc.with welding. | ELEC | labour | SWR10869 | 3426 | TO | 3768.6
281 | 50 | Supply of Danger boards with clamps | ELEC | supply | SMR40070 | 116 | EA | 5800
282 | 6 | S&E-Smart RFID marker | ELEC | labour | SWR25089 | 2745 | EA | 16470
283 | 960 | Excavation & laying of UG Cable (Double Run)-Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts,-In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil/CC-11 KV 3x300 Sqmm Cable | ELEC | labour | SWR11973 | 631.06 | M | 605817.6
284 | 240 | Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-11 KV 3x300 Sqmm Cable | ELEC | labour | SWR12005 | 275.4 | M | 66096
285 | 6 | UG Cables Joints Making of Straight through joints-11 KV 3x300 Sqmm Cable | ELEC | labour. | SWR10386 | 3725.45 | EA | 22352.7
286 | 24 | Making of Outdoor/Indoor End Termination-Making 11 KV 3x300 Sqmm Cable Out Door/Indoor end termination | ELEC | labour. | SWR10391 | 2370.63 | EA | 56895.12
287 | 225 | Supply of PSCC Pole 9.1Mtr 280KG | ELEC | supply | SMR25233 | 3109.41 | EA | 699617.25
288 | 80 | Supply of PSCC Pole 8Mtr 140KG | ELEC | supply | SMR25232 | 1580 | EA | 126400
289 | 185 | supply of V X-Arm with MS Angle 65x65x6 | ELEC | supply | SMR25218 | 743 | EA | 137455
290 | 185 | S-Supply of 11KV Top Cleat for 9.1M(Vertical) | ELEC | Supply | SMR25226 | 256 | EA | 47360
291 | 80 | Supply of 11KV Horizontal Cross Arm | ELEC | supply | SMR25223 | 528 | EA | 42240
292 | 6 | Supply of Materials -- Supply of 11 kV 400 A Double break AB switch | ELEC | supply | SMR12317 | 18150 | EA | 108900
293 | 200 | Supply of Materials -- Supply of MS Flat 50x6 mm | ELEC | supply | SMR12322 | 56.5 | KG | 11300
294 | 400 | Supply of MS Angle 50x50x6 | ELEC | supply | SMR25206 | 58.15 | KG | 23260
295 | 500 | Supply of MS Channel 75x40 mm | ELEC | supply | SMR25205 | 58.45 | KG | 29225
296 | 24 | Supply of 11KV 3x300 Heat Shble O/d End Term Kit | ELEC | supply | SMR25208 | 1372.88 | EA | 32949.12
297 | 6 | Supply of 11KV 3x300 Heat Shble stright through joint Kit | ELEC | supply | SMR25210 | 4110.17 | EA | 24661.02
Sub Total: | [7 empty] | 12832983.929
Civil labour - WBS. No. S-1789-13-07-01-01-001
Sl.No. | Estimate Quantity (only Figures) | Item Detailed Specification Description | Work Type eg. Earth Work, Electrical works. etc (upto 200 Characters) | Item Short Description (upto 100 Characters) | APSS / Morth Cl. Number (upto 200 Characters) | Rate (INR) (Upto 2 Decimals ) | UOM (upto 50 Characters) | Amount
1 | 32 | Leveliing the site by cutting and levelling with the help of JCB including cost,conveyance of all materials,hire chareges etc complete for finished item of work as directed by Engineer-in-charge. | Civil | Labour | SWR34179 | 2165 | Hrs | 69280
2 | 135.61 | Earth work excavation in all type of ordinary soils red earth, Hard gravelly soils, earth mixed with sand and sandy soils etc., in all conditions such as slushy and dry with initial leads and lifts for foundations. | Civil | Labour | SWR33015 | 486 | m3 | 65906.46
3 | 32.45 | Plain Cement concrete PCC (1:4:8) using 40mm HBG metal for foundations and leveling course, including cost and conveyance of all materials, labour all leads and lifts, consolidation and all operations, formwork as required, curing, etc. complete for finished item w | Civil | Labour | SWR33028 | 4685 | m3 | 152028.25
4 | 117.88 | Coursed Rubble stone (CRS) masonry 2nd sort with hard granite stones in cement mortar (1:6) for basement, including cost and conveyance of all materials, labour charges, curing, all leads and lifts, etc, complete for finished item of work. | Civil | Labour | SWR33041 | 4830 | m3 | 569360.4
5 |  | 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge
6 | 3.564 | RCC M20 Grade footing 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33098 | 9437 | m3 | 33633.468
7 | 2.28 | RCC M20 Grade Coloumn . 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33100 | 13186 | m3 | 30064.08
8 | 2.25 | RCC M20 Grade Plinth beams 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33099 | 12307 | m3 | 27690.75
9 | 3.17 | D) RCC M20 Grade Roof Beams landing beam 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33121 | 12224 | m3 | 38750.08
10 | 0.58 | e)RCC M20 Grade Lintels 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33107 | 13015 | m3 | 7548.7
11 | 2.7 | f) RCC M20 Grade Sunshades 600mm wide and 75mm thick'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33114 | 1372 | m2 | 3704.4
12 | 15.224 | g) RCC M20 Grade Roof Slab for Control Room 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33128 | 10811 | m3 | 164586.664
13 | 3 | Reinforcement steelSupplying, Cutting, bending, binding, placing in position and tying reinforcement steel in all heights including cost and conveyance of steel and binding wire etc,. With all leads and lifts, labour charges, etc., complete for finished item of work. | Civil | Labour | SWR33144 | 70687 | Ton | 212061
14 | 38.36 | Brick masonry in cement mortar CM (1:6) for superstructure using well burnt country made second class bricks of approved quality including cost and conveyance of all materials curing, scaffolding with all leads and lifts in all heights etc., complete for fin | Civil | Labour | SWR33068 | 8246 | m3 | 316316.56
15 | 2.7 | Plain Cement concrete PCC (1:2:4) using 20mm size well graded HBG metal for foundations, including cost, conveyance of all materials,labour all leads and lifts,consolidation and all operations, formwork as required, curing,etc. complete for finished item of work | Civil | Labour | SWR33030 | 6054 | m3 | 16345.8
16 | 606.06 | Plastering with CM 2 coats, 20 mm thick, base coat in CM (1:6), 16 mm thick and top coat in CM (1:4), 4mm thick with Dubara sponze finishing including cost of all materials, seigniorage charges, excluding conveyance charges of materials and including all operational, incidental and labour charges for mixing mortar, laying rendering smooth and thread lining, curing, rounding off junctions of wall and slab etc., complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33163 | 560 | m2 | 339393.6
17 | 349.515 | Painting with two coats of Plastic Emulsn paint over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33356 | 210 | m2 | 73398.15
18 | 200.85 | Painting with two coats of Surya Cem paint over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33329 | 85 | m2 | 17072.25
19 | 3 | Supply and Fixng of MS Name Board including cost & conveyance of all materials,labour charges etc complete for finished item of work. | Civil | Labour | SWR33421 | 4326 | m2 | 12978
20 | 1 | Geophysical Investgation charges for water point by Geologist | Civil | Labour | SWR33608 | 5000 | EA | 5000
21 |  | Drilling of 165mm bore well with machine rig including deployment and hire charges of rig and other machinery and equipment labour charges , measuring the yeild of borewell including cost and conveyance etc complete
22 | 90 | Drill-165mm Bore Well 0 to 90 | Civil | Labour | SWR33609 | 336 | M | 30240
23 | 30 | Drill-165mm Bore Well 90M to 120M | Civil | Labour | SWR34830 | 369 | M | 11070
24 | 30 | Drill-165mm Bore Well 120M to 150M | Civil | Labour | SWR34831 | 394 | M | 11820
25 | 30 | Drill-165mm Bore Well 150M to 180M | Civil | Labour | SWR34832 | 492 | M | 14760
26 | 30 | Drill-165mm Bore Well 180M to 210M | Civil | Labour | SWR34833 | 623 | M | 18690
27 | 30 | Drill-165mm Bore Well 210M to 240M | Civil | Labour | SWR34834 | 754 | M | 22620
28 | 30 | Drill-165mm Bore Well 240M to 270M | Civil | Labour | SWR34835 | 918 | M | 27540
29 | 90 | Drill-165mm Bore Well 270M and above | Civil | Labour | SWR34836 | 1082 | M | 97380
30 | 40 | Supply and fixing of 160mm dia PVC casing of A class 6Kg point pressure including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR33611 | 883 | M | 35320
31 | 1 | Supply and erecting, ISI mark submersible 5.0 HP, Single Phase 30 stages pumpset suitable for 106/156mm dia borewell including cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33640 | 48007 | EA | 48007
32 | 328 | Supply and fixing of HDPE pipe 40mm dia of 16Kg/cm2 including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR34410 | 180 | M | 59040
33 | 1 | Supply and erecting D.O.L Starter 415V , Single phase,50Hz with SS enclouserincluding cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33645 | 7854 | EA | 7854
34 | 360 | Supply of 3 Core 2.5 Sqmm Flat Copper cable of ISI for Submersible Motors of makes Finolex / Polycab / Gold Medal / Million / Payal / Sun Light / Power Flex / Fortune Art | Civil | Labour | SWR33641 | 192 | m | 69120
35 | 71 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-28.60mm OD Pipe - SDR 11 | Civil | Labour | SWR34363 | 410 | m | 29110
36 | 35 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type - 25mm NB Size | Civil | Labour | SWR34346 | 466 | EA | 16310
37 | 839.38 | Supplying and filling the substation site with borrowed gravel, watering, ramming, thoroughly complying with the standard specification. | Civil | Labour | SWR33052 | 309 | m3 | 259368.42
38 | 16.56 | Providing Design R.C.M. drop wall of 25mm thickness with cm 1:3 and 6mm dia MS bars at 150mm both ways and chicken mesh in two coats 20mm thick each plastering including cost and conveyance of all materials with leads and lifts, scaffolding and curing, labo | Civil | Labour | SWR33203 | 3042 | m2 | 50375.52
39 | 12.24 | Supply and fixing of Ms ornamental safety grill of approved design including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33310 | 2990 | m2 | 36597.6
40 | 5.91 | Supply and fixing of doors with the MT Wood frames of the door shall be made well seasoned mt wood of cross section 100x75mm. The shutter shall be made isi mark flushed door with decolam sheets pasted on both sides with PVC beading 40mm width all round.Frame shall be painted with two coats of synthetic enamel paint of approved color over one coat of primer over luppum with spary with 3 no 150mm brass hinges 1 no brass door stoper, 1 no 250mm brass aldrops. 2 no 300 mm aluminium tower bolts, 2 no 150mm brass fancy door handlers, 1 no keyless lockset with cp handel. The quoted rate shall include cost and conveyance of the meterials, fixig, labour carges, tools, handles,locking arrangementts and other fixtures & fittings for finished item work as directed by the Engineer - in- charge. | Civil | Labour | SWR33264 | 7314 | m2 | 43225.74
41 | 128.25 | Raised pointing to the exposed surfaces of CRS masonry in cm 1:3 prop. including cost and conveyance of all materials, labour charges, all leads and lifts curing etc, complete for finished item of work. | Civil | Labour | SWR33184 | 124 | m2 | 15903
42 | 8.64 | Supplying and fixing Aluminium sliding windows with grill and fixed glass panels using anodised aluminium extruded sections of mat finish for frames and mullions made from approved aluminium sections 62x32x1.2mm at 0.73kg/Rm providing 5mm plain glass fix | Civil | Labour | SWR33277 | 3623 | m2 | 31302.72
43 | 16.56 | Supply and laying of Ceramic floor over of CM 1:3 20 mm thick including required materials and labour charges etc complete for item of work | Civil | Labour | SWR33224 | 914 | m2 | 15135.84
44 | 121.92 | Flooring with double machine polished and hand cut Tandur blue stone 20mm thick of approved colour, quality and of minimum of 300x300mm size over a bed of cement mortar 1:3 20mm thick including cost of all materials, with all leads and lifts jointing and | Civil | Labour | SWR33219 | 785 | m2 | 95707.2
45 | 6.74 | Supply and fixing of 4" high skirting of shabad stone to the walls including cost and conveyance of all materials, labour etc for finished item of work. | Civil | Labour | SWR33236 | 875 | m2 | 5897.5
46 | 243.69 | Painting with two coats of OBD over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials labour charges etc., complete for finished item of work. | Civil | Labour | SWR33333 | 146 | m2 | 35578.74
47 | 101.17 | Providing impervious coat over RCC roof slab to requried slopes with 20mm thick in CM 1:3 mixed with approved brand of water proffing compound inclding cost and conveyance of all materials, labour charges, curing, rounding off junctions of wall and slab, all leads and lifts, etc . complete for finished item of work as directed by the Engineer - in - charge. | Civil | Labour | SWR33156 | 582 | m2 | 58880.94
48 | 60 | Supply & fixing of 25mm dia 2mm thick suSupply & fixing of 25mm dia 2mm thick surface P.V.C. pipe (ISI MARK) Concealed in wall with all required accessories including masonary work and labour charges etc.complete. | Civil | Labour | SWR33441 | 108 | m | 6480
49 | 1 | Supply & fixing TPN Distribution board w Supply & fixing TPN Distribution board with IP-42 protection (Metal Door)suitable for 3 phase ELCB/RCCB/FP Isolator as incomer and 10kA SP MCBs as out going including internal connection and labour charges for surface / flush mounting etc Complete. | Civil | Labour | SWR33526 | 11353 | EA | 11353
50 | 10 | Supply & fixing of 6A 3 pin wall plug socket with 6A switch control on a common switch board with earth continuity including wire leads,earth connection along with all labour charges etc., complete | Civil | Labour | SWR33468 | 166 | EA | 1660
51 | 6 | Supply & fixing of 16A 3 pin and 6A 3pin plug Flush type socket with indicator lamp and 16Amps fuse unit and 16Amps switch control (5 in one )duly recessed in wall with wooden deep box of 6'' x 8'' x 2 1/2'' size covered with hylam sheet earth connection and all labour charges etc., complete on wall. | Civil | Labour | SWR33470 | 449 | EA | 2694
52 | 24 | Supply and Fixing of modular switch, LP,FP,EFP Wiring with 2 runs of 14/0.3mm (1.0 sq.mm)Fire Retardant (FR) P.V.C. insulated flexible copper cable (ISI MARK) in existing pipe with 6A Flush type Switch,ceiling rose and 3mm thick hylam sheet covering to switch control box including all labour charges etc., complete for light points, bell , fan and exhaust fan points in Non-Residential Buildings. | Civil | Labour | SWR33457 | 676 | EA | 16224
53 | 12 | Supply & Fixing of 28W T5 fluorescent tube. | Civil | Labour | SWR33558 | 148 | EA | 1776
54 | 1 | Supply of 12" (300mm)ISI, 900 RPM Heavy duty exhaust fan with metallic blades with Mark of makes Crompton / Bajaj / Havells / Orient. | Civil | Labour | SWR33571 | 2192 | EA | 2192
55 | 180 | Supply and run of 2 of 22/0.3mm (1.5 sq.mm) (FR) P.V.C. insulated flexible copper cable in existing pipe for mains including all labour charges complete. | Civil | Labour | SWR33496 | 75 | m | 13500
56 | 180 | Supply and run of 2 of 36/0.3mm (2.5 sq.mm) FR P.V.C. insulated flexible copper cable in existing pipe for mains including all labour charges complete. | Civil | Labour | SWR33497 | 103 | m | 18540
57 | 12 | Supply & fixing of batten holder /slanting holder in lieu of ceiling rose of light point complete with all connection and all labour charges with 40W bulb (for new installation). | Civil | Labour | SWR33484 | 141 | EA | 1692
58 | 4 | Supply & fixing of 1200mm (48'') sweep 230v,A.C 50 Hz.Ceiling fan with 3 Blades and double ball bearings with all standared accessories. | Civil | Labour | SWR33563 | 2277 | EA | 9108
59 | 4 | Supply & fixing of Electronic Regulator for ceiling fans 900/1200/1400mm sweep including cost of material, Electrical charges complete for finished item of work | Civil | Labour | SWR33564 | 589 | EA | 2356
60 | 1 | Providing independent EARTHING by excavating a trench to a depth of 2.1M in all solid,as per size specified in the Data,using 40mm dia 'B' class GI pipe of 2.5 Mtrs length with necessary accessories with hume pipe ring duly providing staggered holes including filling with equal proportion of salt and Charcoal in layers and all labour charges etc., compiete for small quarters. | Civil | Labour | SWR33596 | 5345 | EA | 5345
61 | 35 | Supplying, laying, jointing and testing 101.6 mm SWG SP-1 pipes of ISI make conforming to ISI 651 & 4127 with airtight cement joints in CM 1.5:1 prop. Including excavation of trenches and socket pits in any soil (except rock requiring blasting) up to 1524 mm(5'0") depth and refilling with watering and tamping. | Civil | Labour | SWR34281 | 755 | m | 26425
62 | 3 | Constructing 904.0 mm (3#0#) dia brick masonry inspection chamber as per IS - 4111: Part-1:1986 with cement mortar (1:6) prop using 2nd Class Clay Bricks of 225 mm thick from approved source having a minimum crushing strength of 5 N/sq.mm including plastering with cement mortar 1:3 prop; ½# thick both inside and outside fitted with 20# dia RCC manhole covers and frames including excavating pits up to a depth of 904 mm (3'-0") in all sorts of soils (excluding rock) and laying cement concrete (1:4:8) 150 mm thick using 40 mm HBG Metal and P.C.C. 1:2:4 benching and channel 100 mm thick as per Standard specification and including cost and conveyance of all materials like cement, sand, bricks, water etc., to site, cost of seigniorage charges on all materials and all incidental and operational, labour charges like mixing cement mortar, constructing masonry, lift charges, curing etc., complete for finished item of work as per Standard specification. | Civil | Labour | SWR34296 | 8766 | EA | 26298
63 | 4 | Supply & fixing of 110 mm dia - Door Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34381 | 128 | EA | 512
64 | 4 | Supply & fixing of 110 mm dia - Plain Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34380 | 100 | EA | 400
65 | 12 | Supply & fixing of 110 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand | Civil | Labour | SWR34377 | 462 | m | 5544
66 | 18 | Supply & fixing of 90 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand | Civil | Labour | SWR34378 | 410 | m | 7380
67 | 3 | Supplying & fixing 150 mm x 100 mm SWG gully traps conforming to ISI 651 & 4127 with C.I Grating & Cost. Brick masonry in CM 1:6 prop. Intermediate chamber and fitted with 304.8 mm x 288.6mm (12"x9") C.I Frame and hinged cover | Civil | Labour | SWR34286 | 767 | EA | 2301
68 | 1 | Supplying and Fixing of European Water Closet of 1st Quality | Civil | Labour | SWR34312 | 2228 | EA | 2228
69 | 6 | Supply & fixing 15 mm angle stop cock Indian make 400 grams Seiko/ Senior/ Nice/ Senior/ Nice or equivalent | Civil | Labour | SWR34328 | 721 | EA | 4326
70 | 4 | S&F 15 mm N.P bib tap Indian make 400 grams full turn Seiko/ Senior/ Nice or equivalent | Civil | Labour | SWR34329 | 296 | EA | 1184
71 | 1 | Supplying & Fixing Indian make Flat Back Wash Hand Basin (HSW/Parryware/ Neycer) 1st quality conforming to IS:2556-Part-4:1972 with waste fittings like rubber plug, chain, 32 mm nominal size C.P. Fitting with parallel pipe thread conforming to IS:2963-1979 and fitted with 15 mm nominal bore Chromium Plated Pillar Tap of 1st quality Indian make 400 grams Seiko/ Senior/ Nice/ Esso or equivalent complete with standard CI brackets including wooden block: 550 x 400 mm - Single C.P. Pillar cock | Civil | Labour | SWR34316 | 1717 | EA | 1717
72 | 2 | Supply & fixing 38.1 mm C.P waste coupling Half or Full Thread 1st Quality Indian make Parryware or equivalent | Civil | Labour | SWR34428 | 309 | EA | 618
73 | 2 | Supply & fixing of 4" (101.6 mm ) Nahany Trap ( Without Jali with inlet)UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34387 | 134 | EA | 268
74 | 1000 | Providing & Placing on Terrace (at all floor levels) polyethylene water storage tank with Double layer approved brand & manufacture with cover and suitable locking arrangement & making necessary holes for inlet & outlets and over flow pipes but with NECESSARY fittings & base support for tanks | Civil | Labour | SWR34375 | 10 | L | 10000
75 | 2 | Supply & fixing 31.75 mm dia PVC flexible waste pipe of 914.4 mm length of Ist quality | Civil | Labour | SWR34426 | 33 | EA | 66
76 | 45 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)- 15.90mm OD Pipe - SDR 11 | Civil | Labour | SWR34361 | 239 | m | 10755
77 | 200 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-22.20mm OD Pipe - SDR 11 | Civil | Labour | SWR34362 | 313 | m | 62600
78 | 4 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type -20mm NB Size | Civil | Labour | SWR34345 | 331 | EA | 1324
79 | 1 | Supply & fixing 25.4 mm dia & 609.6 mm long aluminium anodized towel rod with brackets and aluminium screws | Civil | Labour | SWR34430 | 489 | EA | 489
80 | 36 | Plain Cement concrete PCC (1:3:6) using 40mm HBG metal for foundations and leveling course, including cost and conveyance of all materials, labour all leads and lifts, consolidation and all operations, formwork as required, curing, etc. complete for finished item w | Civil | Labour | SWR33029 | 4975 | m3 | 179100
81 | 120 | Supply&Fabrication and fixing of Welded wire mesh ( 2" x 2") of 3mm dia. with ISMC (75x40x4.4mm) and Pheriperal frame of ISA(35x35x3mm) incldg cost& conveyance painting with synthetic enamil paint two coats over a coat of red oxide primer etc complete for finished item of work.. | Civil | Labour | SWR33403 | 2310 | m2 | 277200
82 | 1 | Providing Consultancy services for arranging contour surveying with total station incuding preparation of boundary and contour levels with 2 Nos. Hard copies and soft copies complete for finished items of work | Civil | Labour | SWR33427 | 5665 | EA | 5665
83 | 222.2468 | Seigniorage Charges - Sand | Civil | Labour | SWR34470 | 40 | m3 | 8889.873
84 | 725.7496 | Seigniorage Charges - Metal | Civil | Labour | SWR34471 | 97.5 | m3 | 70760.585
85 | 839.38 | Seigniorage Charges - Gravel | Civil | Labour | SWR34472 | 30 | m3 | 25181.4
86 | 60 | Supply and fixing of RCC fencing poles of size 0.1mx0.1mx1.8m (security fencing of sub station), including cost and conveyance of all labour, materials,and hire chareges etc complete for finished item of work. | Civil | Labour | Swr33405 | 1444 | EA | 86640
87 | 1200 | Supply and fixing of galvanised barded wire (1 horizantal & 2 cross strands. including cost and conveyance of all labour, materials,and hire chareges etc complete for finished item of work. | Civil | Labour | Swr33408 | 16 | m | 19200
Civil total | [7 empty] | 4231964.69
Total elec+civil | [7 empty] | 17064948.619

## 6. Bairagiguda
Name of the work: Estimate for erection of new 33/11kV outdoor sub-station at Baiaragiguda with 2x8 MVA PTRs and connected 33kV, 11kV Lines at Baiaragiguda in Himayathsagar (M), Rajendranagar Circle in ECGH Division/MasterPlan/RR Circle
WBS No. S-1790-13-03-02-01-001
Sl No | Estimate Quantity | Description of item | Work Type | Item Short Description | APSS / Month Cl.NumberSSR 11 & 12 | Rate (INR) | UOM | AMOUNT
1 | 16 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | ELEC | Labour | SWR11039 | 928 | EA | 14848
2 | 5.76 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ELEC | Labour | SWR10868 | 6852 | TO | 39467.52
3 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELEC | supply | SMR40009 | 2181 | TO | 12562.56
4 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELEC | labour | SWR10877 | 851 | TO | 4901.76
5 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELEC | supply | SMR40010 | 1293 | TO | 7447.68
6 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELEC | labour | SWR10879 | 482 | TO | 2776.32
7 | 5.76 | Fabrication & erection of Channels-Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ELEC | labour | SWR10867 | 1470 | TO | 8467.2
8 | 16 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-R.S. Joists 150 x 150 mm | ELEC | labour | SWR10348 | 1952.61 | EA | 31241.76
9 | 17.758 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 116829.882
10 | 9.24 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ELEC | labour | SWR10862 | 373 | M2 | 3446.52
11 | 16 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | ELEC | labour | SWR11089 | 48 | EA | 768
12 | 4 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-8.0Mtrs PSCC Poles 0.76 M x 0.76M x 1.52M (2.6" x 2.6" x 5.0') 0.88 cum | ELEC | labour | SWR11037 | 793 | EA | 3172
13 | 1 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ELEC | Labour | SWR10868 | 6852 | TO | 6852
14 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELEC | supply | SMR40009 | 2181 | TO | 2181
15 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELEC | labour | SWR10877 | 851 | TO | 851
16 | 1 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELEC | supply | SMR40010 | 1293 | TO | 1293
17 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELEC | labour | SWR10879 | 482 | TO | 482
18 | 1 | Fabrication & erection of Channels-Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ELEC | labour | SWR10867 | 1470 | TO | 1470
19 | 4 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Box pole 12 Mtr | ELEC | labour | SWR11267 | 3901.37 | EA | 15605.48
20 | 2.65 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 17434.35
21 | 2.31 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ELEC | labour | SWR10862 | 373 | M2 | 861.63
22 | 4 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | ELEC | labour | SWR11089 | 48 | EA | 192
23 | 5.063 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ELEC | labour | SWR10868 | 6852 | TO | 34691.676
24 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELEC | supply | SMR40009 | 2181 | TO | 11042.403
25 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELEC | labour | SWR10877 | 851 | TO | 4308.613
26 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELEC | labour | SMR40010 | 1293 | TO | 6546.459
27 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELEC | labour | SWR10879 | 482 | TO | 2440.366
28 | 5.063 | Fabrication & erection of Channels-Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ELEC | labour | SWR10867 | 1470 | TO | 7442.61
29 | 13 | Erection of AB Switch and aligment complete Erection of 33 KV AB Switch including alignment and earthing | ELEC | labour | SWR10392 | 4500 | EA | 58500
30 | 34 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Note:-The requirement of 2nd coat is to be justified by the concerned Divisional Engineer /Executive Engineer before execution of this work Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | ELEC | labour | SWR10881 | 142 | EA | 4828
31 | 34 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | ELEC | labour | SWR12331 | 146.63 | EA | 4985.42
32 | 6 | Loading of 33 KV CTs/ PTs | ELEC | labour | SWR10200 | 165 | EA | 990
33 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
34 | 6 | Un loading of 33 KV CTs/ PTs | ELEC | labour | SWR10518 | 128 | EA | 768
35 | 2 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33kv single phase PT s | ELEC | labour | SWR10401 | 1079 | SET | 2158
36 | 12 | Loading of 33 KV, 10 KA LAs Station typ | ELEC | labour | SWR10266 | 41 | EA | 492
37 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
38 | 12 | Un loading of 33 KV, 10 KA LAs Station type | ELEC | labour | SWR10584 | 35 | EA | 420
39 | 4 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33 KV LAS station/Line type including earthing | ELEC | labour | SWR10396 | 880 | SET | 3520
40 | 2 | Loading of 33 KV VCBs along with Panel boards | ELEC | labour | SWR10198 | 1024 | EA | 2048
41 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
42 | 2 | Un loading of 33 KV VCBs along with Panel boards | ELEC | labour | SWR10516 | 1044.48 | EA | 2088.96
43 | 12.584 | Excavate-Pit for 33KV VCB | ELEC | labour | SWR23224 | 331 | M3 | 4165.304
44 | 14.52 | Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x 1.8 x 0.75 cum for VCB Plinth | ELEC | labour | SWR20685 | 5160 | M3 | 74923.2
45 | 2 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33 KV VCB with Control Panel | ELEC | labour | SWR10460 | 12500 | EA | 25000
46 | 2 | Loading and unloading of PTR on constructed plinth-Loading of 8MVA PTR | ELEC | labour | SWR10613 | 5805.84 | EA | 11611.68
47 | 2 | Transport of Power transformers (0 to 100 KM) from one place to another place in GHMC Area.(excluding of loading & unloading )-8MVA power transformer | ELEC | labour | SWR10854 | 21945 | EA | 43890
48 | 2 | Loading and unloading of PTR on constructed plinth-Unloading of 8MVA PTR | ELEC | labour | SWR10627 | 5805.84 | EA | 11611.68
49 | 700 | S/o rail poles 90/105lb (250x2N) | ELEC | supply | SMR22718 | 47.27 | KG | 33089
50 | 14 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Rail pole 90 lbs | ELEC | labour | SWR10344 | 3510 | EA | 49140
51 | 2 | Erection of PTR on constructed plinth-Erection of 8 MVA PTR. | ELEC | labour | SWR21321 | 49480.2 | 49480.2 | 98960.4
52 | 0.436 | Extention of 33KV Bay at 132/33KV Sub-station-Zebra condutor | ELEC | supply | SMR24910 | 299369 | 299369 | 130524.884
53 | 30 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing | ELEC | supply | SMR11915 | 2055 | 2055 | 61650
54 | 30 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of I-Bolts | ELEC | supply | SMR22473 | 294 | 294 | 8820
55 | 45 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 "to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating . Sup T clamp LM6 Al alloy of 12 mm, 800 A | ELEC | labour | SMR40011 | 299 | 299 | 13455
56 | 6 | Bus stringing Hoisting of Insulators and hardware, stretching the conductor and stringing of 33 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bussection of 4.5mt) Hoisting post ins&hrd wr 1panther 33kv | ELEC | labour | SWR21240 | 781 | 781 | 4686
57 | 84 | Stringing of bus with panther conductor including jumpering etc., complete to all the equipment in SS fixing to all clamps and equipment.(3 Conductors) | ELEC | labour | SWR10404 | 327.68 | 327.68 | 27525.12
58 | 30 | Bus stringing Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | ELEC | labour | SWR10884 | 224 | 224 | 6720
59 | 75 | Labour for Fixing of all types of clamps | ELEC | labour | SWR10917 | 65 | 65 | 4875
60 | 25 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | ELEC | labour | SWR11039 | 928 | 928 | 23200
61 | 8.68 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ELEC | labour | SWR10868 | 6852 | 6852 | 59475.36
62 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELEC | supply | SMR40009 | 2181 | 2181 | 18931.08
63 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELEC | labour | SWR10877 | 851 | 851 | 7386.68
64 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELEC | supply | SMR40010 | 1293 | 1293 | 11223.24
65 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELEC | labour | SWR10879 | 482 | 482 | 4183.76
66 | 8.68 | Fabrication & erection of Channels-Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ELEC | labour | SWR10867 | 1470 | 1470 | 12759.6
67 | 25 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-R.S. Joists 150 x 150 mm | ELEC | labour | SWR10348 | 1952.61 | 1952.61 | 48815.25
68 | 27.75 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | 6579 | 182567.25
69 | 17.91 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ELEC | labour | SWR10862 | 373 | 373 | 6680.43
70 | 25 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | ELEC | labour | SWR11089 | 48 | 48 | 1200
71 | 4.642 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ELEC | labour | SWR10868 | 6852 | 6852 | 31806.984
72 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELEC | supply | SMR40009 | 2181 | 2181 | 10124.202
73 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELEC | labour | SWR10877 | 851 | 851 | 3950.342
74 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELEC | supply | SMR40010 | 1293 | 1293 | 6002.106
75 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELEC | labour | SWR10879 | 482 | TO | 2237.444
76 | 4.642 | Fabrication & erection of Channels-Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ELEC | labour | SWR10867 | 1470 | TO | 6823.74
77 | 17 | Erection of AB Switch and aligment complete-Erection of 11KV 800A double throw AB Switches | ELEC | labour | SWR21277 | 3500 | EA | 59500
78 | 3 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | ELEC | labour | SWR10393 | 3200 | EA | 9600
79 | 2 | Loading of 11 KV CT - PT Sets | ELEC | labour | SWR10201 | 190 | EA | 380
80 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
81 | 2 | Un loading of 11 KV CT - PT Sets | ELEC | labour | SWR10519 | 101 | EA | 202
82 | 2 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc-Erection of 11 KV three phase PTs | ELEC | labour | SWR10402 | 800 | SET | 1600
83 | 24 | Loading of 11 KV, 10 KA LAs Station type | ELEC | labour | SWR10264 | 32 | EA | 768
84 | 2 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 6599.4
85 | 24 | Un loading of 11 KV, 10 KA LAs Station type | ELEC | labour | SWR10582 | 32 | EA | 768
86 | 2 | Erection of 11 KV LAS station type including earthing | ELEC | labour | SWR10397 | 559 | SET | 1118
87 | 6 | Erection of 11 KV LAS line type including earthing | ELEC | labour | SWR10398 | 505 | SET | 3030
88 | 8 | Loading of 11 KV VCBs along with Panel boards | ELEC | labour | SWR10199 | 1024 | EA | 8192
89 | 4 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 13198.8
90 | 8 | Un Loading of 11 KV VCBs along with Panel boards | ELEC | labour | SWR10517 | 1044.48 | EA | 8355.84
91 | 41.6 | Excavate-Pit for 33KV VCB | ELEC | labour | SWR23224 | 331 | M3 | 13769.6
92 | 48 | Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x 1.8 x 0.75 cum for VCB Plinth | ELEC | labour | SWR20685 | 5160 | M3 | 247680
93 | 8 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc-Erection of 11 KV VCB with Control Panel | ELEC | labour | SWR10461 | 12000 | EA | 96000
94 | 12 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing | ELEC | supply | SMR11915 | 2055 | SET | 24660
95 | 12 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of I-Bolts | ELEC | supply | SMR22473 | 294 | EA | 3528
96 | 45 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 "to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating . Sup T clamp LM6 Al alloy of 12 mm, 800 A | ELEC | supply | SMR40011 | 299 | EA | 13455
97 | 2 | Bus Stringing -Hoisting of Insulators and hardware, stretching the conductor and stringing of 11 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 3.5mt) Hoisting post ins&hrd wr 1panther 11kv | ELEC | labour | SWR21241 | 507 | EA | 1014
98 | 63 | Stringing of bus with panther conductor including jumpering etc., complete to all the equipment in SS fixing to all clamps and equipment.(3 Conductors) | ELEC | labour | SWR10404 | 327.68 | M | 20643.84
99 | 45 | Bus stringing Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | ELEC | labour | SWR10884 | 224 | EA | 10080
100 | 57 | Labour for Fixing of all types of clamps | ELEC | labour | SWR10917 | 65 | EA | 3705
101 | 584 | Laying of earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication 75x 8mm MS Flat / GI Flat. Laying of earth mat,excavation 75x 8mm | ELEC | labour | SWR10920 | 65 | RMT | 37960
102 | 1010 | Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) Earthing for raisers of SS Flat 50x6 mm. | ELEC | labour | SWR10919 | 41 | RMT | 41410
103 | 36 | Supply of earthing pipe with materials -Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | ELEC | supply | SMR11482 | 3486 | EA | 125496
104 | 36 | Providing of Earthing-Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | ELEC | labour | SWR10357 | 1234.2 | EA | 44431.2
105 | 36 | Providing of RCC collar to earth pit-Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINES-Providing of RCC collar | ELEC | labour | SWR10359 | 386 | EA | 13896
106 | 2 | Supply of Copper Flexible jumper with 75 X 8 of length 250 mm at neutral of Power tranformer end and 50 X 6 of length 50mm two Nos at double neutral end duly brasing with flexible jumper of capacity of 5kA/3 sec for power transformer neutral. SupCU Flexi jumper for Power T/F Neutral | ELEC | supply | SMR40033 | 4725 | EA | 9450
107 | 2 | Providing of earthing with various types of earth electrodes-Providing of double earthing for neutral with flexible copper jumpers including arrangement by fixing M.S.Channel 100x50mm. | ELEC | labour | SWR11892 | 1323 | EA | 2646
108 | 80 | Providing of control cable trench as per DATA-XII | ELEC | labour | SWR22093 | 3148 | RMT | 251840
109 | 3074 | Control Cable-Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends . Lay-4C/10C 2.5Sqmm Control Cable | ELEC | labour | SWR11879 | 27 | M | 82998
110 | 270 | Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per specification (including cost of ferrules, lugs and glands) | ELEC | labour | SWR12510 | 27 | EA | 7290
111 | 4 | Marshalling Box Supply of FRP PT Marshalling Box | ELEC | supply | SMR40048 | 4463 | EA | 17852
112 | 4 | Marshalling Box Erection of Marshalling boxes | ELEC | labour | SWR10940 | 374.85 | EA | 1499.4
113 | 1 | Loading of 220 V Batterry with charger | ELEC | labour | SWR11166 | 1612 | SET | 1612
114 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
115 | 1 | Un loading of 220 V Batterry with charger | ELEC | labour | SWR11147 | 1024 | SET | 1024
116 | 1 | Batteries-Erection of 220 V, 200 AH battery in complete shape fit for charging . Conventional lead acid | ELEC | labour | SWR12350 | 7666 | EA | 7666
117 | 1 | Control Panels -Supply of DC Annunciation & relay panel for 10 feeder panel including the cost of LED Indiacation lamps, VAA auxilairy relays, Electronic Hooters complete as per specification. | ELEC | supply | SMR40044 | 42500 | EA | 42500
118 | 1 | Control Panels -Supply of AC Supply panel inluding providing of changeover switch, SFU, metering unit, 32 A three phase MCB, 16 A Single phase MCB complete as per specification. Supply of AC Supply panel complete | ELEC | supply | SMR40045 | 42000 | EA | 42000
119 | 2 | Fixing of AC/DC Panel and giving Connections to the protection equipment and Metering circuits as per the specification and standards. The 3 1/2 core 25 Sqmm power cable required from distribution box to AC/DC panel in the control room is also to be supply | ELEC | labour | SWR20025 | 7871.85 | SET | 15743.7
120 | 8 | Yard lightning-Supply of stepped tubular poles single way made of steel of length 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9 mm, 2.1 mtrs with outer dia 76.1 mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79 kgf as per IS 2713 | ELEC | supply | SMR40051 | 13913 | EA | 111304
121 | 8 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE/CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA /OSRAM /SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty S-90W LED fixture set | ELEC | labour | SMR11594 | 8200 | EA | 65600
122 | 8 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | ELEC | labour | SWR11039 | 928 | EA | 7424
123 | 8 | Erection of tubular poles | ELEC | labour | SWR10955 | 1379 | EA | 11032
124 | 5.27 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 34671.33
125 | 8 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE/CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA /OSRAM /SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty. Fixing of Metal halide lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5 GI pipe complete Fixing of LED/Metal halide complete. | ELEC | labour | SWR10956 | 1268 | EA | 10144
126 | 45 | Supply of HBG metal-Supply & spreading of 20mm machine crushed metal (HBG) including cost of conveneyance of all materials, labour charges etc complete for finished item of work and directed by the engineer incharge | ELEC | labour | SWR10860 | 2113 | M3 | 95085
127 | 2 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M Ex of Hard pit w/o blast 0.75X0.9X1.95M | ELEC | labour | SWR11040 | 990.68 | EA | 1981.36
128 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELEC | Supply | SMR40009 | 2181 | TO | 1635.75
129 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELEC | labour | SWR10877 | 851 | TO | 638.25
130 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELEC | Supply | SMR40010 | 1293 | TO | 969.75
131 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELEC | labour | SWR10879 | 482 | TO | 361.5
132 | 1 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Box pole 12 Mtr | ELEC | labour | SWR11267 | 3901.37 | EA | 3901.37
133 | 2.22 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 14605.38
134 | 1.16 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ELEC | labour | SWR10862 | 373 | M2 | 432.68
135 | 2 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | ELEC | labour | SWR11089 | 48 | EA | 96
136 | 1 | Construction of DTR Plinth-RCC Column type DTR Plinth of size 1'X1'X10',topslab 4'x4'x6" & beam size 4'X8'X8" upto 160KVA | ELEC | labour | SWR21843 | 25967.57 | EA | 25967.57
137 | 1 | Loading of 50,63, 75 & 100 KVA DTR | ELEC | labour | SWR10195 | 350 | EA | 350
138 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
139 | 1 | Un loading of 50,63, 75 & 100 KVA DTR | ELEC | labour | SWR10513 | 280 | EA | 280
140 | 1 | Erection of DTR's including loading and Unloading DTR on the Structure/Plinth etc-Erection of 3 Phase DTRs 63,75 & 100 KVA | ELEC | labour | SWR20905 | 1650 | EA | 1650
141 | 1 | Erection of AB Switch and aligment complete Erection of 11KV 200A TT type AB Switch including fixing of cross angles and alignment complete | ELEC | labour | SWR20102 | 1813.49 | EA | 1813.49
142 | 40 | Excavation & laying of UG Cable in Single Run Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.-In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road-11KV 3x185 Sqmm Cable | ELEC | labour | SWR11920 | 465.46 | M | 18618.4
143 | 20 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-11 KV 3x185 Sqmm Cable | ELEC | labour | SWR11956 | 126.23 | M | 2524.6
144 | 2 | Making of Outdoor/Indoor End Termination Making 11 KV 3x185 Sqmm Cable Out Door/Indoor end termination | ELEC | labour | SWR10390 | 2370.63 | EA | 4741.26
145 | 1 | Erection of LT distribution box including laying of LT cable from distribution box to LT OH line and DTR to distribution box including earthing of distribution box and crimping of lugs connecting of jumpers etc | ELEC | labour | SWR10674 | 1594.67 | EA | 1594.67
146 | 85 | LAYING OF 33KV, 11KV UG CABLE Excavation & laying of UG Cable in Single Run Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road-LT 3 1/2 x 185 Sqmm Cable | ELEC | labour | SWR11923 | 377.63 | M | 32098.55
147 | 15 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-LT 3 1/2 x 185 Sqmm Cable | ELEC | labour | SWR11959 | 85.43 | M | 1281.45
148 | 2 | UG Cables Joints :-Making of Outdoor/Indoor End Termination -Supply & fixing of Oout Door/Indoor end termination LT 3 1/2 x 185 Sqmm Cable | ELEC | labour | SWR10765 | 968.9 | EA | 1937.8
149 | 1 | Supply and fixing of Substation board of size 3'x2.5' indicating the layout of switchyard Sup &fix of board ind Switchyard layout | ELEC | labour | SWR20032 | 1654 | EA | 1654
150 | 1 | Supply and fixing of safety instructions/Substation operation instruction board. Sup& fix safety inst/SS Op. inst board | ELEC | labour | SWR22090 | 2205 | EA | 2205
151 | 750 | Control Panels Supplying & fabrication erection of 6mm Checkerd plates as per the field conditions Supply,fabricati of 6mm Checkerd plates | ELEC | Labour | SWR10873 | 83 | KG | 62250
152 | 1 | T & P Supply of Wall clock standard make | ELEC | Supply | SMR40059 | 578 | EA | 578
153 | 1 | S-10ft Aluminium Ladder | ELEC | Supply | SMR12378 | 1654 | EA | 1654
154 | 1 | Sup Alluminium Ladder for indoor works | ELEC | Supply | SMR40062 | 4410 | EA | 4410
155 | 30 | T & P Painting of Name Plates for any equipmen | ELEC | labour | SWR10963 | 122 | EA | 3660
156 | 1 | T & P Supply of Taparia Tool kit of Size 20”x10”x15” with tier arrangements Tool box with locking arrangement & key containing (1) Double Ended fix Spanner sets, (Ribbed) 6 x 7, 8 x 9, 10 x 11, 12 x 13, 14 x 15, 16 x 17, 18 x19, 20 x 22, 21 x 23, 24 x 27, 25 x28, 30 x 32, (2) Double Ended Ring Spanners sets, 6 x 7 , 8 x 9, 10 x 11, 12 x 13, 14 x 15. 16 x 17 , 18 x 19, 20 x 22 , 21 x 23, 24 x 27, 25 x28, 30 x 32 mm, (3) Adjustable Spanner 305 mm length least maximum opening 35mm chrome, (4) Pipe Wrench Length 350 mm 14”, (5) Soft faced Hammer with suitable handle 2 lb, (6) Hacksaw frame with metal handle heavy duty for 12" hacksaw blade with High Speed blade, (7) Insulated Screw drivers Transparent Green Handle Set Length 6”, 8” & 12”, (8) Star Screw Driver Transparent Green Handle Length 6”, (9) Insulated Wire Cutter, (10) Insulated Cutting Plier Length 8” with cable stripper insulated with thick C. A. sleeve confirming to IS: 4378 - 1990, (11) Long Nose Plier insulated with thick C.A. sleeve generally confirming to IS:3552-1989, (12) Tester type screw driver (special with neon bulb) generally confirm to IS: 5579- 1985 Grade:II handle yellow/ green colour overall length 130 mm, (13) Insulated Crimping Plier of all Taparia make. SupTaparia Tool kit complete as per Spec | ELEC | Supply | SMR40063 | 4925 | SET | 4925
157 | 1 | T & P Sup Rechargeable LED torch light of Standard make | ELEC | Supply | SMR40064 | 1733 | EA | 1733
158 | 1 | T & P-Steel almarah(61/2 X 3ft) Godrej | ELEC | Supply | SMR40061 | 9818 | EA | 9818
159 | 4 | T & P-S type chairs (Godrej) | ELEC | Supply | SMR40058 | 924 | EA | 3696
160 | 1 | T & P Sup Angle racks(18x36.6inches) Godrej | ELEC | Supply | SMR40060 | 1733 | EA | 1733
161 | 1 | T & P Supply of Hack saw (12 inches) | ELEC | Supply | SMR40065 | 289 | EA | 289
162 | 4 | Sup Earth Rods (8ft) Screw & clamp type | ELEC | Supply | SMR40066 | 578 | EA | 2312
163 | 2 | Supply of Hand Gloves | ELEC | Supply | SMR40067 | 289 | SET | 578
164 | 12 | SupRubber mats( 6'x3')size fo indoorSS | ELEC | Supply | SMR40068 | 1386 | EA | 16632
165 | 1 | Biometric Time attendence System & Telecom Sup Stand basic cell phone with charger | ELEC | Supply | SMR40069 | 1386 | EA | 1386
166 | 14 | Supply of Danger boards with clamps | ELEC | Supply | SMR40070 | 116 | EA | 1624
167 | 2 | Supply of Materials -Fire bucket stand with 3 buckets (8 -10 ltr capacity) | ELEC | Supply | SMR40088 | 1386 | SET | 2772
168 | 2 | Room fire extinguisher (2 ltrs capacity) for control room | ELEC | Supply | SMR40089 | 4620 | EA | 9240
169 | 4 | Sup TrollyMounted Co2 (6.5Kgs) Cylinders(IS-2878) | ELEC | Supply | SMR40087 | 9240 | EA | 36960
170 | 6 | Supply of Safety Helmet of standard make | ELEC | Supply | SMR40071 | 231 | EA | 1386
171 | 8 | Supply of LC Boards | ELEC | Supply | SMR40072 | 116 | EA | 928
172 | 4 | Supply of Gum Boots(Pairs) | ELEC | Supply | SMR40073 | 693 | EA | 2772
173 | 1 | Supply of 5000v megger | ELEC | Supply | SMR40074 | 13860 | EA | 13860
174 | 1 | Supply of Earth megger (1000v) | ELEC | Supply | SMR40075 | 8085 | EA | 8085
175 | 1 | Supply of Digital clamp meter. | ELEC | Supply | SMR40076 | 2888 | EA | 2888
176 | 1 | Name board of the 33/11kV Sub-Station(As per Standard Specification) Sup 33/11kv S.S Permanent name board | ELEC | Supply | SMR40086 | 10238 | EA | 10238
177 | 800 | Supply of Hot dip galvanized/zinc coated bolts & nuts including spring washers, pack washers and flat washers etc. | ELEC | Supply | SMR12488 | 90 | KG | 72000
178 | 2 | Fabrication of poles-Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | ELEC | labour | SWR10642 | 512.55 | EA | 1025.1
179 | 1 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-RS Joists 150x75/175 x 85 mm | ELEC | labour | SWR10346 | 1934 | EA | 1934
180 | 5760 | S-Supply of RS Joist Grider Pole (150x150mm) | ELEC | Supply | SMR12302 | 59.25 | KG | 341280
181 | 1000 | S-Supply of RS Joist Pole (175x85mm) | ELEC | Supply | SMR12303 | 60.75 | KG | 60750
182 | 5063 | S- Supply of MS Channel 100x50mm | ELEC | Supply | SMR22745 | 57.45 | KGS | 290869.35
183 | 13 | S-Supply of 33KV 800A DB Break AB Switch | ELEC | Supply | SMR12315 | 40658.78 | EA | 528564.14
184 | 8680 | S-Supply of RS Joist Grider Pole (150x150mm) | ELEC | Supply | SMR12302 | 59.25 | KG | 514290
185 | 4642 | S- Supply of MS Channel 100x50mm | ELEC | Supply | SMR22745 | 57.45 | KGS | 266682.9
186 | 17 | S-Supply of 11KV 800A DB Break AB Switch | ELEC | Supply | SMR12316 | 30847.46 | EA | 524406.82
187 | 3 | S-Supply of 11KV 400A DB Break AB Switch | ELEC | Supply | SMR12317 | 18150 | EA | 54450
188 | 3045 | S-Supply of MS Flat 75x8mm | ELEC | Supply | SMR12321 | 56.42 | KG | 171798.9
189 | 2666 | S-Supply of MS Flat 50x6mm | ELEC | Supply | SMR12322 | 56.5 | KG | 150629
190 | 750 | S-Supply of RS Joist Pole (175x85mm) | ELEC | Supply | SMR12303 | 60.75 | KG | 45562.5
191 | 1 | S-Supply of 11KV 200A Tilting Type AB Switch | ELEC | Supply | SMR12318 | 8991 | EA | 8991
192 | 1 | S-Supply of 11KV HG FuseSet for StationTransformer | ELEC | Supply | SMR12324 | 1974 | EA | 1974
193 | 1 | S-Supply of LT Distribution Box (SMC) | ELEC | Supply | SMR25200 | 7797 | EA | 7797
194 | 2 | S-Supply of 11KV 3x185 Heat Shble O/d End Term Kit | ELEC | Supply | SMR25201 | 1182.97 | EA | 2365.94
195 | 40 | S-Supply of LT XLPE Cable 1C 150 sqmm | ELEC | Supply | SMR25203 | 114.83 | M | 4593.2
196 | 100 | Supply of LT XLPE Cable 31/2C185sqmm. | ELEC | supply | SMR25204 | 547 | M | 54700
197 | 1 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erect. of 11kv HG Fuseset incl earthing | ELEC | labour | SWR10395 | 740.52 | SET | 740.52
198 | 1 | T & P-Table (3x6ft) Godrej | ELEC | Supply | SMR40057 | 6050 | EA | 6050
199 | 4 | Loading of LT AB Cable 3X16+25 Sqmm | ELEC | labour | SWR11702 | 200 | DR | 800
200 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
201 | 4 | Un loading of LT AB Cable 3X16+25 Sqmm | ELEC | labour | SWR11713 | 204 | DR | 816
202 | 22.2 | survey line&cabl inc peg mark&tree clear | ELEC | labour | SWR22092 | 765 | KM | 16983
203 | 22.2 | Paving out and stringing of conductor by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location-100 Sqmm Single Circuit (3 Conductors) | ELEC | labour | SWR10366 | 13856.7 | KM | 307618.74
204 | 124 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M Ex of Hard pit w/o blast 0.75X0.9X1.95M | ELEC | labour | SWR11040 | 990.68 | EA | 122844.32
205 | 124 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Errection of 11 M long PSCC pole | ELEC | labour | SWR10978 | 4336.85 | EA | 537769.4
206 | 43.317 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 284982.543
207 | 124 | Painting of poles-Numbering of poles incl. cost of paint | ELEC | labour | SWR10378 | 32 | EA | 3968
208 | 45 | Excavation of pits in all soils except hard rock requiring blasting-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") 1.05 cum | ELEC | labour | SWR10107 | 700 | EA | 31500
209 | 45 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Erec of 9.1 Mts PSCC poles for stuts | ELEC | labour | SWR11083 | 2400 | EA | 108000
210 | 23.625 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 155428.875
211 | 24 | Formation of Cut points - Formation of Cut point for 11 KV Single Circuit line excluding pole erection and stays Formatn of Horiz Cut point for 11KV line | ELEC | labour | SWR10653 | 1435.81 | EA | 34459.44
212 | 200 | Supply of earthing pipe with materials S-GI Bolts & Nuts,Washers etc., | ELEC | supply | SMR11488 | 117.5 | KG | 23500
213 | 10 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 50 Km and upto 80 Km with Lorry for each trip | ELEC | labour | SWR11864 | 5290.74 | EA | 52907.4
214 | 21 | LOADING of Conductor drums | ELEC | labour | SWR10191 | 202 | EA | 4242
215 | 21 | UNLOADING of Conductor drums | ELEC | labour | SWR10509 | 100 | EA | 2100
216 | 97 | Loading of 33 KV Pin insulators | ELEC | labour | SWR10211 | 3 | CRT | 291
217 | 97 | Un loading of 33 KV Pin insulators | ELEC | labour | SWR10529 | 3 | CRT | 291
218 | 15 | Loading of 33 KV Metal parts | ELEC | labour | SWR10618 | 65 | BAG | 975
219 | 15 | Un loading of 33 KV Metal parts | ELEC | labour | SWR10632 | 65 | BAG | 975
220 | 960 | Excavation & laying of UG Cable (Double Run) Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, Along the CC / BT multi layer road requiring compressor-33 KV 3x400 Sqmm Cable | ELEC | labour | SWR11980 | 1388.84 | M | 1333286.4
221 | 960 | Laying of 2nd cable in excavated trench | ELEC | labour | SWR10988 | 204.1 | M | 195936
222 | 40 | Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-33 KV 3x400 Sqmm Cable | ELEC | labour | SWR12004 | 323.85 | M | 12954
223 | 12 | Cost of Pipes and slabs-Supply of 6" B class GI pipe | ELEC | supply | SMR40081 | 1044 | M | 12528
224 | 30 | Cost of Pipes and slabs-Supply of 250 mm Hume pipe of class NP3 with compresive strength of 35N/mm2 for 28 days curing,barewall thickness of 30mm,1.25kG linear/meter and withstanding capability of 22.50KN/linear meter as per IS 458-1993. | ELEC | supply | SMR40077 | 363 | M | 10890
225 | 6 | Cost of Pipes and slabs-Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters , CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | ELEC | supply | SMR40085 | 484 | EA | 2904
226 | 6 | Load-11/33KV XLPE UG Cable for all sizes | ELEC | labour | SWR11230 | 1024 | DR | 6144
227 | 6 | Unload-11/33KV XLPE UG Cable for all sizes | ELEC | labour | SWR11231 | 1024 | DR | 6144
228 | 8 | Making of Outdoor/Indoor End Making 33 KV 3x400 Sqmm Cable Out Door/Indoor end termination TerminationOD/Idoor end termination 33kv 3x400 xlpe | ELEC | labour | SWR10387 | 2764.76 | EA | 22118.08
229 | 2 | UG Cables Joints 33 KV 3x400 Sqmm Cable Straight through joint 33kv 3x400 xlpe | ELEC | labour | SWR10382 | 5700.78 | EA | 11401.56
230 | 2.1 | Fabrication & erection of Channels -Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to theRS-Joist poles excluding cost of Mild Steel and transportcharges to substation site, including erection. Fabrication of struc.with welding. | ELEC | labour | SWR10869 | 3426 | TO | 7194.6
231 | 50 | Supply of earthing pipe with materials-Supply of GI wire No 8 | ELEC | supply | SMR11486 | 105 | KG | 5250
232 | 2 | Supply of earthing pipe with materials-Supply of CI eath pipe with 80mm dia,2.0 M Length | ELEC | labour | SMR11483 | 2789 | EA | 5578
233 | 2 | Providing of Earthing-Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | ELEC | labour | SWR10357 | 1234.2 | EA | 2468.4
234 | 2 | Providing of RCC collar to earth pit-Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINES-Providing of RCC collar | ELEC | labour | SWR10359 | 386 | EA | 772
235 | 40 | Supply of earthing pipe with materials-Supply of GI Flat 25X3 mm | ELEC | supply | SMR11485 | 105 | KG | 4200
236 | 20 | Supply of Danger boards with clamps | ELEC | supply | SMR40070 | 116 | EA | 2320
237 | 30 | Supply of M+3 Tower (Galvanized) | ELEC | supply | SMR11683 | 140674.3 | EA | 4220229
238 | 142.56 | Earth work excavation of pits in hard rock requiring blasting.(wherever feasible/ required) | ELEC | labour | SWR20769 | 1012.35 | M3 | 144320.616
239 | 30 | Supply of material for Extension of 3Mtrs for M+3 (Galvanized) S-Mat. for Extn of M+3 Tower by 3M GALV | ELEC | supply | SMR11684 | 28520.64 | EA | 855619.2
240 | 30 | Erection of M+3 Tower GALV | ELEC | labour | SWR11850 | 64576 | EA | 1937280
241 | 30 | Erection of Extension of 3Mtrs for M+3 (Galvanized) | ELEC | labour | SWR11851 | 5168.95 | EA | 155068.5
242 | 6 | S&E-Smart RFID marker | ELEC | labour | SWR25089 | 2745 | EA | 16470
243 | 124 | Supply of PSCC Pole 11Mtr 365KG | ELEC | supply | SMR25236 | 5399 | EA | 669476
244 | 45 | Supply of PSCC Pole 9.1Mtr 280KG | ELEC | supply | SMR25233 | 3109.41 | EA | 139923.45
245 | 1200 | Supply of Materials -- Supply of MS Channel 100X50mm | ELEC | supply | SMR22745 | 57.45 | KGS | 68940
246 | 700 | Supply of MS Angle 65x65x6 | ELEC | supply | SMR25207 | 57.25 | KG | 40075
247 | 200 | Supply of Materials -- Supply of MS Flat 75x8 mm | ELEC | supply | SMR12321 | 56.42 | KG | 11284
248 | 8 | UG Cables Joints : Making of Outdoor/Indoor End Termination -- Supply 33KV 3x400Sqmm Outdoor | ELEC | supply | SMR22222 | 4554 | EA | 36432
249 | 2 | UG Cables Joints : Making of Straight through joints -- Supply of 33KV 3x400SQmm Straight Through Joint Kit | ELEC | supply | SMR22223 | 24151 | EA | 48302
250 | 200 | Supply of 33KV V-Cross Arm without Clamps | ELEC | supply | SMR25229 | 1678 | EA | 335600
251 | 9 | survey line&cabl inc peg mark&tree clear | ELEC | labour | SWR22092 | 765 | KM | 6885
252 | 9 | Paving out and stringing of conductor by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location-55 Sqmm Single Circuit (3 Conductors) | ELEC | labour | SWR10365 | 9454.81 | KM | 85093.29
253 | 175 | Excavation of pits in all soils except hard rock requiring blasting-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") 1.05 cum | ELEC | labour | SWR10107 | 700 | EA | 122500
254 | 50 | Excavation of pits in hard rock requiring blasting. (other than SS)-9.1Mtrs PSCC Pole 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | ELEC | labour | SWR10112 | 1770 | EA | 88500
255 | 213 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-9.1 M long PSCC pole | ELEC | labour | SWR10343 | 2400 | EA | 511200
256 | 37.8 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 248686.2
257 | 225 | Painting of poles-Numbering of poles incl. cost of paint | ELEC | labour | SWR10378 | 32 | EA | 7200
258 | 80 | Excavation of pits in all soils except hard rock requiring blasting-Stud Poles 0.6 M x 0.9 M x 1.5 M | ELEC | labour | SWR10106 | 645 | EA | 51600
259 | 80 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-8.0 m long PSCC poles for Strut | ELEC | labour | SWR21590 | 1500 | EA | 120000
260 | 32 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 210528
261 | 40 | Formation of Cut points - Formation of Cut point for 11 KV Single Circuit line excluding pole erection and stays Formatn of Horiz Cut point for 11KV line | ELEC | labour | SWR10653 | 1435.81 | EA | 57432.4
262 | 350 | Supply of earthing pipe with materials S-GI Bolts & Nuts,Washers etc., | ELEC | supply | SMR11488 | 117.5 | KG | 41125
263 | 4 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 50 Km and upto 80 Km with Lorry for each trip | ELEC | labour | SWR11864 | 5290.74 | EA | 21162.96
264 | 4 | LOADING of Conductor drums | ELEC | labour | SWR10191 | 202 | EA | 808
265 | 4 | UNLOADING of Conductor drums | ELEC | labour | SWR10509 | 100 | EA | 400
266 | 6 | Supply of earthing pipe with materials-Supply of CI eath pipe with 50mm dia,2.0 M Length | ELEC | supply | SMR11484 | 2441 | EA | 14646
267 | 6 | Providing of Earthing-Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | ELEC | labour | SWR10357 | 1234.2 | EA | 7405.2
268 | 6 | Providing of RCC collar to earth pit-Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINES-Providing of RCC collar | ELEC | labour | SWR10359 | 386 | EA | 2316
269 | 6 | Assembly and erection of Structure as per specification which includes fixing of top channels and cross bracings, transport of all materials from road side to the location, earthing, back filling with earth ramming etc excluding pit excavation and concreting.-11KV DP Structure with 9.1 Mtrs PSCC Poles | ELEC | labour | SWR21130 | 3363.96 | SET | 20183.76
270 | 6 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | ELEC | labour | SWR10393 | 3200 | EA | 19200
271 | 6 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | ELEC | labour | SWR10881 | 142 | EA | 852
272 | 50 | Supply of earthing pipe with materials-Supply of GI wire No 8 | ELEC | supply | SMR11486 | 105 | KG | 5250
273 | 675 | Loading of 11KV Polymer Pin Insulators with GI pins | ELEC | labour | SWR11248 | 1 | EA | 675
274 | 675 | Un loading of 11KV Polymer Pin Insulators with GI pins | ELEC | labour | SWR11249 | 1 | EA | 675
275 | 240 | Loading of 11KV Polymer Pin Insulators with GI pins | ELEC | labour | SWR11248 | 1 | EA | 240
276 | 240 | Un loading of 11KV Polymer Pin Insulators with GI pins | ELEC | labour | SWR11249 | 1 | EA | 240
277 | 6 | Loading of 11 KV Metal parts | ELEC | labour | SWR12402 | 48 | BAG | 288
278 | 6 | Un loading of 11 KV Metal parts | ELEC | labour | SWR12421 | 48 | BAG | 288
279 | 960 | Laying of 2nd cable in excavated trench | ELEC | labour | SWR10988 | 204.1 | M | 195936
280 | 72 | Cost of Pipes and slabs-Supply of 6" B class GI pipe | ELEC | supply | SMR40081 | 1044 | M | 75168
281 | 200 | Cost of Pipes and slabs-Supply of 250 mm Hume pipe of class NP3 with compresive strength of 35N/mm2 for 28 days curing,barewall thickness of 30mm,1.25kG linear/meter and withstanding capability of 22.50KN/linear meter as per IS 458-1993. | ELEC | supply | SMR40077 | 363 | M | 72600
282 | 6 | Cost of Pipes and slabs-Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters , CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | ELEC | supply | SMR40085 | 484 | EA | 2904
283 | 5 | Load-11/33KV XLPE UG Cable for all sizes | ELEC | labour | SWR11230 | 1024 | DR | 5120
284 | 5 | Unload-11/33KV XLPE UG Cable for all sizes | ELEC | labour | SWR11231 | 1024 | DR | 5120
285 | 1.1 | Fabrication & erection of Channels -Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to theRS-Joist poles excluding cost of Mild Steel and transportcharges to substation site, including erection. Fabrication of struc.with welding. | ELEC | labour | SWR10869 | 3426 | TO | 3768.6
286 | 50 | Supply of Danger boards with clamps | ELEC | supply | SMR40070 | 116 | EA | 5800
287 | 6 | S&E-Smart RFID marker | ELEC | labour | SWR25089 | 2745 | EA | 16470
288 | 960 | Excavation & laying of UG Cable (Double Run)-Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts,-In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil/CC-11 KV 3x300 Sqmm Cable | ELEC | labour | SWR11973 | 631.06 | M | 605817.6
289 | 240 | Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-11 KV 3x300 Sqmm Cable | ELEC | labour | SWR12005 | 275.4 | M | 66096
290 | 6 | UG Cables Joints Making of Straight through joints-11 KV 3x300 Sqmm Cable | ELEC | labour. | SWR10386 | 3725.45 | EA | 22352.7
291 | 24 | Making of Outdoor/Indoor End Termination-Making 11 KV 3x300 Sqmm Cable Out Door/Indoor end termination | ELEC | labour. | SWR10391 | 2370.63 | EA | 56895.12
292 | 225 | Supply of PSCC Pole 9.1Mtr 280KG | ELEC | supply | SMR25233 | 3109.41 | EA | 699617.25
293 | 80 | Supply of PSCC Pole 8Mtr 140KG | ELEC | supply | SMR25232 | 1580 | EA | 126400
294 | 185 | supply of V X-Arm with MS Angle 65x65x6 | ELEC | supply | SMR25218 | 743 | EA | 137455
295 | 185 | S-Supply of 11KV Top Cleat for 9.1M(Vertical) | ELEC | Supply | SMR25226 | 256 | EA | 47360
296 | 80 | Supply of 11KV Horizontal Cross Arm | ELEC | supply | SMR25223 | 528 | EA | 42240
297 | 6 | Supply of Materials -- Supply of 11 kV 400 A Double break AB switch | ELEC | supply | SMR12317 | 18150 | EA | 108900
298 | 200 | Supply of Materials -- Supply of MS Flat 50x6 mm | ELEC | supply | SMR12322 | 56.5 | KG | 11300
299 | 400 | Supply of MS Angle 50x50x6 | ELEC | supply | SMR25206 | 58.15 | KG | 23260
300 | 500 | Supply of MS Channel 75x40 mm | ELEC | supply | SMR25205 | 58.45 | KG | 29225
301 | 24 | Supply of 11KV 3x300 Heat Shble O/d End Term Kit | ELEC | supply | SMR25208 | 1372.88 | EA | 32949.12
302 | 6 | Supply of 11KV 3x300 Heat Shble stright through joint Kit | ELEC | supply | SMR25210 | 4110.17 | EA | 24661.02
Electrical Total | [7 empty] | 22655512.859
Civil Labour - WBS. No. S-1790-13-07-01-01-001
Sl.No. | Estimate Quantity (only Figures) | Item Detailed Specification Description | Work Type eg. Earth Work, Electrical works. etc (upto 200 Characters) | Item Short Description (upto 100 Characters) | APSS / Morth Cl. Number (upto 200 Characters) | Rate (INR) (Upto 2 Decimals ) | UOM (upto 50 Characters) | Amount
1 | 32 | Leveliing the site by cutting and levelling with the help of JCB including cost,conveyance of all materials,hire chareges etc complete for finished item of work as directed by Engineer-in-charge. | Civil | Labour | SWR34179 | 2165 | Hrs | 69280
2 | 135.61 | Earth work excavation in all type of ordinary soils red earth, Hard gravelly soils, earth mixed with sand and sandy soils etc., in all conditions such as slushy and dry with initial leads and lifts for foundations. | Civil | Labour | SWR33015 | 486 | m3 | 65906.46
3 | 32.45 | Plain Cement concrete PCC (1:4:8) using 40mm HBG metal for foundations and leveling course, including cost and conveyance of all materials, labour all leads and lifts, consolidation and all operations, formwork as required, curing, etc. complete for finished item w | Civil | Labour | SWR33028 | 4771 | m3 | 154818.95
4 | 117.88 | Coursed Rubble stone (CRS) masonry 2nd sort with hard granite stones in cement mortar (1:6) for basement, including cost and conveyance of all materials, labour charges, curing, all leads and lifts, etc, complete for finished item of work. | Civil | Labour | SWR33041 | 4892 | m3 | 576668.96
5 |  | 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge
6 | 3.564 | RCC M20 Grade footing 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33098 | 9523 | m3 | 33939.972
7 | 2.28 | RCC M20 Grade Coloumn . 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33100 | 13272 | m3 | 30260.16
8 | 2.25 | RCC M20 Grade Plinth beams 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33099 | 12394 | m3 | 27886.5
9 | 3.17 | D) RCC M20 Grade Roof Beams landing beam 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33121 | 12310 | m3 | 39022.7
10 | 0.58 | e)RCC M20 Grade Lintels 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33107 | 13101 | m3 | 7598.58
11 | 2.7 | f) RCC M20 Grade Sunshades 600mm wide and 75mm thick'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33114 | 1378 | m2 | 3720.6
12 | 15.224 | g) RCC M20 Grade Roof Slab for Control Room 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33128 | 10898 | m3 | 165911.152
13 | 3 | Reinforcement steelSupplying, Cutting, bending, binding, placing in position and tying reinforcement steel in all heights including cost and conveyance of steel and binding wire etc,. With all leads and lifts, labour charges, etc., complete for finished item of work. | Civil | Labour | SWR33144 | 70687 | Ton | 212061
14 | 38.36 | Brick masonry in cement mortar CM (1:6) for superstructure using well burnt country made second class bricks of approved quality including cost and conveyance of all materials curing, scaffolding with all leads and lifts in all heights etc., complete for fin | Civil | Labour | SWR33068 | 8285 | m3 | 317812.6
15 | 2.7 | Plain Cement concrete PCC (1:2:4) using 20mm size well graded HBG metal for foundations, including cost, conveyance of all materials,labour all leads and lifts,consolidation and all operations, formwork as required, curing,etc. complete for finished item of work | Civil | Labour | SWR33030 | 6140 | m3 | 16578
16 | 606.06 | Plastering with CM 2 coats, 20 mm thick, base coat in CM (1:6), 16 mm thick and top coat in CM (1:4), 4mm thick with Dubara sponze finishing including cost of all materials, seigniorage charges, excluding conveyance charges of materials and including all operational, incidental and labour charges for mixing mortar, laying rendering smooth and thread lining, curing, rounding off junctions of wall and slab etc., complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33163 | 564 | m2 | 341817.84
17 | 349.515 | Painting with two coats of Plastic Emulsn paint over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33356 | 210 | m2 | 73398.15
18 | 200.85 | Painting with two coats of Surya Cem paint over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33329 | 85 | m2 | 17072.25
19 | 3 | Supply and Fixng of MS Name Board including cost & conveyance of all materials,labour charges etc complete for finished item of work. | Civil | Labour | SWR33421 | 4326 | m2 | 12978
20 | 1 | Geophysical Investgation charges for water point by Geologist | Civil | Labour | SWR33608 | 5000 | EA | 5000
21 |  | Drilling of 165mm bore well with machine rig including deployment and hire charges of rig and other machinery and equipment labour charges , measuring the yeild of borewell including cost and conveyance etc complete
22 | 90 | Drill-165mm Bore Well 0 to 90 | Civil | Labour | SWR33609 | 336 | M | 30240
23 | 30 | Drill-165mm Bore Well 90M to 120M | Civil | Labour | SWR34830 | 369 | M | 11070
24 | 30 | Drill-165mm Bore Well 120M to 150M | Civil | Labour | SWR34831 | 394 | M | 11820
25 | 30 | Drill-165mm Bore Well 150M to 180M | Civil | Labour | SWR34832 | 492 | M | 14760
26 | 30 | Drill-165mm Bore Well 180M to 210M | Civil | Labour | SWR34833 | 623 | M | 18690
27 | 30 | Drill-165mm Bore Well 210M to 240M | Civil | Labour | SWR34834 | 754 | M | 22620
28 | 30 | Drill-165mm Bore Well 240M to 270M | Civil | Labour | SWR34835 | 918 | M | 27540
29 | 85 | Drill-165mm Bore Well 270M and above | Civil | Labour | SWR34836 | 1082 | M | 91970
30 | 40 | Supply and fixing of 160mm dia PVC casing of A class 6Kg point pressure including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR33611 | 883 | M | 35320
31 | 1 | Supply and erecting, ISI mark submersible 5.0 HP, 3 Phase 30 stages pumpset suitable for 106/156mm dia borewell including cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33640 | 48007 | EA | 48007
32 | 295 | Supply and fixing of HDPE pipe 40mm dia of 16Kg/cm2 including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR34410 | 180 | M | 53100
33 | 1 | Supply and erecting D.O.L Starter 415V , 3phase,50Hz with SS enclouserincluding cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33645 | 7854 | EA | 7854
34 | 305 | Supply of 3 Core 2.5 Sqmm Flat Copper cable of ISI for Submersible Motors of makes Finolex / Polycab / Gold Medal / Million / Payal / Sun Light / Power Flex / Fortune Art | Civil | Labour | SWR33641 | 192 | m | 58560
35 | 71 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-28.60mm OD Pipe - SDR 11 | Civil | Labour | SWR34363 | 410 | m | 29110
36 | 35 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type - 25mm NB Size | Civil | Labour | SWR34346 | 466 | EA | 16310
37 | 839.38 | Supplying and filling the substation site with borrowed gravel, watering, ramming, thoroughly complying with the standard specification. | Civil | Labour | SWR33052 | 309 | m3 | 259368.42
38 | 16.56 | Providing Design R.C.M. drop wall of 25mm thickness with cm 1:3 and 6mm dia MS bars at 150mm both ways and chicken mesh in two coats 20mm thick each plastering including cost and conveyance of all materials with leads and lifts, scaffolding and curing, labo | Civil | Labour | SWR33203 | 3109 | m2 | 51485.04
39 | 12.24 | Supply and fixing of Ms ornamental safety grill of approved design including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33310 | 2990 | m2 | 36597.6
40 | 5.91 | Supply and fixing of doors with the MT Wood frames of the door shall be made well seasoned mt wood of cross section 100x75mm. The shutter shall be made isi mark flushed door with decolam sheets pasted on both sides with PVC beading 40mm width all round.Frame shall be painted with two coats of synthetic enamel paint of approved color over one coat of primer over luppum with spary with 3 no 150mm brass hinges 1 no brass door stoper, 1 no 250mm brass aldrops. 2 no 300 mm aluminium tower bolts, 2 no 150mm brass fancy door handlers, 1 no keyless lockset with cp handel. The quoted rate shall include cost and conveyance of the meterials, fixig, labour carges, tools, handles,locking arrangementts and other fixtures & fittings for finished item work as directed by the Engineer - in- charge. | Civil | Labour | SWR33264 | 7314 | m2 | 43225.74
41 | 128.25 | Raised pointing to the exposed surfaces of CRS masonry in cm 1:3 prop. including cost and conveyance of all materials, labour charges, all leads and lifts curing etc, complete for finished item of work. | Civil | Labour | SWR33184 | 125 | m2 | 16031.25
42 | 8.64 | Supplying and fixing Aluminium sliding windows with grill and fixed glass panels using anodised aluminium extruded sections of mat finish for frames and mullions made from approved aluminium sections 62x32x1.2mm at 0.73kg/Rm providing 5mm plain glass fix | Civil | Labour | SWR33277 | 3623 | m2 | 31302.72
43 | 16.56 | Supply and laying of Ceramic floor over of CM 1:3 20 mm thick including required materials and labour charges etc complete for item of work | Civil | Labour | SWR33224 | 914 | m2 | 15135.84
44 | 121.92 | Flooring with double machine polished and hand cut Tandur blue stone 20mm thick of approved colour, quality and of minimum of 300x300mm size over a bed of cement mortar 1:3 20mm thick including cost of all materials, with all leads and lifts jointing and | Civil | Labour | SWR33219 | 788 | m2 | 96072.96
45 | 6.74 | Supply and fixing of 4" high skirting of shabad stone to the walls including cost and conveyance of all materials, labour etc for finished item of work. | Civil | Labour | SWR33236 | 877 | m2 | 5910.98
46 | 243.69 | Painting with two coats of OBD over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials labour charges etc., complete for finished item of work. | Civil | Labour | SWR33333 | 146 | m2 | 35578.74
47 | 101.17 | Providing impervious coat over RCC roof slab to requried slopes with 20mm thick in CM 1:3 mixed with approved brand of water proffing compound inclding cost and conveyance of all materials, labour charges, curing, rounding off junctions of wall and slab, all leads and lifts, etc . complete for finished item of work as directed by the Engineer - in - charge. | Civil | Labour | SWR33156 | 586 | m2 | 59285.62
48 | 60 | Supply & fixing of 25mm dia 2mm thick suSupply & fixing of 25mm dia 2mm thick surface P.V.C. pipe (ISI MARK) Concealed in wall with all required accessories including masonary work and labour charges etc.complete. | Civil | Labour | SWR33441 | 108 | m | 6480
49 | 1 | Supply & fixing TPN Distribution board w Supply & fixing TPN Distribution board with IP-42 protection (Metal Door)suitable for 3 phase ELCB/RCCB/FP Isolator as incomer and 10kA SP MCBs as out going including internal connection and labour charges for surface / flush mounting etc Complete. | Civil | Labour | SWR33526 | 11353 | EA | 11353
50 | 10 | Supply & fixing of 6A 3 pin wall plug socket with 6A switch control on a common switch board with earth continuity including wire leads,earth connection along with all labour charges etc., complete | Civil | Labour | SWR33468 | 166 | EA | 1660
51 | 6 | Supply & fixing of 16A 3 pin and 6A 3pin plug Flush type socket with indicator lamp and 16Amps fuse unit and 16Amps switch control (5 in one )duly recessed in wall with wooden deep box of 6'' x 8'' x 2 1/2'' size covered with hylam sheet earth connection and all labour charges etc., complete on wall. | Civil | Labour | SWR33470 | 449 | EA | 2694
52 | 24 | Supply and Fixing of modular switch, LP,FP,EFP Wiring with 2 runs of 14/0.3mm (1.0 sq.mm)Fire Retardant (FR) P.V.C. insulated flexible copper cable (ISI MARK) in existing pipe with 6A Flush type Switch,ceiling rose and 3mm thick hylam sheet covering to switch control box including all labour charges etc., complete for light points, bell , fan and exhaust fan points in Non-Residential Buildings. | Civil | Labour | SWR33457 | 676 | EA | 16224
53 | 12 | Supply & Fixing of 28W T5 fluorescent tube. | Civil | Labour | SWR33558 | 148 | EA | 1776
54 | 1 | Supply of 12" (300mm)ISI, 900 RPM Heavy duty exhaust fan with metallic blades with Mark of makes Crompton / Bajaj / Havells / Orient. | Civil | Labour | SWR33571 | 2192 | EA | 2192
55 | 180 | Supply and run of 2 of 22/0.3mm (1.5 sq.mm) (FR) P.V.C. insulated flexible copper cable in existing pipe for mains including all labour charges complete. | Civil | Labour | SWR33496 | 75 | m | 13500
56 | 180 | Supply and run of 2 of 36/0.3mm (2.5 sq.mm) FR P.V.C. insulated flexible copper cable in existing pipe for mains including all labour charges complete. | Civil | Labour | SWR33497 | 103 | m | 18540
57 | 12 | Supply & fixing of batten holder /slanting holder in lieu of ceiling rose of light point complete with all connection and all labour charges with 40W bulb (for new installation). | Civil | Labour | SWR33484 | 141 | EA | 1692
58 | 4 | Supply & fixing of 1200mm (48'') sweep 230v,A.C 50 Hz.Ceiling fan with 3 Blades and double ball bearings with all standared accessories. | Civil | Labour | SWR33563 | 2277 | EA | 9108
59 | 4 | Supply & fixing of Electronic Regulator for ceiling fans 900/1200/1400mm sweep including cost of material, Electrical charges complete for finished item of work | Civil | Labour | SWR33564 | 589 | EA | 2356
60 | 1 | Providing independent EARTHING by excavating a trench to a depth of 2.1M in all solid,as per size specified in the Data,using 40mm dia 'B' class GI pipe of 2.5 Mtrs length with necessary accessories with hume pipe ring duly providing staggered holes including filling with equal proportion of salt and Charcoal in layers and all labour charges etc., compiete for small quarters. | Civil | Labour | SWR33596 | 5345 | EA | 5345
61 | 35 | Supplying, laying, jointing and testing 101.6 mm SWG SP-1 pipes of ISI make conforming to ISI 651 & 4127 with airtight cement joints in CM 1.5:1 prop. Including excavation of trenches and socket pits in any soil (except rock requiring blasting) up to 1524 mm(5'0") depth and refilling with watering and tamping. | Civil | Labour | SWR34281 | 755 | m | 26425
62 | 3 | Constructing 904.0 mm (3#0#) dia brick masonry inspection chamber as per IS - 4111: Part-1:1986 with cement mortar (1:6) prop using 2nd Class Clay Bricks of 225 mm thick from approved source having a minimum crushing strength of 5 N/sq.mm including plastering with cement mortar 1:3 prop; ½# thick both inside and outside fitted with 20# dia RCC manhole covers and frames including excavating pits up to a depth of 904 mm (3'-0") in all sorts of soils (excluding rock) and laying cement concrete (1:4:8) 150 mm thick using 40 mm HBG Metal and P.C.C. 1:2:4 benching and channel 100 mm thick as per Standard specification and including cost and conveyance of all materials like cement, sand, bricks, water etc., to site, cost of seigniorage charges on all materials and all incidental and operational, labour charges like mixing cement mortar, constructing masonry, lift charges, curing etc., complete for finished item of work as per Standard specification. | Civil | Labour | SWR34296 | 8766 | EA | 26298
63 | 4 | Supply & fixing of 110 mm dia - Door Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34381 | 128 | EA | 512
64 | 4 | Supply & fixing of 110 mm dia - Plain Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34380 | 100 | EA | 400
65 | 12 | Supply & fixing of 110 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand | Civil | Labour | SWR34377 | 462 | m | 5544
66 | 18 | Supply & fixing of 90 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand | Civil | Labour | SWR34378 | 410 | m | 7380
67 | 3 | Supplying & fixing 150 mm x 100 mm SWG gully traps conforming to ISI 651 & 4127 with C.I Grating & Cost. Brick masonry in CM 1:6 prop. Intermediate chamber and fitted with 304.8 mm x 288.6mm (12"x9") C.I Frame and hinged cover | Civil | Labour | SWR34286 | 767 | EA | 2301
68 | 1 | Supplying and Fixing of European Water Closet of 1st Quality | Civil | Labour | SWR34312 | 2228 | EA | 2228
69 | 6 | Supply & fixing 15 mm angle stop cock Indian make 400 grams Seiko/ Senior/ Nice/ Senior/ Nice or equivalent | Civil | Labour | SWR34328 | 721 | EA | 4326
70 | 4 | S&F 15 mm N.P bib tap Indian make 400 grams full turn Seiko/ Senior/ Nice or equivalent | Civil | Labour | SWR34329 | 296 | EA | 1184
71 | 1 | Supplying & Fixing Indian make Flat Back Wash Hand Basin (HSW/Parryware/ Neycer) 1st quality conforming to IS:2556-Part-4:1972 with waste fittings like rubber plug, chain, 32 mm nominal size C.P. Fitting with parallel pipe thread conforming to IS:2963-1979 and fitted with 15 mm nominal bore Chromium Plated Pillar Tap of 1st quality Indian make 400 grams Seiko/ Senior/ Nice/ Esso or equivalent complete with standard CI brackets including wooden block: 550 x 400 mm - Single C.P. Pillar cock | Civil | Labour | SWR34316 | 1717 | EA | 1717
72 | 2 | Supply & fixing 38.1 mm C.P waste coupling Half or Full Thread 1st Quality Indian make Parryware or equivalent | Civil | Labour | SWR34428 | 309 | EA | 618
73 | 2 | Supply & fixing of 4" (101.6 mm ) Nahany Trap ( Without Jali with inlet)UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34387 | 134 | EA | 268
74 | 1000 | Providing & Placing on Terrace (at all floor levels) polyethylene water storage tank with Double layer approved brand & manufacture with cover and suitable locking arrangement & making necessary holes for inlet & outlets and over flow pipes but with NECESSARY fittings & base support for tanks | Civil | Labour | SWR34375 | 10 | L | 10000
75 | 2 | Supply & fixing 31.75 mm dia PVC flexible waste pipe of 914.4 mm length of Ist quality | Civil | Labour | SWR34426 | 33 | EA | 66
76 | 45 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)- 15.90mm OD Pipe - SDR 11 | Civil | Labour | SWR34361 | 239 | m | 10755
77 | 200 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-22.20mm OD Pipe - SDR 11 | Civil | Labour | SWR34362 | 313 | m | 62600
78 | 4 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type -20mm NB Size | Civil | Labour | SWR34345 | 331 | EA | 1324
79 | 1 | Supply & fixing 25.4 mm dia & 609.6 mm long aluminium anodized towel rod with brackets and aluminium screws | Civil | Labour | SWR34430 | 489 | EA | 489
80 | 36 | Plain Cement concrete PCC (1:3:6) using 40mm HBG metal for foundations and leveling course, including cost and conveyance of all materials, labour all leads and lifts, consolidation and all operations, formwork as required, curing, etc. complete for finished item w | Civil | Labour | SWR33029 | 5061 | m3 | 182196
81 | 120 | Supply&Fabrication and fixing of Welded wire mesh ( 2" x 2") of 3mm dia. with ISMC (75x40x4.4mm) and Pheriperal frame of ISA(35x35x3mm) incldg cost& conveyance painting with synthetic enamil paint two coats over a coat of red oxide primer etc complete for finished item of work.. | Civil | Labour | SWR33403 | 2310 | m2 | 277200
82 | 1 | Providing Consultancy services for arranging contour surveying with total station incuding preparation of boundary and contour levels with 2 Nos. Hard copies and soft copies complete for finished items of work | Civil | Labour | SWR33427 | 5665 | EA | 5665
83 | 222.2468 | Seigniorage Charges - Sand | Civil | Labour | SWR34470 | 40 | m3 | 8889.873
84 | 725.7496 | Seigniorage Charges - Metal | Civil | Labour | SWR34471 | 97.5 | m3 | 70760.585
85 | 839.38 | Seigniorage Charges - Gravel | Civil | Labour | SWR34472 | 30 | m3 | 25181.4
86 | 60 | Supply and fixing of RCC fencing poles of size 0.1mx0.1mx1.8m (security fencing of sub station), including cost and conveyance of all labour, materials,and hire chareges etc complete for finished item of work. | Civil | Labour | Swr33405 | 1444 | EA | 86640
87 | 1200 | Supply and fixing of galvanised barded wire (1 horizantal & 2 cross strands. including cost and conveyance of all labour, materials,and hire chareges etc complete for finished item of work. | Civil | Labour | Swr33408 | 16 | m | 19200
Total Rs. | [7 empty] | 4231785.642
Total Elec+Civil |  |  | 18% GST Rs. |  |  |  |  | 26887298.501

## 7. Huda Colony
Name of the work: Erection of 33/11 kV outdoor SS at Huda Colony in Shamshabad (M) with 2x8 MVA PTRS and connected 33kV, 11kV Lines at Shamshabad Town in Shamshabad (M) in ECGH DIVISION/Master Plan/RR Circle
WBS No. S-1791-13-03-02-01-001
Sl No | Estimate Quantity | Description of item | Work Type | Item Short Description | APSS / Month Cl.NumberSSR 11 & 12 | Rate (INR) | UOM | AMOUNT
1 | 16 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | ELEC | Labour | SWR11039 | 928 | EA | 14848
2 | 5.76 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ELEC | Labour | SWR10868 | 6852 | TO | 39467.52
3 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELEC | supply | SMR40009 | 2181 | TO | 12562.56
4 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELEC | labour | SWR10877 | 851 | TO | 4901.76
5 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELEC | supply | SMR40010 | 1293 | TO | 7447.68
6 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELEC | labour | SWR10879 | 482 | TO | 2776.32
7 | 5.76 | Fabrication & erection of Channels-Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ELEC | labour | SWR10867 | 1470 | TO | 8467.2
8 | 16 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-R.S. Joists 150 x 150 mm | ELEC | labour | SWR10348 | 1952.61 | EA | 31241.76
9 | 17.758 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 116829.882
10 | 9.24 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ELEC | labour | SWR10862 | 373 | M2 | 3446.52
11 | 16 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | ELEC | labour | SWR11089 | 48 | EA | 768
12 | 4 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-8.0Mtrs PSCC Poles 0.76 M x 0.76M x 1.52M (2.6" x 2.6" x 5.0') 0.88 cum | ELEC | labour | SWR11037 | 793 | EA | 3172
13 | 1 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ELEC | Labour | SWR10868 | 6852 | TO | 6852
14 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELEC | supply | SMR40009 | 2181 | TO | 2181
15 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELEC | labour | SWR10877 | 851 | TO | 851
16 | 1 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELEC | supply | SMR40010 | 1293 | TO | 1293
17 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELEC | labour | SWR10879 | 482 | TO | 482
18 | 1 | Fabrication & erection of Channels-Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ELEC | labour | SWR10867 | 1470 | TO | 1470
19 | 4 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Box pole 12 Mtr | ELEC | labour | SWR11267 | 3901.37 | EA | 15605.48
20 | 2.65 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 17434.35
21 | 2.31 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ELEC | labour | SWR10862 | 373 | M2 | 861.63
22 | 4 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | ELEC | labour | SWR11089 | 48 | EA | 192
23 | 5.063 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ELEC | labour | SWR10868 | 6852 | TO | 34691.676
24 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELEC | supply | SMR40009 | 2181 | TO | 11042.403
25 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELEC | labour | SWR10877 | 851 | TO | 4308.613
26 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELEC | labour | SMR40010 | 1293 | TO | 6546.459
27 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELEC | labour | SWR10879 | 482 | TO | 2440.366
28 | 5.063 | Fabrication & erection of Channels-Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ELEC | labour | SWR10867 | 1470 | TO | 7442.61
29 | 13 | Erection of AB Switch and aligment complete Erection of 33 KV AB Switch including alignment and earthing | ELEC | labour | SWR10392 | 4500 | EA | 58500
30 | 34 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Note:-The requirement of 2nd coat is to be justified by the concerned Divisional Engineer /Executive Engineer before execution of this work Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | ELEC | labour | SWR10881 | 142 | EA | 4828
31 | 34 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | ELEC | labour | SWR12331 | 146.63 | EA | 4985.42
32 | 6 | Loading of 33 KV CTs/ PTs | ELEC | labour | SWR10200 | 165 | EA | 990
33 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
34 | 6 | Un loading of 33 KV CTs/ PTs | ELEC | labour | SWR10518 | 128 | EA | 768
35 | 2 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33kv single phase PT s | ELEC | labour | SWR10401 | 1079 | SET | 2158
36 | 12 | Loading of 33 KV, 10 KA LAs Station typ | ELEC | labour | SWR10266 | 41 | EA | 492
37 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
38 | 12 | Un loading of 33 KV, 10 KA LAs Station type | ELEC | labour | SWR10584 | 35 | EA | 420
39 | 4 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33 KV LAS station/Line type including earthing | ELEC | labour | SWR10396 | 880 | SET | 3520
40 | 2 | Loading of 33 KV VCBs along with Panel boards | ELEC | labour | SWR10198 | 1024 | EA | 2048
41 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
42 | 2 | Un loading of 33 KV VCBs along with Panel boards | ELEC | labour | SWR10516 | 1044.48 | EA | 2088.96
43 | 12.584 | Excavate-Pit for 33KV VCB | ELEC | labour | SWR23224 | 331 | M3 | 4165.304
44 | 14.52 | Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x 1.8 x 0.75 cum for VCB Plinth | ELEC | labour | SWR20685 | 5160 | M3 | 74923.2
45 | 2 | Erection of 33 KV VCB with Control Panel | ELEC | labour | SWR10460 | 12500 | EA | 25000
46 | 2 | Loading of 8MVA PTR | ELEC | labour | SWR10613 | 5805.84 | EA | 11611.68
47 | 2 | Transport of Power transformers (0 to 100 KM) from one place to another place in GHMC Area.(excluding of loading & unloading )-8MVA power transformer | ELEC | labour | SWR10854 | 21945 | EA | 43890
48 | 2 | Unloading of 8MVA PTR | ELEC | labour | SWR10627 | 5805.84 | EA | 11611.68
49 | 700 | S/o rail poles 90/105lb (250x2N) | ELEC | supply | SMR22718 | 47.27 | KG | 33089
50 | 14 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Rail pole 90 lbs | ELEC | labour | SWR10344 | 3510 | EA | 49140
51 | 2 | Erection of PTR on constructed plinth-Erection of 8 MVA PTR. | ELEC | labour | SWR21321 | 49480.2 | 49480.2 | 98960.4
52 | 0.436 | Extention of 33KV Bay at 132/33KV Sub-station-Supply of Zebra condutor | ELEC | supply | SMR24910 | 299369 | 299369 | 130524.884
53 | 30 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing | ELEC | supply | SMR11915 | 2055 | 2055 | 61650
54 | 30 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of I-Bolts | ELEC | supply | SMR22473 | 294 | 294 | 8820
55 | 45 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 "to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating . Sup T clamp LM6 Al alloy of 12 mm, 800 A | ELEC | labour | SMR40011 | 299 | 299 | 13455
56 | 6 | Bus stringing Hoisting of Insulators and hardware, stretching the conductor and stringing of 33 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bussection of 4.5mt) Hoisting post ins&hrd wr 1panther 33kv | ELEC | labour | SWR21240 | 781 | 781 | 4686
57 | 84 | Stringing of bus with panther conductor including jumpering etc., complete to all the equipment in SS fixing to all clamps and equipment.(3 Conductors) | ELEC | labour | SWR10404 | 327.68 | 327.68 | 27525.12
58 | 30 | Bus stringing Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | ELEC | labour | SWR10884 | 224 | 224 | 6720
59 | 75 | Labour for Fixing of all types of clamps | ELEC | labour | SWR10917 | 65 | 65 | 4875
60 | 25 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | ELEC | labour | SWR11039 | 928 | 928 | 23200
61 | 8.68 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ELEC | labour | SWR10868 | 6852 | 6852 | 59475.36
62 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELEC | supply | SMR40009 | 2181 | 2181 | 18931.08
63 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELEC | labour | SWR10877 | 851 | 851 | 7386.68
64 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELEC | supply | SMR40010 | 1293 | 1293 | 11223.24
65 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELEC | labour | SWR10879 | 482 | 482 | 4183.76
66 | 8.68 | Fabrication & erection of Channels-Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ELEC | labour | SWR10867 | 1470 | 1470 | 12759.6
67 | 25 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-R.S. Joists 150 x 150 mm | ELEC | labour | SWR10348 | 1952.61 | 1952.61 | 48815.25
68 | 27.75 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | 6579 | 182567.25
69 | 17.91 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ELEC | labour | SWR10862 | 373 | 373 | 6680.43
70 | 25 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | ELEC | labour | SWR11089 | 48 | 48 | 1200
71 | 4.642 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ELEC | labour | SWR10868 | 6852 | 6852 | 31806.984
72 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELEC | supply | SMR40009 | 2181 | 2181 | 10124.202
73 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELEC | labour | SWR10877 | 851 | 851 | 3950.342
74 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELEC | supply | SMR40010 | 1293 | 1293 | 6002.106
75 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELEC | labour | SWR10879 | 482 | TO | 2237.444
76 | 4.642 | Fabrication & erection of Channels-Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ELEC | labour | SWR10867 | 1470 | TO | 6823.74
77 | 17 | Erection of AB Switch and aligment complete-Erection of 11KV 800A double throw AB Switches | ELEC | labour | SWR21277 | 3500 | EA | 59500
78 | 3 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | ELEC | labour | SWR10393 | 3200 | EA | 9600
79 | 2 | Loading of 11 KV CT - PT Sets | ELEC | labour | SWR10201 | 190 | EA | 380
80 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
81 | 2 | Un loading of 11 KV CT - PT Sets | ELEC | labour | SWR10519 | 101 | EA | 202
82 | 2 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc-Erection of 11 KV three phase PTs | ELEC | labour | SWR10402 | 800 | SET | 1600
83 | 24 | Loading of 11 KV, 10 KA LAs Station type | ELEC | labour | SWR10264 | 32 | EA | 768
84 | 2 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 6599.4
85 | 24 | Un loading of 11 KV, 10 KA LAs Station type | ELEC | labour | SWR10582 | 32 | EA | 768
86 | 2 | Erection of 11 KV LAS station type including earthing | ELEC | labour | SWR10397 | 559 | SET | 1118
87 | 6 | Erection of 11 KV LAS line type including earthing | ELEC | labour | SWR10398 | 505 | SET | 3030
88 | 8 | Loading of 11 KV VCBs along with Panel boards | ELEC | labour | SWR10199 | 1024 | EA | 8192
89 | 4 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 13198.8
90 | 8 | Un Loading of 11 KV VCBs along with Panel boards | ELEC | labour | SWR10517 | 1044.48 | EA | 8355.84
91 | 41.6 | Excavate-Pit for 33KV VCB | ELEC | labour | SWR23224 | 331 | M3 | 13769.6
92 | 48 | Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x 1.8 x 0.75 cum for VCB Plinth | ELEC | labour | SWR20685 | 5160 | M3 | 247680
93 | 8 | Erection of 11 KV VCB with Control Panel | ELEC | labour | SWR10461 | 12000 | EA | 96000
94 | 12 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing | ELEC | supply | SMR11915 | 2055 | SET | 24660
95 | 12 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of I-Bolts | ELEC | supply | SMR22473 | 294 | EA | 3528
96 | 45 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 "to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating . Sup T clamp LM6 Al alloy of 12 mm, 800 A | ELEC | supply | SMR40011 | 299 | EA | 13455
97 | 2 | Bus Stringing -Hoisting of Insulators and hardware, stretching the conductor and stringing of 11 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 3.5mt) Hoisting post ins&hrd wr 1panther 11kv | ELEC | labour | SWR21241 | 507 | EA | 1014
98 | 63 | Stringing of bus with panther conductor including jumpering etc., complete to all the equipment in SS fixing to all clamps and equipment.(3 Conductors) | ELEC | labour | SWR10404 | 327.68 | M | 20643.84
99 | 45 | Bus stringing Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | ELEC | labour | SWR10884 | 224 | EA | 10080
100 | 57 | Labour for Fixing of all types of clamps | ELEC | labour | SWR10917 | 65 | EA | 3705
101 | 584 | Laying of earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication 75x 8mm MS Flat / GI Flat. Laying of earth mat,excavation 75x 8mm | ELEC | labour | SWR10920 | 65 | RMT | 37960
102 | 1010 | Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) Earthing for raisers of SS Flat 50x6 mm. | ELEC | labour | SWR10919 | 41 | RMT | 41410
103 | 36 | Supply of earthing pipe with materials -Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | ELEC | supply | SMR11482 | 3486 | EA | 125496
104 | 36 | Providing of Earthing-Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | ELEC | labour | SWR10357 | 1234.2 | EA | 44431.2
105 | 36 | Providing of RCC collar to earth pit-Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINES-Providing of RCC collar | ELEC | labour | SWR10359 | 386 | EA | 13896
106 | 2 | Supply of Copper Flexible jumper with 75 X 8 of length 250 mm at neutral of Power tranformer end and 50 X 6 of length 50mm two Nos at double neutral end duly brasing with flexible jumper of capacity of 5kA/3 sec for power transformer neutral. SupCU Flexi jumper for Power T/F Neutral | ELEC | supply | SMR40033 | 4725 | EA | 9450
107 | 2 | Providing of earthing with various types of earth electrodes-Providing of double earthing for neutral with flexible copper jumpers including arrangement by fixing M.S.Channel 100x50mm. | ELEC | labour | SWR11892 | 1323 | EA | 2646
108 | 4 | Loading of LT AB Cable 3X16+25 Sqmm | ELEC | labour | SWR11702 | 200 | DR | 800
109 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
110 | 4 | Un loading of LT AB Cable 3X16+25 Sqmm | ELEC | labour | SWR11713 | 204 | DR | 816
111 | 80 | Providing of control cable trench as per DATA-XII | ELEC | labour | SWR22093 | 3148 | RMT | 251840
112 | 3074 | Control Cable-Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends . Lay-4C/10C 2.5Sqmm Control Cable | ELEC | labour | SWR11879 | 27 | M | 82998
113 | 270 | Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per specification (including cost of ferrules, lugs and glands) | ELEC | labour | SWR12510 | 27 | EA | 7290
114 | 4 | Marshalling Box Supply of FRP PT Marshalling Box | ELEC | supply | SMR40048 | 4463 | EA | 17852
115 | 4 | Marshalling Box Erection of Marshalling boxes | ELEC | labour | SWR10940 | 374.85 | EA | 1499.4
116 | 1 | Loading of 220 V Batterry with charger | ELEC | labour | SWR11166 | 1612 | SET | 1612
117 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
118 | 1 | Un loading of 220 V Batterry with charger | ELEC | labour | SWR11147 | 1024 | SET | 1024
119 | 1 | Batteries-Erection of 220 V, 200 AH battery in complete shape fit for charging . Conventional lead acid | ELEC | labour | SWR12350 | 7666 | EA | 7666
120 | 1 | Control Panels -Supply of DC Annunciation & relay panel for 10 feeder panel including the cost of LED Indiacation lamps, VAA auxilairy relays, Electronic Hooters complete as per specification. | ELEC | supply | SMR40044 | 42500 | EA | 42500
121 | 1 | Control Panels -Supply of AC Supply panel inluding providing of changeover switch, SFU, metering unit, 32 A three phase MCB, 16 A Single phase MCB complete as per specification. Supply of AC Supply panel complete | ELEC | supply | SMR40045 | 42000 | EA | 42000
122 | 2 | Fixing of AC/DC Panel and giving Connections to the protection equipment and Metering circuits as per the specification and standards. The 3 1/2 core 25 Sqmm power cable required from distribution box to AC/DC panel in the control room is also to be supply | ELEC | labour | SWR20025 | 7871.85 | SET | 15743.7
123 | 8 | Yard lightning-Supply of stepped tubular poles single way made of steel of length 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9 mm, 2.1 mtrs with outer dia 76.1 mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79 kgf as per IS 2713 | ELEC | supply | SMR40051 | 13913 | EA | 111304
124 | 8 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE/CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA /OSRAM /SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty S-90W LED fixture set | ELEC | labour | SMR11594 | 8200 | EA | 65600
125 | 8 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | ELEC | labour | SWR11039 | 928 | EA | 7424
126 | 8 | Erection of tubular poles | ELEC | labour | SWR10955 | 1379 | EA | 11032
127 | 5.27 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 34671.33
128 | 8 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE/CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA /OSRAM /SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty. Fixing of Metal halide lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5 GI pipe complete Fixing of LED/Metal halide complete. | ELEC | labour | SWR10956 | 1268 | EA | 10144
129 | 45 | Supply of HBG metal-Supply & spreading of 20mm machine crushed metal (HBG) including cost of conveneyance of all materials, labour charges etc complete for finished item of work and directed by the engineer incharge | ELEC | labour | SWR10860 | 2113 | M3 | 95085
130 | 2 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M Ex of Hard pit w/o blast 0.75X0.9X1.95M | ELEC | labour | SWR11040 | 990.68 | EA | 1981.36
131 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELEC | Supply | SMR40009 | 2181 | TO | 1635.75
132 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELEC | labour | SWR10877 | 851 | TO | 638.25
133 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELEC | Supply | SMR40010 | 1293 | TO | 969.75
134 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELEC | labour | SWR10879 | 482 | TO | 361.5
135 | 1 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Box pole 12 Mtr | ELEC | labour | SWR11267 | 3901.37 | EA | 3901.37
136 | 2.22 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 14605.38
137 | 1.16 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ELEC | labour | SWR10862 | 373 | M2 | 432.68
138 | 2 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | ELEC | labour | SWR11089 | 48 | EA | 96
139 | 1 | Construction of DTR Plinth-RCC Column type DTR Plinth of size 1'X1'X10',topslab 4'x4'x6" & beam size 4'X8'X8" upto 160KVA | ELEC | labour | SWR21843 | 25967.57 | EA | 25967.57
140 | 1 | Loading of 50,63, 75 & 100 KVA DTR | ELEC | labour | SWR10195 | 350 | EA | 350
141 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
142 | 1 | Un loading of 50,63, 75 & 100 KVA DTR | ELEC | labour | SWR10513 | 280 | EA | 280
143 | 1 | Erection of DTR's including loading and Unloading DTR on the Structure/Plinth etc-Erection of 3 Phase DTRs 63,75 & 100 KVA | ELEC | labour | SWR20905 | 1650 | EA | 1650
144 | 1 | Erection of AB Switch and aligment complete Erection of 11KV 200A TT type AB Switch including fixing of cross angles and alignment complete | ELEC | labour | SWR20102 | 1813.49 | EA | 1813.49
145 | 1 | Erect. of 11kv HG Fuseset incl earthing | ELEC | labour | SWR10395 | 740.52 | SET | 740.52
146 | 40 | Excavation & laying of UG Cable in Single Run Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.-In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road-11KV 3x185 Sqmm Cable | ELEC | labour | SWR11920 | 465.46 | M | 18618.4
147 | 20 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-11 KV 3x185 Sqmm Cable | ELEC | labour | SWR11956 | 126.23 | M | 2524.6
148 | 2 | Making of Outdoor/Indoor End Termination Making 11 KV 3x185 Sqmm Cable Out Door/Indoor end termination | ELEC | labour | SWR10390 | 2370.63 | EA | 4741.26
149 | 1 | Erection of LT distribution box including laying of LT cable from distribution box to LT OH line and DTR to distribution box including earthing of distribution box and crimping of lugs connecting of jumpers etc | ELEC | labour | SWR10674 | 1594.67 | EA | 1594.67
150 | 85 | LAYING OF 33KV, 11KV UG CABLE Excavation & laying of UG Cable in Single Run Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road-LT 3 1/2 x 185 Sqmm Cable | ELEC | labour | SWR11923 | 377.63 | M | 32098.55
151 | 15 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-LT 3 1/2 x 185 Sqmm Cable | ELEC | labour | SWR11959 | 85.43 | M | 1281.45
152 | 2 | UG Cables Joints :-Making of Outdoor/Indoor End Termination -Supply & fixing of Oout Door/Indoor end termination LT 3 1/2 x 185 Sqmm Cable | ELEC | labour | SWR10765 | 968.9 | EA | 1937.8
153 | 1 | Supply and fixing of Substation board of size 3'x2.5' indicating the layout of switchyard Sup &fix of board ind Switchyard layout | ELEC | labour | SWR20032 | 1654 | EA | 1654
154 | 1 | Supply and fixing of safety instructions/Substation operation instruction board. Sup& fix safety inst/SS Op. inst board | ELEC | labour | SWR22090 | 2205 | EA | 2205
155 | 750 | Control Panels Supplying & fabrication erection of 6mm Checkerd plates as per the field conditions Supply,fabricati of 6mm Checkerd plates | ELEC | Labour | SWR10873 | 83 | KG | 62250
156 | 1 | T & P Supply of Wall clock standard make | ELEC | Supply | SMR40059 | 578 | EA | 578
157 | 1 | S-10ft Aluminium Ladder | ELEC | Supply | SMR12378 | 1654 | EA | 1654
158 | 1 | Sup Alluminium Ladder for indoor works | ELEC | Supply | SMR40062 | 4410 | EA | 4410
159 | 30 | T & P Painting of Name Plates for any equipmen | ELEC | labour | SWR10963 | 122 | EA | 3660
160 | 1 | T & P Supply of Taparia Tool kit of Size 20”x10”x15” with tier arrangements Tool box with locking arrangement & key containing (1) Double Ended fix Spanner sets, (Ribbed) 6 x 7, 8 x 9, 10 x 11, 12 x 13, 14 x 15, 16 x 17, 18 x19, 20 x 22, 21 x 23, 24 x 27, 25 x28, 30 x 32, (2) Double Ended Ring Spanners sets, 6 x 7 , 8 x 9, 10 x 11, 12 x 13, 14 x 15. 16 x 17 , 18 x 19, 20 x 22 , 21 x 23, 24 x 27, 25 x28, 30 x 32 mm, (3) Adjustable Spanner 305 mm length least maximum opening 35mm chrome, (4) Pipe Wrench Length 350 mm 14”, (5) Soft faced Hammer with suitable handle 2 lb, (6) Hacksaw frame with metal handle heavy duty for 12" hacksaw blade with High Speed blade, (7) Insulated Screw drivers Transparent Green Handle Set Length 6”, 8” & 12”, (8) Star Screw Driver Transparent Green Handle Length 6”, (9) Insulated Wire Cutter, (10) Insulated Cutting Plier Length 8” with cable stripper insulated with thick C. A. sleeve confirming to IS: 4378 - 1990, (11) Long Nose Plier insulated with thick C.A. sleeve generally confirming to IS:3552-1989, (12) Tester type screw driver (special with neon bulb) generally confirm to IS: 5579- 1985 Grade:II handle yellow/ green colour overall length 130 mm, (13) Insulated Crimping Plier of all Taparia make. SupTaparia Tool kit complete as per Spec | ELEC | Supply | SMR40063 | 4925 | SET | 4925
161 | 1 | T & P Sup Rechargeable LED torch light of Standard make | ELEC | Supply | SMR40064 | 1733 | EA | 1733
162 | 1 | T & P-Steel almarah(61/2 X 3ft) Godrej | ELEC | Supply | SMR40061 | 9818 | EA | 9818
163 | 1 | T & P-Table (3x6ft) Godrej | ELEC | Supply | SMR40057 | 6050 | EA | 6050
164 | 4 | T & P-S type chairs (Godrej) | ELEC | Supply | SMR40058 | 924 | EA | 3696
165 | 1 | T & P Sup Angle racks(18x36.6inches) Godrej | ELEC | Supply | SMR40060 | 1733 | EA | 1733
166 | 1 | T & P Supply of Hack saw (12 inches) | ELEC | Supply | SMR40065 | 289 | EA | 289
167 | 4 | Sup Earth Rods (8ft) Screw & clamp type | ELEC | Supply | SMR40066 | 578 | EA | 2312
168 | 2 | Supply of Hand Gloves | ELEC | Supply | SMR40067 | 289 | SET | 578
169 | 12 | SupRubber mats( 6'x3')size fo indoorSS | ELEC | Supply | SMR40068 | 1386 | EA | 16632
170 | 1 | Biometric Time attendence System & Telecom Sup Stand basic cell phone with charger | ELEC | Supply | SMR40069 | 1386 | EA | 1386
171 | 14 | Supply of Danger boards with clamps | ELEC | Supply | SMR40070 | 116 | EA | 1624
172 | 2 | Supply of Materials -Fire bucket stand with 3 buckets (8 -10 ltr capacity) | ELEC | Supply | SMR40088 | 1386 | SET | 2772
173 | 2 | Room fire extinguisher (2 ltrs capacity) for control room | ELEC | Supply | SMR40089 | 4620 | EA | 9240
174 | 4 | Sup TrollyMounted Co2 (6.5Kgs) Cylinders(IS-2878) | ELEC | Supply | SMR40087 | 9240 | EA | 36960
175 | 6 | Supply of Safety Helmet of standard make | ELEC | Supply | SMR40071 | 231 | EA | 1386
176 | 8 | Supply of LC Boards | ELEC | Supply | SMR40072 | 116 | EA | 928
177 | 4 | Supply of Gum Boots(Pairs) | ELEC | Supply | SMR40073 | 693 | EA | 2772
178 | 1 | Supply of 5000v megger | ELEC | Supply | SMR40074 | 13860 | EA | 13860
179 | 1 | Supply of Earth megger (1000v) | ELEC | Supply | SMR40075 | 8085 | EA | 8085
180 | 1 | Supply of Digital clamp meter. | ELEC | Supply | SMR40076 | 2888 | EA | 2888
181 | 1 | Name board of the 33/11kV Sub-Station(As per Standard Specification) Sup 33/11kv S.S Permanent name board | ELEC | Supply | SMR40086 | 10238 | EA | 10238
182 | 800 | Supply of Hot dip galvanized/zinc coated bolts & nuts including spring washers, pack washers and flat washers etc. | ELEC | Supply | SMR12488 | 90 | KG | 72000
183 | 2 | Fabrication of poles-Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | ELEC | labour | SWR10642 | 512.55 | EA | 1025.1
184 | 1 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-RS Joists 150x75/175 x 85 mm | ELEC | labour | SWR10346 | 1934 | EA | 1934
185 | 5760 | S-Supply of RS Joist Grider Pole (150x150mm) | ELEC | Supply | SMR12302 | 59.25 | KG | 341280
186 | 1000 | S-Supply of RS Joist Pole (175x85mm) | ELEC | Supply | SMR12303 | 60.75 | KG | 60750
187 | 5063 | S- Supply of MS Channel 100x50mm | ELEC | Supply | SMR22745 | 57.45 | KGS | 290869.35
188 | 13 | S-Supply of 33KV 800A DB Break AB Switch | ELEC | Supply | SMR12315 | 40658.78 | EA | 528564.14
189 | 8680 | S-Supply of RS Joist Grider Pole (150x150mm) | ELEC | Supply | SMR12302 | 59.25 | KG | 514290
190 | 4642 | S- Supply of MS Channel 100x50mm | ELEC | Supply | SMR22745 | 57.45 | KGS | 266682.9
191 | 17 | S-Supply of 11KV 800A DB Break AB Switch | ELEC | Supply | SMR12316 | 30847.46 | EA | 524406.82
192 | 3 | S-Supply of 11KV 400A DB Break AB Switch | ELEC | Supply | SMR12317 | 18150 | EA | 54450
193 | 3045 | S-Supply of MS Flat 75x8mm | ELEC | Supply | SMR12321 | 56.42 | KG | 171798.9
194 | 2666 | S-Supply of MS Flat 50x6mm | ELEC | Supply | SMR12322 | 56.5 | KG | 150629
195 | 750 | S-Supply of RS Joist Pole (175x85mm) | ELEC | Supply | SMR12303 | 60.75 | KG | 45562.5
196 | 1 | S-Supply of 11KV 200A Tilting Type AB Switch | ELEC | Supply | SMR12318 | 8991 | EA | 8991
197 | 1 | S-Supply of 11KV HG FuseSet for StationTransformer | ELEC | Supply | SMR12324 | 1974 | EA | 1974
198 | 1 | S-Supply of LT Distribution Box (SMC) | ELEC | Supply | SMR25200 | 7797 | EA | 7797
199 | 2 | S-Supply of 11KV 3x185 Heat Shble O/d End Term Kit | ELEC | Supply | SMR25201 | 1182.97 | EA | 2365.94
200 | 40 | S-Supply of LT XLPE Cable 1C 150 sqmm | ELEC | Supply | SMR25203 | 114.83 | M | 4593.2
201 | 100 | Supply of LT XLPE Cable 31/2C185sqmm. | ELEC | supply | SMR25204 | 547 | M | 54700
202 | 9 | survey line&cabl inc peg mark&tree clear | ELEC |  | SWR22092 | 765 | KM | 6885
203 | 9 | Paving out and stringing of conductor by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location-100 Sqmm Single Circuit (3 Conductors) | ELEC | labour | SWR10366 | 13856.7 | KM | 124710.3
204 | 180 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M Ex of Hard pit w/o blast 0.75X0.9X1.95M | ELEC | labour | SWR11040 | 990.68 | EA | 178322.4
205 | 180 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Errection of 11 M long PSCC pole | ELEC | labour | SWR10978 | 4336.85 | EA | 780633
206 | 62.88 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 413687.52
207 | 180 | Painting of poles-Numbering of poles incl. cost of paint | ELEC | labour | SWR10378 | 32 | EA | 5760
208 | 50 | Excavation of pits in all soils except hard rock requiring blasting-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") 1.05 cum | ELEC | labour | SWR10107 | 700 | EA | 35000
209 | 50 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Erec of 9.1 Mts PSCC poles for stuts | ELEC | labour | SWR11083 | 2400 | EA | 120000
210 | 26.25 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 172698.75
211 | 30 | Formation of Cut points - Formation of Cut point for 11 KV Single Circuit line excluding pole erection and stays Formatn of Horiz Cut point for 11KV line | ELEC | labour | SWR10653 | 1435.81 | EA | 43074.3
212 | 300 | Supply of earthing pipe with materials S-GI Bolts & Nuts,Washers etc., | ELEC | supply | SMR11488 | 117.5 | KG | 35250
213 | 7 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 50 Km and upto 80 Km with Lorry for each trip | ELEC | labour | SWR11864 | 5290.74 | EA | 37035.18
214 | 9 | LOADING of Conductor drums | ELEC | labour | SWR10191 | 202 | EA | 1818
215 | 9 | UNLOADING of Conductor drums | ELEC | labour | SWR10509 | 100 | EA | 900
216 | 60 | Loading of 33 KV Pin insulators | ELEC | labour | SWR10211 | 3 | CRT | 180
217 | 60 | Un loading of 33 KV Pin insulators | ELEC | labour | SWR10529 | 3 | CRT | 180
218 | 30 | Loading of 33 KV Metal parts | ELEC | labour | SWR10618 | 65 | BAG | 1950
219 | 30 | Un loading of 33 KV Metal parts | ELEC | labour | SWR10632 | 65 | BAG | 1950
220 | 210 | Excavation & laying of UG Cable (Double Run) Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, Along the CC / BT multi layer road requiring compressor-33 KV 3x400 Sqmm Cable | ELEC | labour | SWR11980 | 1388.84 | M | 291656.4
221 | 210 | Laying of 2nd cable in excavated trench | ELEC | labour | SWR10988 | 204.1 | M | 42861
222 | 40 | Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-33 KV 3x400 Sqmm Cable | ELEC | labour | SWR12004 | 323.85 | M | 12954
223 | 12 | Cost of Pipes and slabs-Supply of 6" B class GI pipe | ELEC | supply | SMR40081 | 1044 | M | 12528
224 | 30 | Cost of Pipes and slabs-Supply of 250 mm Hume pipe of class NP3 with compresive strength of 35N/mm2 for 28 days curing,barewall thickness of 30mm,1.25kG linear/meter and withstanding capability of 22.50KN/linear meter as per IS 458-1993. | ELEC | supply | SMR40077 | 363 | M | 10890
225 | 2 | Cost of Pipes and slabs-Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters , CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | ELEC | supply | SMR40085 | 484 | EA | 968
226 | 2 | Load-11/33KV XLPE UG Cable for all sizes | ELEC | labour | SWR11230 | 1024 | DR | 2048
227 | 2 | Unload-11/33KV XLPE UG Cable for all sizes | ELEC | labour | SWR11231 | 1024 | DR | 2048
228 | 8 | Making of Outdoor/Indoor End Making 33 KV 3x400 Sqmm Cable Out Door/Indoor end termination TerminationOD/Idoor end termination 33kv 3x400 xlpe | ELEC | labour | SWR10387 | 2764.76 | EA | 22118.08
229 | 2 | UG Cables Joints 33 KV 3x400 Sqmm Cable Straight through joint 33kv 3x400 xlpe | ELEC | labour | SWR10382 | 5700.78 | EA | 11401.56
230 | 2 | Fabrication & erection of Channels -Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to theRS-Joist poles excluding cost of Mild Steel and transportcharges to substation site, including erection. Fabrication of struc.with welding. | ELEC | labour | SWR10869 | 3426 | TO | 6852
231 | 50 | Supply of earthing pipe with materials-Supply of GI wire No 8 | ELEC | supply | SMR11486 | 105 | KG | 5250
232 | 2 | Supply of earthing pipe with materials-Supply of CI eath pipe with 80mm dia,2.0 M Length | ELEC | labour | SMR11483 | 2789 | EA | 5578
233 | 2 | Providing of Earthing-Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | ELEC | labour | SWR10357 | 1234.2 | EA | 2468.4
234 | 2 | Providing of RCC collar to earth pit-Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINES-Providing of RCC collar | ELEC | labour | SWR10359 | 386 | EA | 772
235 | 40 | Supply of earthing pipe with materials-Supply of GI Flat 25X3 mm | ELEC | supply | SMR11485 | 105 | KG | 4200
236 | 20 | Supply of Danger boards with clamps | ELEC | supply | SMR40070 | 116 | EA | 2320
237 | 3 | Supply of M+3 Tower (Galvanized) | ELEC | supply | SMR11683 | 140674.3 | EA | 422022.9
238 | 14.256 | Earth work excavation of pits in hard rock requiring blasting.(wherever feasible/ required) | ELEC | labour | SWR20769 | 1012.35 | M3 | 14432.0616
239 | 3 | Supply of material for Extension of 3Mtrs for M+3 (Galvanized) S-Mat. for Extn of M+3 Tower by 3M GALV | ELEC | supply | SMR11684 | 28520.64 | EA | 85561.92
240 | 3 | Erection of M+3 Tower GALV | ELEC | labour | SWR11850 | 64576 | EA | 193728
241 | 3 | Erection of Extension of 3Mtrs for M+3 (Galvanized) | ELEC | labour | SWR11851 | 5168.95 | EA | 15506.85
242 | 2 | S&E-Smart RFID marker | ELEC | labour | SWR25089 | 2745 | EA | 5490
243 | 50 | Supply of PSCC Pole 9.1Mtr 280KG | ELEC | supply | SMR25233 | 3109.41 | EA | 155470.5
244 | 1200 | Supply of Materials -- Supply of MS Channel 100X50mm | ELEC | supply | SMR22745 | 57.45 | KGS | 68940
245 | 600 | Supply of MS Angle 65x65x6 | ELEC | supply | SMR25207 | 57.25 | KG | 34350
246 | 200 | Supply of Materials -- Supply of MS Flat 75x8 mm | ELEC | supply | SMR12321 | 56.42 | KG | 11284
247 | 8 | UG Cables Joints : Making of Outdoor/Indoor End Termination -- Supply 33KV 3x400Sqmm Outdoor | ELEC | supply | SMR22222 | 4554 | EA | 36432
248 | 2 | UG Cables Joints : Making of Straight through joints -- Supply of 33KV 3x400SQmm Straight Through Joint Kit | ELEC | supply | SMR22223 | 24151 | EA | 48302
249 | 180 | Supply of PSCC Spun Pole 11Mtr | ELEC | supply | SMR25234 | 6540 | EA | 1177200
250 | 150 | Supply of 33KV V-Cross Arm without Clamps | ELEC | supply | SMR25229 | 1678 | EA | 251700
251 | 9 | survey line&cabl inc peg mark&tree clear | ELEC | labour | SWR22092 | 765 | KM | 6885
252 | 9 | Paving out and stringing of conductor by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location-55 Sqmm Single Circuit (3 Conductors) | ELEC | labour | SWR10365 | 9454.81 | KM | 85093.29
253 | 175 | Excavation of pits in all soils except hard rock requiring blasting-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") 1.05 cum | ELEC | labour | SWR10107 | 700 | EA | 122500
254 | 50 | Excavation of pits in hard rock requiring blasting. (other than SS)-9.1Mtrs PSCC Pole 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | ELEC | labour | SWR10112 | 1770 | EA | 88500
255 | 213 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Erec of 9.1 Mts PSCC poles for stuts | ELEC | labour | SWR11083 | 2400 | EA | 511200
256 | 33.29 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 219014.91
257 | 225 | Painting of poles-Numbering of poles incl. cost of paint | ELEC | labour | SWR10378 | 32 | EA | 7200
258 | 80 | Excavation of pits in all soils except hard rock requiring blasting-Stud Poles 0.6 M x 0.9 M x 1.5 M | ELEC | labour | SWR10106 | 645 | EA | 51600
259 | 80 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-8.0 m long PSCC poles for Strut | ELEC | labour | SWR21590 | 1500 | EA | 120000
260 | 32.4 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 213159.6
261 | 40 | Formation of Cut points - Formation of Cut point for 11 KV Single Circuit line excluding pole erection and stays Formatn of Horiz Cut point for 11KV line | ELEC | labour | SWR10653 | 1435.81 | EA | 57432.4
262 | 350 | Supply of earthing pipe with materials S-GI Bolts & Nuts,Washers etc., | ELEC | supply | SMR11488 | 117.5 | KG | 41125
263 | 9 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 50 Km and upto 80 Km with Lorry for each trip | ELEC | labour | SWR11864 | 5290.74 | EA | 47616.66
264 | 9 | LOADING of Conductor drums | ELEC | labour | SWR10191 | 202 | EA | 1818
265 | 9 | UNLOADING of Conductor drums | ELEC | labour | SWR10509 | 100 | EA | 900
266 | 6 | Supply of earthing pipe with materials-Supply of CI eath pipe with 50mm dia,2.0 M Length | ELEC | supply | SMR11484 | 2441 | EA | 14646
267 | 6 | Providing of Earthing-Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | ELEC | labour | SWR10357 | 1234.2 | EA | 7405.2
268 | 6 | Providing of RCC collar to earth pit-Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINES-Providing of RCC collar | ELEC | labour | SWR10359 | 386 | EA | 2316
269 | 6 | Assembly and erection of Structure as per specification which includes fixing of top channels and cross bracings, transport of all materials from road side to the location, earthing, back filling with earth ramming etc excluding pit excavation and concreting.-11KV DP Structure with 9.1 Mtrs PSCC Poles | ELEC | labour | SWR21130 | 3363.96 | SET | 20183.76
270 | 6 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | ELEC | labour | SWR10393 | 3200 | EA | 19200
271 | 6 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | ELEC | labour | SWR10881 | 142 | EA | 852
272 | 50 | Supply of earthing pipe with materials-Supply of GI wire No 8 | ELEC | supply | SMR11486 | 105 | KG | 5250
273 | 675 | Loading of 11KV Polymer Pin Insulators with GI pins | ELEC | labour | SWR11248 | 1 | EA | 675
274 | 675 | Un loading of 11KV Polymer Pin Insulators with GI pins | ELEC | labour | SWR11249 | 1 | EA | 675
275 | 240 | Loading of 11KV Polymer Pin Insulators with GI pins | ELEC | labour | SWR11248 | 1 | EA | 240
276 | 240 | Un loading of 11KV Polymer Pin Insulators with GI pins | ELEC | labour | SWR11249 | 1 | EA | 240
277 | 6 | Loading of 11 KV Metal parts | ELEC | labour | SWR12402 | 48 | BAG | 288
278 | 6 | Un loading of 11 KV Metal parts | ELEC | labour | SWR12421 | 48 | BAG | 288
279 | 960 | Laying of 2nd cable in excavated trench | ELEC | labour | SWR10988 | 204.1 | M | 195936
280 | 72 | Cost of Pipes and slabs-Supply of 6" B class GI pipe | ELEC | supply | SMR40081 | 1044 | M | 75168
281 | 200 | Cost of Pipes and slabs-Supply of 250 mm Hume pipe of class NP3 with compresive strength of 35N/mm2 for 28 days curing,barewall thickness of 30mm,1.25kG linear/meter and withstanding capability of 22.50KN/linear meter as per IS 458-1993. | ELEC | supply | SMR40077 | 363 | M | 72600
282 | 10 | Cost of Pipes and slabs-Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters , CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | ELEC | supply | SMR40085 | 484 | EA | 4840
283 | 5 | Load-11/33KV XLPE UG Cable for all sizes | ELEC | labour | SWR11230 | 1024 | DR | 5120
284 | 5 | Unload-11/33KV XLPE UG Cable for all sizes | ELEC | labour | SWR11231 | 1024 | DR | 5120
285 | 1.1 | Fabrication & erection of Channels -Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to theRS-Joist poles excluding cost of Mild Steel and transportcharges to substation site, including erection. Fabrication of struc.with welding. | ELEC | labour | SWR10869 | 3426 | TO | 3768.6
286 | 50 | Supply of Danger boards with clamps | ELEC | supply | SMR40070 | 116 | EA | 5800
287 | 6 | S&E-Smart RFID marker | ELEC | labour | SWR25089 | 2745 | EA | 16470
288 | 960 | Excavation & laying of UG Cable (Double Run)-Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts,-In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil/CC-11 KV 3x300 Sqmm Cable | ELEC | labour | SWR11973 | 631.06 | M | 605817.6
289 | 240 | Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-11 KV 3x300 Sqmm Cable | ELEC | labour | SWR12005 | 275.4 | M | 66096
290 | 6 | UG Cables Joints Making of Straight through joints-11 KV 3x300 Sqmm Cable | ELEC | labour. | SWR10386 | 3725.45 | EA | 22352.7
291 | 24 | Making of Outdoor/Indoor End Termination-Making 11 KV 3x300 Sqmm Cable Out Door/Indoor end termination | ELEC | labour. | SWR10391 | 2370.63 | EA | 56895.12
292 | 225 | Supply of PSCC Pole 9.1Mtr 280KG | ELEC | supply | SMR25233 | 3109.41 | EA | 699617.25
293 | 80 | Supply of PSCC Pole 8Mtr 140KG | ELEC | supply | SMR25232 | 1580 | EA | 126400
294 | 185 | supply of V X-Arm with MS Angle 65x65x6 | ELEC | supply | SMR25218 | 743 | EA | 137455
295 | 185 | S-Supply of 11KV Top Cleat for 9.1M(Vertical) | ELEC | Supply | SMR25226 | 256 | EA | 47360
296 | 80 | Supply of 11KV Horizontal Cross Arm | ELEC | supply | SMR25223 | 528 | EA | 42240
297 | 6 | Supply of Materials -- Supply of 11 kV 400 A Double break AB switch | ELEC | supply | SMR12317 | 18150 | EA | 108900
298 | 200 | Supply of Materials -- Supply of MS Flat 50x6 mm | ELEC | supply | SMR12322 | 56.5 | KG | 11300
299 | 400 | Supply of MS Angle 50x50x6 | ELEC | supply | SMR25206 | 58.15 | KG | 23260
300 | 500 | Supply of MS Channel 75x40 mm | ELEC | supply | SMR25205 | 58.45 | KG | 29225
301 | 24 | Supply of 11KV 3x300 Heat Shble O/d End Term Kit | ELEC | supply | SMR25208 | 1372.88 | EA | 32949.12
302 | 6 | Supply of 11KV 3x300 Heat Shble stright through joint Kit | ELEC | supply | SMR25210 | 4110.17 | EA | 24661.02
Total electrical labour | [7 empty] | 15565796.4666
Civil labour-S-1791-13-07-01-01-001
Sl.No. | Estimate Quantity (only Figures) | Item Detailed Specification Description | Work Type eg. Earth Work, Electrical works. etc (upto 200 Characters) | Item Short Description (upto 100 Characters) | APSS / Morth Cl. Number (upto 200 Characters) | Rate (INR) (Upto 2 Decimals ) | UOM (upto 50 Characters) | Amount
1 | 32 | Leveliing the site by cutting and levelling with the help of JCB including cost,conveyance of all materials,hire chareges etc complete for finished item of work as directed by Engineer-in-charge. | Civil | Labour | SWR34179 | 2165 | Hrs | 69280
2 | 135.61 | Earth work excavation in all type of ordinary soils red earth, Hard gravelly soils, earth mixed with sand and sandy soils etc., in all conditions such as slushy and dry with initial leads and lifts for foundations. | Civil | Labour | SWR33015 | 486 | m3 | 65906.46
3 | 32.45 | Plain Cement concrete PCC (1:4:8) using 40mm HBG metal for foundations and leveling course, including cost and conveyance of all materials, labour all leads and lifts, consolidation and all operations, formwork as required, curing, etc. complete for finished item w | Civil | Labour | SWR33028 | 4688 | m3 | 152125.6
4 | 117.88 | Coursed Rubble stone (CRS) masonry 2nd sort with hard granite stones in cement mortar (1:6) for basement, including cost and conveyance of all materials, labour charges, curing, all leads and lifts, etc, complete for finished item of work. | Civil | Labour | SWR33041 | 4833 | m3 | 569714.04
5 |  | 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge
6 | 3.564 | RCC M20 Grade footing 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33098 | 9439 | m3 | 33640.596
7 | 2.28 | RCC M20 Grade Coloumn . 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33100 | 13188 | m3 | 30068.64
8 | 2.25 | RCC M20 Grade Plinth beams 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33099 | 12310 | m3 | 27697.5
9 | 3.17 | D) RCC M20 Grade Roof Beams landing beam 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33121 | 12226 | m3 | 38756.42
10 | 0.58 | e)RCC M20 Grade Lintels 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33107 | 13018 | m3 | 7550.44
11 | 2.7 | f) RCC M20 Grade Sunshades 600mm wide and 75mm thick'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33114 | 1372 | m2 | 3704.4
12 | 15.224 | g) RCC M20 Grade Roof Slab for Control Room 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33128 | 10814 | m3 | 164632.336
13 | 3 | Reinforcement steelSupplying, Cutting, bending, binding, placing in position and tying reinforcement steel in all heights including cost and conveyance of steel and binding wire etc,. With all leads and lifts, labour charges, etc., complete for finished item of work. | Civil | Labour | SWR33144 | 70687 | Ton | 212061
14 | 38.36 | Brick masonry in cement mortar CM (1:6) for superstructure using well burnt country made second class bricks of approved quality including cost and conveyance of all materials curing, scaffolding with all leads and lifts in all heights etc., complete for fin | Civil | Labour | SWR33068 | 8248 | m3 | 316393.28
15 | 2.7 | Plain Cement concrete PCC (1:2:4) using 20mm size well graded HBG metal for foundations, including cost, conveyance of all materials,labour all leads and lifts,consolidation and all operations, formwork as required, curing,etc. complete for finished item of work | Civil | Labour | SWR33030 | 6057 | m3 | 16353.9
16 | 606.06 | Plastering with CM 2 coats, 20 mm thick, base coat in CM (1:6), 16 mm thick and top coat in CM (1:4), 4mm thick with Dubara sponze finishing including cost of all materials, seigniorage charges, excluding conveyance charges of materials and including all operational, incidental and labour charges for mixing mortar, laying rendering smooth and thread lining, curing, rounding off junctions of wall and slab etc., complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33163 | 560 | m2 | 339393.6
17 | 349.515 | Painting with two coats of Plastic Emulsn paint over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33356 | 210 | m2 | 73398.15
18 | 200.85 | Painting with two coats of Surya Cem paint over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33329 | 85 | m2 | 17072.25
19 | 3 | Supply and Fixng of MS Name Board including cost & conveyance of all materials,labour charges etc complete for finished item of work. | Civil | Labour | SWR33421 | 4326 | m2 | 12978
20 | 1 | Geophysical Investgation charges for water point by Geologist | Civil | Labour | SWR33608 | 5000 | EA | 5000
21 |  | Drilling of 165mm bore well with machine rig including deployment and hire charges of rig and other machinery and equipment labour charges , measuring the yeild of borewell including cost and conveyance etc complete
22 | 90 | Drill-165mm Bore Well 0 to 90 | Civil | Labour | SWR33609 | 336 | M | 30240
23 | 30 | Drill-165mm Bore Well 90M to 120M | Civil | Labour | SWR34830 | 369 | M | 11070
24 | 30 | Drill-165mm Bore Well 120M to 150M | Civil | Labour | SWR34831 | 394 | M | 11820
25 | 30 | Drill-165mm Bore Well 150M to 180M | Civil | Labour | SWR34832 | 492 | M | 14760
26 | 30 | Drill-165mm Bore Well 180M to 210M | Civil | Labour | SWR34833 | 623 | M | 18690
27 | 30 | Drill-165mm Bore Well 210M to 240M | Civil | Labour | SWR34834 | 754 | M | 22620
28 | 30 | Drill-165mm Bore Well 240M to 270M | Civil | Labour | SWR34835 | 918 | M | 27540
29 | 90 | Drill-165mm Bore Well 270M and above | Civil | Labour | SWR34836 | 1082 | M | 97380
30 | 40 | Supply and fixing of 160mm dia PVC casing of A class 6Kg point pressure including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR33611 | 883 | M | 35320
31 | 1 | Supply and erecting, ISI mark submersible 5.0 HP, Single Phase 30 stages pumpset suitable for 106/156mm dia borewell including cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33640 | 48007 | EA | 48007
32 | 322 | Supply and fixing of HDPE pipe 40mm dia of 16Kg/cm2 including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR34410 | 180 | M | 57960
33 | 1 | Supply and erecting D.O.L Starter 415V , Single phase,50Hz with SS enclouserincluding cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33645 | 7854 | EA | 7854
34 | 360 | Supply of 3 Core 2.5 Sqmm Flat Copper cable of ISI for Submersible Motors of makes Finolex / Polycab / Gold Medal / Million / Payal / Sun Light / Power Flex / Fortune Art | Civil | Labour | SWR33641 | 192 | m | 69120
35 | 71 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-28.60mm OD Pipe - SDR 11 | Civil | Labour | SWR34363 | 410 | m | 29110
36 | 35 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type - 25mm NB Size | Civil | Labour | SWR34346 | 466 | EA | 16310
37 | 839.38 | Supplying and filling the substation site with borrowed gravel, watering, ramming, thoroughly complying with the standard specification. | Civil | Labour | SWR33052 | 309 | m3 | 259368.42
38 | 16.56 | Providing Design R.C.M. drop wall of 25mm thickness with cm 1:3 and 6mm dia MS bars at 150mm both ways and chicken mesh in two coats 20mm thick each plastering including cost and conveyance of all materials with leads and lifts, scaffolding and curing, labo | Civil | Labour | SWR33203 | 3044 | m2 | 50408.64
39 | 12.24 | Supply and fixing of Ms ornamental safety grill of approved design including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33310 | 2990 | m2 | 36597.6
40 | 5.91 | Supply and fixing of doors with the MT Wood frames of the door shall be made well seasoned mt wood of cross section 100x75mm. The shutter shall be made isi mark flushed door with decolam sheets pasted on both sides with PVC beading 40mm width all round.Frame shall be painted with two coats of synthetic enamel paint of approved color over one coat of primer over luppum with spary with 3 no 150mm brass hinges 1 no brass door stoper, 1 no 250mm brass aldrops. 2 no 300 mm aluminium tower bolts, 2 no 150mm brass fancy door handlers, 1 no keyless lockset with cp handel. The quoted rate shall include cost and conveyance of the meterials, fixig, labour carges, tools, handles,locking arrangementts and other fixtures & fittings for finished item work as directed by the Engineer - in- charge. | Civil | Labour | SWR33264 | 7314 | m2 | 43225.74
41 | 128.25 | Raised pointing to the exposed surfaces of CRS masonry in cm 1:3 prop. including cost and conveyance of all materials, labour charges, all leads and lifts curing etc, complete for finished item of work. | Civil | Labour | SWR33184 | 124 | m2 | 15903
42 | 8.64 | Supplying and fixing Aluminium sliding windows with grill and fixed glass panels using anodised aluminium extruded sections of mat finish for frames and mullions made from approved aluminium sections 62x32x1.2mm at 0.73kg/Rm providing 5mm plain glass fix | Civil | Labour | SWR33277 | 3623 | m2 | 31302.72
43 | 16.56 | Supply and laying of Ceramic floor over of CM 1:3 20 mm thick including required materials and labour charges etc complete for item of work | Civil | Labour | SWR33224 | 914 | m2 | 15135.84
44 | 121.92 | Flooring with double machine polished and hand cut Tandur blue stone 20mm thick of approved colour, quality and of minimum of 300x300mm size over a bed of cement mortar 1:3 20mm thick including cost of all materials, with all leads and lifts jointing and | Civil | Labour | SWR33219 | 785 | m2 | 95707.2
45 | 6.74 | Supply and fixing of 4" high skirting of shabad stone to the walls including cost and conveyance of all materials, labour etc for finished item of work. | Civil | Labour | SWR33236 | 875 | m2 | 5897.5
46 | 243.69 | Painting with two coats of OBD over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials labour charges etc., complete for finished item of work. | Civil | Labour | SWR33333 | 146 | m2 | 35578.74
47 | 101.17 | Providing impervious coat over RCC roof slab to requried slopes with 20mm thick in CM 1:3 mixed with approved brand of water proffing compound inclding cost and conveyance of all materials, labour charges, curing, rounding off junctions of wall and slab, all leads and lifts, etc . complete for finished item of work as directed by the Engineer - in - charge. | Civil | Labour | SWR33156 | 582 | m2 | 58880.94
48 | 60 | Supply & fixing of 25mm dia 2mm thick suSupply & fixing of 25mm dia 2mm thick surface P.V.C. pipe (ISI MARK) Concealed in wall with all required accessories including masonary work and labour charges etc.complete. | Civil | Labour | SWR33441 | 108 | m | 6480
49 | 1 | Supply & fixing TPN Distribution board w Supply & fixing TPN Distribution board with IP-42 protection (Metal Door)suitable for 3 phase ELCB/RCCB/FP Isolator as incomer and 10kA SP MCBs as out going including internal connection and labour charges for surface / flush mounting etc Complete. | Civil | Labour | SWR33526 | 11353 | EA | 11353
50 | 10 | Supply & fixing of 6A 3 pin wall plug socket with 6A switch control on a common switch board with earth continuity including wire leads,earth connection along with all labour charges etc., complete | Civil | Labour | SWR33468 | 166 | EA | 1660
51 | 6 | Supply & fixing of 16A 3 pin and 6A 3pin plug Flush type socket with indicator lamp and 16Amps fuse unit and 16Amps switch control (5 in one )duly recessed in wall with wooden deep box of 6'' x 8'' x 2 1/2'' size covered with hylam sheet earth connection and all labour charges etc., complete on wall. | Civil | Labour | SWR33470 | 449 | EA | 2694
52 | 24 | Supply and Fixing of modular switch, LP,FP,EFP Wiring with 2 runs of 14/0.3mm (1.0 sq.mm)Fire Retardant (FR) P.V.C. insulated flexible copper cable (ISI MARK) in existing pipe with 6A Flush type Switch,ceiling rose and 3mm thick hylam sheet covering to switch control box including all labour charges etc., complete for light points, bell , fan and exhaust fan points in Non-Residential Buildings. | Civil | Labour | SWR33457 | 676 | EA | 16224
53 | 12 | Supply & Fixing of 28W T5 fluorescent tube. | Civil | Labour | SWR33558 | 148 | EA | 1776
54 | 1 | Supply of 12" (300mm)ISI, 900 RPM Heavy duty exhaust fan with metallic blades with Mark of makes Crompton / Bajaj / Havells / Orient. | Civil | Labour | SWR33571 | 2192 | EA | 2192
55 | 180 | Supply and run of 2 of 22/0.3mm (1.5 sq.mm) (FR) P.V.C. insulated flexible copper cable in existing pipe for mains including all labour charges complete. | Civil | Labour | SWR33496 | 75 | m | 13500
56 | 180 | Supply and run of 2 of 36/0.3mm (2.5 sq.mm) FR P.V.C. insulated flexible copper cable in existing pipe for mains including all labour charges complete. | Civil | Labour | SWR33497 | 103 | m | 18540
57 | 12 | Supply & fixing of batten holder /slanting holder in lieu of ceiling rose of light point complete with all connection and all labour charges with 40W bulb (for new installation). | Civil | Labour | SWR33484 | 141 | EA | 1692
58 | 4 | Supply & fixing of 1200mm (48'') sweep 230v,A.C 50 Hz.Ceiling fan with 3 Blades and double ball bearings with all standared accessories. | Civil | Labour | SWR33563 | 2277 | EA | 9108
59 | 4 | Supply & fixing of Electronic Regulator for ceiling fans 900/1200/1400mm sweep including cost of material, Electrical charges complete for finished item of work | Civil | Labour | SWR33564 | 589 | EA | 2356
60 | 1 | Providing independent EARTHING by excavating a trench to a depth of 2.1M in all solid,as per size specified in the Data,using 40mm dia 'B' class GI pipe of 2.5 Mtrs length with necessary accessories with hume pipe ring duly providing staggered holes including filling with equal proportion of salt and Charcoal in layers and all labour charges etc., compiete for small quarters. | Civil | Labour | SWR33596 | 5345 | EA | 5345
61 | 35 | Supplying, laying, jointing and testing 101.6 mm SWG SP-1 pipes of ISI make conforming to ISI 651 & 4127 with airtight cement joints in CM 1.5:1 prop. Including excavation of trenches and socket pits in any soil (except rock requiring blasting) up to 1524 mm(5'0") depth and refilling with watering and tamping. | Civil | Labour | SWR34281 | 755 | m | 26425
62 | 3 | Constructing 904.0 mm (3#0#) dia brick masonry inspection chamber as per IS - 4111: Part-1:1986 with cement mortar (1:6) prop using 2nd Class Clay Bricks of 225 mm thick from approved source having a minimum crushing strength of 5 N/sq.mm including plastering with cement mortar 1:3 prop; ½# thick both inside and outside fitted with 20# dia RCC manhole covers and frames including excavating pits up to a depth of 904 mm (3'-0") in all sorts of soils (excluding rock) and laying cement concrete (1:4:8) 150 mm thick using 40 mm HBG Metal and P.C.C. 1:2:4 benching and channel 100 mm thick as per Standard specification and including cost and conveyance of all materials like cement, sand, bricks, water etc., to site, cost of seigniorage charges on all materials and all incidental and operational, labour charges like mixing cement mortar, constructing masonry, lift charges, curing etc., complete for finished item of work as per Standard specification. | Civil | Labour | SWR34296 | 8766 | EA | 26298
63 | 4 | Supply & fixing of 110 mm dia - Door Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34381 | 128 | EA | 512
64 | 4 | Supply & fixing of 110 mm dia - Plain Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34380 | 100 | EA | 400
65 | 12 | Supply & fixing of 110 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand | Civil | Labour | SWR34377 | 462 | m | 5544
66 | 18 | Supply & fixing of 90 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand | Civil | Labour | SWR34378 | 410 | m | 7380
67 | 3 | Supplying & fixing 150 mm x 100 mm SWG gully traps conforming to ISI 651 & 4127 with C.I Grating & Cost. Brick masonry in CM 1:6 prop. Intermediate chamber and fitted with 304.8 mm x 288.6mm (12"x9") C.I Frame and hinged cover | Civil | Labour | SWR34286 | 767 | EA | 2301
68 | 1 | Supplying and Fixing of European Water Closet of 1st Quality | Civil | Labour | SWR34312 | 2228 | EA | 2228
69 | 6 | Supply & fixing 15 mm angle stop cock Indian make 400 grams Seiko/ Senior/ Nice/ Senior/ Nice or equivalent | Civil | Labour | SWR34328 | 721 | EA | 4326
70 | 4 | S&F 15 mm N.P bib tap Indian make 400 grams full turn Seiko/ Senior/ Nice or equivalent | Civil | Labour | SWR34329 | 296 | EA | 1184
71 | 1 | Supplying & Fixing Indian make Flat Back Wash Hand Basin (HSW/Parryware/ Neycer) 1st quality conforming to IS:2556-Part-4:1972 with waste fittings like rubber plug, chain, 32 mm nominal size C.P. Fitting with parallel pipe thread conforming to IS:2963-1979 and fitted with 15 mm nominal bore Chromium Plated Pillar Tap of 1st quality Indian make 400 grams Seiko/ Senior/ Nice/ Esso or equivalent complete with standard CI brackets including wooden block: 550 x 400 mm - Single C.P. Pillar cock | Civil | Labour | SWR34316 | 1717 | EA | 1717
72 | 2 | Supply & fixing 38.1 mm C.P waste coupling Half or Full Thread 1st Quality Indian make Parryware or equivalent | Civil | Labour | SWR34428 | 309 | EA | 618
73 | 2 | Supply & fixing of 4" (101.6 mm ) Nahany Trap ( Without Jali with inlet)UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34387 | 134 | EA | 268
74 | 1000 | Providing & Placing on Terrace (at all floor levels) polyethylene water storage tank with Double layer approved brand & manufacture with cover and suitable locking arrangement & making necessary holes for inlet & outlets and over flow pipes but with NECESSARY fittings & base support for tanks | Civil | Labour | SWR34375 | 10 | L | 10000
75 | 2 | Supply & fixing 31.75 mm dia PVC flexible waste pipe of 914.4 mm length of Ist quality | Civil | Labour | SWR34426 | 33 | EA | 66
76 | 45 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)- 15.90mm OD Pipe - SDR 11 | Civil | Labour | SWR34361 | 239 | m | 10755
77 | 200 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-22.20mm OD Pipe - SDR 11 | Civil | Labour | SWR34362 | 313 | m | 62600
78 | 4 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type -20mm NB Size | Civil | Labour | SWR34345 | 331 | EA | 1324
79 | 1 | Supply & fixing 25.4 mm dia & 609.6 mm long aluminium anodized towel rod with brackets and aluminium screws | Civil | Labour | SWR34430 | 489 | EA | 489
80 | 36 | Plain Cement concrete PCC (1:3:6) using 40mm HBG metal for foundations and leveling course, including cost and conveyance of all materials, labour all leads and lifts, consolidation and all operations, formwork as required, curing, etc. complete for finished item w | Civil | Labour | SWR33029 | 4978 | m3 | 179208
81 | 120 | Supply&Fabrication and fixing of Welded wire mesh ( 2" x 2") of 3mm dia. with ISMC (75x40x4.4mm) and Pheriperal frame of ISA(35x35x3mm) incldg cost& conveyance painting with synthetic enamil paint two coats over a coat of red oxide primer etc complete for finished item of work.. | Civil | Labour | SWR33403 | 2310 | m2 | 277200
82 | 1 | Providing Consultancy services for arranging contour surveying with total station incuding preparation of boundary and contour levels with 2 Nos. Hard copies and soft copies complete for finished items of work | Civil | Labour | SWR33427 | 5665 | EA | 5665
83 | 222.2468 | Seigniorage Charges - Sand | Civil | Labour | SWR34470 | 40 | m3 | 8889.873
84 | 725.7496 | Seigniorage Charges - Metal | Civil | Labour | SWR34471 | 97.5 | m3 | 70760.585
85 | 839.38 | Seigniorage Charges - Gravel | Civil | Labour | SWR34472 | 30 | m3 | 25181.4
86 | 60 | Supply and fixing of RCC fencing poles of size 0.1mx0.1mx1.8m (security fencing of sub station), including cost and conveyance of all labour, materials,and hire chareges etc complete for finished item of work. | Civil | Labour | Swr33405 | 1444 | EA | 86640
87 | 1200 | Supply and fixing of galvanised barded wire (1 horizantal & 2 cross strands. including cost and conveyance of all labour, materials,and hire chareges etc complete for finished item of work. | Civil | Labour | Swr33408 | 16 | m | 19200
Civil labour |  |  | Total Rs. |  |  |  |  | 4231633.81
Total electrical and civil labour | [7 empty] | 19797430.2766

## 8. Satamrai
Name of Work: Estimate for erection of new 33/11kV Satamrai Outdoor Sub-Station with connected 33kV and 11kV Lines at Gaganpahad in Rajendranagar (M) in ECGH Division/Master plan/RR Circle- under Improvement works.
WBS No. S-1792-13-03-02-01-001
Sl No | Estimate Quantity | Description of item | Work Type | Item Short Description | APSS / Month Cl.NumberSSR 11 & 12 | Rate (INR) | UOM | AMOUNT
1 | 16 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | ELEC | Labour | SWR11039 | 928 | EA | 14848
2 | 5.76 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ELEC | Labour | SWR10868 | 6852 | TO | 39467.52
3 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELEC | supply | SMR40009 | 2181 | TO | 12562.56
4 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELEC | labour | SWR10877 | 851 | TO | 4901.76
5 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELEC | supply | SMR40010 | 1293 | TO | 7447.68
6 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELEC | labour | SWR10879 | 482 | TO | 2776.32
7 | 5.76 | Fabrication & erection of Channels-Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ELEC | labour | SWR10867 | 1470 | TO | 8467.2
8 | 16 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-R.S. Joists 150 x 150 mm | ELEC | labour | SWR10348 | 1952.61 | EA | 31241.76
9 | 17.758 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 116829.882
10 | 9.24 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ELEC | labour | SWR10862 | 373 | M2 | 3446.52
11 | 16 | Painting of poles-Paint of coping with 2 coats of white cement incl cost of paints etc. | ELEC | labour | SWR11089 | 48 | EA | 768
12 | 4 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-8.0Mtrs PSCC Poles 0.76 M x 0.76M x 1.52M (2.6" x 2.6" x 5.0') 0.88 cum | ELEC | labour | SWR11037 | 793 | EA | 3172
13 | 1 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ELEC | Labour | SWR10868 | 6852 | TO | 6852
14 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELEC | supply | SMR40009 | 2181 | TO | 2181
15 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELEC | labour | SWR10877 | 851 | TO | 851
16 | 1 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELEC | supply | SMR40010 | 1293 | TO | 1293
17 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELEC | labour | SWR10879 | 482 | TO | 482
18 | 1 | Fabrication & erection of Channels-Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ELEC | labour | SWR10867 | 1470 | TO | 1470
19 | 4 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Box pole 12 Mtr | ELEC | labour | SWR11267 | 3901.37 | EA | 15605.48
20 | 2.65 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 17434.35
21 | 2.31 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ELEC | labour | SWR10862 | 373 | M2 | 861.63
22 | 4 | Painting of poles- Paint of coping with 2 coats of white cement incl cost of paints etc. | ELEC | labour | SWR11089 | 48 | EA | 192
23 | 5.063 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ELEC | labour | SWR10868 | 6852 | TO | 34691.676
24 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELEC | supply | SMR40009 | 2181 | TO | 11042.403
25 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELEC | labour | SWR10877 | 851 | TO | 4308.613
26 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELEC | labour | SMR40010 | 1293 | TO | 6546.459
27 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELEC | labour | SWR10879 | 482 | TO | 2440.366
28 | 5.063 | Fabrication & erection of Channels-Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ELEC | labour | SWR10867 | 1470 | TO | 7442.61
29 | 13 | Erection of 33 KV AB Switch including alignment and earthing | ELEC | labour | SWR10392 | 4500 | EA | 58500
30 | 34 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Note:-The requirement of 2nd coat is to be justified by the concerned Divisional Engineer /Executive Engineer before execution of this work. Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | ELEC | labour | SWR10881 | 142 | EA | 4828
31 | 34 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | ELEC | labour | SWR12331 | 146.63 | EA | 4985.42
32 | 6 | Loading of 33 KV CTs/ PTs | ELEC | labour | SWR10200 | 165 | EA | 990
33 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
34 | 6 | Un loading of 33 KV CTs/ PTs | ELEC | labour | SWR10518 | 128 | EA | 768
35 | 2 | Erection of 33kv single phase PT s | ELEC | labour | SWR10401 | 1079 | SET | 2158
36 | 12 | Loading of 33 KV, 10 KA LAs Station typ | ELEC | labour | SWR10266 | 41 | EA | 492
37 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
38 | 12 | Un loading of 33 KV, 10 KA LAs Station type | ELEC | labour | SWR10584 | 35 | EA | 420
39 | 4 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33 KV LAS station/Line type including earthing | ELEC | labour | SWR10396 | 880 | SET | 3520
40 | 2 | Loading of 33 KV VCBs along with Panel boards | ELEC | labour | SWR10198 | 1024 | EA | 2048
41 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
42 | 2 | Un loading of 33 KV VCBs along with Panel boards | ELEC | labour | SWR10516 | 1044.48 | EA | 2088.96
43 | 12.584 | Excavate-Pit for 33KV VCB | ELEC | labour | SWR23224 | 331 | M3 | 4165.304
44 | 14.52 | Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x 1.8 x 0.75 cum for VCB Plinth | ELEC | labour | SWR20685 | 5160 | M3 | 74923.2
45 | 2 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33 KV VCB with Control Panel | ELEC | labour | SWR10460 | 12500 | EA | 25000
46 | 2 | Loading and unloading of PTR on constructed plinth-Loading of 8MVA PTR | ELEC | labour | SWR10613 | 5805.84 | EA | 11611.68
47 | 2 | Transport of Power transformers (0 to 100 KM) from one place to another place in GHMC Area.(excluding of loading & unloading )-8MVA power transformer | ELEC | labour | SWR10854 | 21945 | EA | 43890
48 | 2 | Loading and unloading of PTR on constructed plinth-Unloading of 8MVA PTR | ELEC | labour | SWR10627 | 5805.84 | EA | 11611.68
49 | 700 | S/o rail poles 90/105lb (250x2N) | ELEC | supply | SMR22718 | 47.27 | KG | 33089
50 | 14 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Rail pole 90 lbs | ELEC | labour | SWR10344 | 3510 | EA | 49140
51 | 2 | Erection of PTR on constructed plinth-Erection of 8 MVA PTR. | ELEC | labour | SWR21321 | 49480.2 | 49480.2 | 98960.4
52 | 0.436 | Extention of 33KV Bay at 132/33KV Sub-station-Zebra condutor | ELEC | supply | SMR24910 | 299369 | 299369 | 130524.884
53 | 30 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing | ELEC | supply | SMR11915 | 2055 | 2055 | 61650
54 | 30 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of I-Bolts | ELEC | supply | SMR22473 | 294 | 294 | 8820
55 | 45 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 "to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating . Sup T clamp LM6 Al alloy of 12 mm, 800 A | ELEC | labour | SMR40011 | 299 | 299 | 13455
56 | 6 | Bus stringing Hoisting of Insulators and hardware, stretching the conductor and stringing of 33 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bussection of 4.5mt) Hoisting post ins&hrd wr 1panther 33kv | ELEC | labour | SWR21240 | 781 | 781 | 4686
57 | 84 | Stringing of bus with panther conductor including jumpering etc., complete to all the equipment in SS fixing to all clamps and equipment.(3 Conductors) | ELEC | labour | SWR10404 | 327.68 | 327.68 | 27525.12
58 | 30 | Bus stringing Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | ELEC | labour | SWR10884 | 224 | 224 | 6720
59 | 75 | Labour for Fixing of all types of clamps | ELEC | labour | SWR10917 | 65 | 65 | 4875
60 | 25 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | ELEC | labour | SWR11039 | 928 | 928 | 23200
61 | 8.68 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ELEC | labour | SWR10868 | 6852 | 6852 | 59475.36
62 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELEC | supply | SMR40009 | 2181 | 2181 | 18931.08
63 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELEC | labour | SWR10877 | 851 | 851 | 7386.68
64 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELEC | supply | SMR40010 | 1293 | 1293 | 11223.24
65 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELEC | labour | SWR10879 | 482 | 482 | 4183.76
66 | 8.68 | Fabrication & erection of Channels-Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ELEC | labour | SWR10867 | 1470 | 1470 | 12759.6
67 | 25 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-R.S. Joists 150 x 150 mm | ELEC | labour | SWR10348 | 1952.61 | 1952.61 | 48815.25
68 | 27.75 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | 6579 | 182567.25
69 | 17.91 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ELEC | labour | SWR10862 | 373 | 373 | 6680.43
70 | 25 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | ELEC | labour | SWR11089 | 48 | 48 | 1200
71 | 4.642 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ELEC | labour | SWR10868 | 6852 | 6852 | 31806.984
72 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELEC | supply | SMR40009 | 2181 | 2181 | 10124.202
73 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELEC | labour | SWR10877 | 851 | 851 | 3950.342
74 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELEC | supply | SMR40010 | 1293 | 1293 | 6002.106
75 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELEC | labour | SWR10879 | 482 | TO | 2237.444
76 | 4.642 | Fabrication & erection of Channels-Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ELEC | labour | SWR10867 | 1470 | TO | 6823.74
77 | 17 | Erection of AB Switch and aligment complete-Erection of 11KV 800A double throw AB Switches | ELEC | labour | SWR21277 | 3500 | EA | 59500
78 | 3 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | ELEC | labour | SWR10393 | 3200 | EA | 9600
79 | 2 | Loading of 11 KV CT - PT Sets | ELEC | labour | SWR10201 | 190 | EA | 380
80 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
81 | 2 | Un loading of 11 KV CT - PT Sets | ELEC | labour | SWR10519 | 101 | EA | 202
82 | 2 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc-Erection of 11 KV three phase PTs | ELEC | labour | SWR10402 | 800 | SET | 1600
83 | 24 | Loading of 11 KV, 10 KA LAs Station type | ELEC | labour | SWR10264 | 32 | EA | 768
84 | 2 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 6599.4
85 | 24 | Un loading of 11 KV, 10 KA LAs Station type | ELEC | labour | SWR10582 | 32 | EA | 768
86 | 2 | Erection of 11 KV LAS station type including earthing | ELEC | labour | SWR10397 | 559 | SET | 1118
87 | 6 | Erection of 11 KV LAS line type including earthing | ELEC | labour | SWR10398 | 505 | SET | 3030
88 | 8 | Loading of 11 KV VCBs along with Panel boards | ELEC | labour | SWR10199 | 1024 | EA | 8192
89 | 4 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 13198.8
90 | 8 | Un Loading of 11 KV VCBs along with Panel boards | ELEC | labour | SWR10517 | 1044.48 | EA | 8355.84
91 | 41.6 | Excavate-Pit for 33KV VCB | ELEC | labour | SWR23224 | 331 | M3 | 13769.6
92 | 48 | Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x 1.8 x 0.75 cum for VCB Plinth | ELEC | labour | SWR20685 | 5160 | M3 | 247680
93 | 8 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc-Erection of 11 KV VCB with Control Panel | ELEC | labour | SWR10461 | 12000 | EA | 96000
94 | 12 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing | ELEC | supply | SMR11915 | 2055 | SET | 24660
95 | 12 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of I-Bolts | ELEC | supply | SMR22473 | 294 | EA | 3528
96 | 45 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 "to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating . Sup T clamp LM6 Al alloy of 12 mm, 800 A | ELEC | supply | SMR40011 | 299 | EA | 13455
97 | 2 | Bus Stringing -Hoisting of Insulators and hardware, stretching the conductor and stringing of 11 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 3.5mt) Hoisting post ins&hrd wr 1panther 11kv | ELEC | labour | SWR21241 | 507 | EA | 1014
98 | 63 | Stringing of bus with panther conductor including jumpering etc., complete to all the equipment in SS fixing to all clamps and equipment.(3 Conductors) | ELEC | labour | SWR10404 | 327.68 | M | 20643.84
99 | 45 | Bus stringing Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | ELEC | labour | SWR10884 | 224 | EA | 10080
100 | 57 | Labour for Fixing of all types of clamps | ELEC | labour | SWR10917 | 65 | EA | 3705
101 | 584 | Laying of earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication 75x 8mm MS Flat / GI Flat. Laying of earth mat,excavation 75x 8mm | ELEC | labour | SWR10920 | 65 | RMT | 37960
102 | 1010 | Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) Earthing for raisers of SS Flat 50x6 mm. | ELEC | labour | SWR10919 | 41 | RMT | 41410
103 | 36 | Supply of earthing pipe with materials -Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | ELEC | supply | SMR11482 | 3486 | EA | 125496
104 | 36 | Providing of Earthing-Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | ELEC | labour | SWR10357 | 1234.2 | EA | 44431.2
105 | 36 | Providing of RCC collar to earth pit-Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINES-Providing of RCC collar | ELEC | labour | SWR10359 | 386 | EA | 13896
106 | 2 | Supply of Copper Flexible jumper with 75 X 8 of length 250 mm at neutral of Power tranformer end and 50 X 6 of length 50mm two Nos at double neutral end duly brasing with flexible jumper of capacity of 5kA/3 sec for power transformer neutral. SupCU Flexi jumper for Power T/F Neutral | ELEC | supply | SMR40033 | 4725 | EA | 9450
107 | 2 | Providing of earthing with various types of earth electrodes-Providing of double earthing for neutral with flexible copper jumpers including arrangement by fixing M.S.Channel 100x50mm. | ELEC | labour | SWR11892 | 1323 | EA | 2646
108 | 80 | Providing of control cable trench as per DATA-XII | ELEC | labour | SWR22093 | 3148 | RMT | 251840
109 | 3074 | Control Cable-Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends . Lay-4C/10C 2.5Sqmm Control Cable | ELEC | labour | SWR11879 | 27 | M | 82998
110 | 270 | Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per specification (including cost of ferrules, lugs and glands) | ELEC | labour | SWR12510 | 27 | EA | 7290
111 | 4 | Marshalling Box Supply of FRP PT Marshalling Box | ELEC | supply | SMR40048 | 4463 | EA | 17852
112 | 4 | Marshalling Box Erection of Marshalling boxes | ELEC | labour | SWR10940 | 374.85 | EA | 1499.4
113 | 1 | Loading of 220 V Batterry with charger | ELEC | labour | SWR11166 | 1612 | SET | 1612
114 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
115 | 1 | Un loading of 220 V Batterry with charger | ELEC | labour | SWR11147 | 1024 | SET | 1024
116 | 1 | Batteries-Erection of 220 V, 200 AH battery in complete shape fit for charging . Conventional lead acid | ELEC | labour | SWR12350 | 7666 | EA | 7666
117 | 1 | Control Panels -Supply of DC Annunciation & relay panel for 10 feeder panel including the cost of LED Indiacation lamps, VAA auxilairy relays, Electronic Hooters complete as per specification. | ELEC | supply | SMR40044 | 42500 | EA | 42500
118 | 1 | Control Panels -Supply of AC Supply panel inluding providing of changeover switch, SFU, metering unit, 32 A three phase MCB, 16 A Single phase MCB complete as per specification. Supply of AC Supply panel complete | ELEC | supply | SMR40045 | 42000 | EA | 42000
119 | 2 | Fixing of AC/DC Panel and giving Connections to the protection equipment and Metering circuits as per the specification and standards. The 3 1/2 core 25 Sqmm power cable required from distribution box to AC/DC panel in the control room is also to be supply | ELEC | labour | SWR20025 | 7871.85 | SET | 15743.7
120 | 8 | Yard lightning-Supply of stepped tubular poles single way made of steel of length 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9 mm, 2.1 mtrs with outer dia 76.1 mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79 kgf as per IS 2713 | ELEC | supply | SMR40051 | 13913 | EA | 111304
121 | 8 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE/CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA /OSRAM /SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty S-90W LED fixture set | ELEC | labour | SMR11594 | 8200 | EA | 65600
122 | 8 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | ELEC | labour | SWR11039 | 928 | EA | 7424
123 | 8 | Erection of tubular poles | ELEC | labour | SWR10955 | 1379 | EA | 11032
124 | 5.27 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 34671.33
125 | 8 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE/CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA /OSRAM /SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty. Fixing of Metal halide lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5 GI pipe complete Fixing of LED/Metal halide complete. | ELEC | labour | SWR10956 | 1268 | EA | 10144
126 | 45 | Supply of HBG metal-Supply & spreading of 20mm machine crushed metal (HBG) including cost of conveneyance of all materials, labour charges etc complete for finished item of work and directed by the engineer incharge | ELEC | labour | SWR10860 | 2113 | M3 | 95085
127 | 2 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M Ex of Hard pit w/o blast 0.75X0.9X1.95M | ELEC | labour | SWR11040 | 990.68 | EA | 1981.36
128 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELEC | Supply | SMR40009 | 2181 | TO | 1635.75
129 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELEC | labour | SWR10877 | 851 | TO | 638.25
130 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELEC | Supply | SMR40010 | 1293 | TO | 969.75
131 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELEC | labour | SWR10879 | 482 | TO | 361.5
132 | 1 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Box pole 12 Mtr | ELEC | labour | SWR11267 | 3901.37 | EA | 3901.37
133 | 2.22 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 14605.38
134 | 1.16 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ELEC | labour | SWR10862 | 373 | M2 | 432.68
135 | 2 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | ELEC | labour | SWR11089 | 48 | EA | 96
136 | 1 | Construction of DTR Plinth-RCC Column type DTR Plinth of size 1'X1'X10',topslab 4'x4'x6" & beam size 4'X8'X8" upto 160KVA | ELEC | labour | SWR21843 | 25967.57 | EA | 25967.57
137 | 1 | Loading of 50,63, 75 & 100 KVA DTR | ELEC | labour | SWR10195 | 350 | EA | 350
138 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
139 | 1 | Un loading of 50,63, 75 & 100 KVA DTR | ELEC | labour | SWR10513 | 280 | EA | 280
140 | 1 | Erection of DTR's including loading and Unloading DTR on the Structure/Plinth etc-Erection of 3 Phase DTRs 63,75 & 100 KVA | ELEC | labour | SWR20905 | 1650 | EA | 1650
141 | 1 | Erection of AB Switch and aligment complete Erection of 11KV 200A TT type AB Switch including fixing of cross angles and alignment complete | ELEC | labour | SWR20102 | 1813.49 | EA | 1813.49
142 | 1 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erect. of 11kv HG Fuseset incl earthing | ELEC | labour | SWR10395 | 740.52 | SET | 740.52
143 | 40 | Excavation & laying of UG Cable in Single Run Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.-In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road-11KV 3x185 Sqmm Cable | ELEC | labour | SWR11920 | 465.46 | M | 18618.4
144 | 20 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-11 KV 3x185 Sqmm Cable | ELEC | labour | SWR11956 | 126.23 | M | 2524.6
145 | 2 | Making of Outdoor/Indoor End Termination Making 11 KV 3x185 Sqmm Cable Out Door/Indoor end termination | ELEC | labour | SWR10390 | 2370.63 | EA | 4741.26
146 | 1 | Erection of LT distribution box including laying of LT cable from distribution box to LT OH line and DTR to distribution box including earthing of distribution box and crimping of lugs connecting of jumpers etc | ELEC | labour | SWR10674 | 1594.67 | EA | 1594.67
147 | 85 | LAYING OF 33KV, 11KV UG CABLE Excavation & laying of UG Cable in Single Run Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road-LT 3 1/2 x 185 Sqmm Cable | ELEC | labour | SWR11923 | 377.63 | M | 32098.55
148 | 15 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-LT 3 1/2 x 185 Sqmm Cable | ELEC | labour | SWR11959 | 85.43 | M | 1281.45
149 | 2 | UG Cables Joints :-Making of Outdoor/Indoor End Termination -Supply & fixing of Oout Door/Indoor end termination LT 3 1/2 x 185 Sqmm Cable | ELEC | labour | SWR10765 | 968.9 | EA | 1937.8
150 | 1 | Supply and fixing of Substation board of size 3'x2.5' indicating the layout of switchyard Sup &fix of board ind Switchyard layout | ELEC | labour | SWR20032 | 1654 | EA | 1654
151 | 1 | Supply and fixing of safety instructions/Substation operation instruction board. Sup& fix safety inst/SS Op. inst board | ELEC | labour | SWR22090 | 2205 | EA | 2205
152 | 750 | Control Panels Supplying & fabrication erection of 6mm Checkerd plates as per the field conditions Supply,fabricati of 6mm Checkerd plates | ELEC | Labour | SWR10873 | 83 | KG | 62250
153 | 1 | T & P Supply of Wall clock standard make | ELEC | Supply | SMR40059 | 578 | EA | 578
154 | 1 | S-10ft Aluminium Ladder | ELEC | Supply | SMR12378 | 1654 | EA | 1654
155 | 1 | Sup Alluminium Ladder for indoor works | ELEC | Supply | SMR40062 | 4410 | EA | 4410
156 | 30 | T & P Painting of Name Plates for any equipmen | ELEC | labour | SWR10963 | 122 | EA | 3660
157 | 1 | T & P Supply of Taparia Tool kit of Size 20”x10”x15” with tier arrangements Tool box with locking arrangement & key containing (1) Double Ended fix Spanner sets, (Ribbed) 6 x 7, 8 x 9, 10 x 11, 12 x 13, 14 x 15, 16 x 17, 18 x19, 20 x 22, 21 x 23, 24 x 27, 25 x28, 30 x 32, (2) Double Ended Ring Spanners sets, 6 x 7 , 8 x 9, 10 x 11, 12 x 13, 14 x 15. 16 x 17 , 18 x 19, 20 x 22 , 21 x 23, 24 x 27, 25 x28, 30 x 32 mm, (3) Adjustable Spanner 305 mm length least maximum opening 35mm chrome, (4) Pipe Wrench Length 350 mm 14”, (5) Soft faced Hammer with suitable handle 2 lb, (6) Hacksaw frame with metal handle heavy duty for 12" hacksaw blade with High Speed blade, (7) Insulated Screw drivers Transparent Green Handle Set Length 6”, 8” & 12”, (8) Star Screw Driver Transparent Green Handle Length 6”, (9) Insulated Wire Cutter, (10) Insulated Cutting Plier Length 8” with cable stripper insulated with thick C. A. sleeve confirming to IS: 4378 - 1990, (11) Long Nose Plier insulated with thick C.A. sleeve generally confirming to IS:3552-1989, (12) Tester type screw driver (special with neon bulb) generally confirm to IS: 5579- 1985 Grade:II handle yellow/ green colour overall length 130 mm, (13) Insulated Crimping Plier of all Taparia make. SupTaparia Tool kit complete as per Spec | ELEC | Supply | SMR40063 | 4925 | SET | 4925
158 | 1 | T & P Sup Rechargeable LED torch light of Standard make | ELEC | Supply | SMR40064 | 1733 | EA | 1733
159 | 1 | T & P-Steel almarah(61/2 X 3ft) Godrej | ELEC | Supply | SMR40061 | 9818 | EA | 9818
160 | 1 | T & P-Table (3x6ft) Godrej | ELEC | Supply | SMR40057 | 6050 | EA | 6050
161 | 4 | T & P-S type chairs (Godrej) | ELEC | Supply | SMR40058 | 924 | EA | 3696
162 | 1 | T & P Sup Angle racks(18x36.6inches) Godrej | ELEC | Supply | SMR40060 | 1733 | EA | 1733
163 | 1 | T & P Supply of Hack saw (12 inches) | ELEC | Supply | SMR40065 | 289 | EA | 289
164 | 4 | Sup Earth Rods (8ft) Screw & clamp type | ELEC | Supply | SMR40066 | 578 | EA | 2312
165 | 2 | Supply of Hand Gloves | ELEC | Supply | SMR40067 | 289 | SET | 578
166 | 12 | SupRubber mats( 6'x3')size fo indoorSS | ELEC | Supply | SMR40068 | 1386 | EA | 16632
167 | 1 | Biometric Time attendence System & Telecom Sup Stand basic cell phone with charger | ELEC | Supply | SMR40069 | 1386 | EA | 1386
168 | 14 | Supply of Danger boards with clamps | ELEC | Supply | SMR40070 | 116 | EA | 1624
169 | 2 | Supply of Materials -Fire bucket stand with 3 buckets (8 -10 ltr capacity) | ELEC | Supply | SMR40088 | 1386 | SET | 2772
170 | 2 | Room fire extinguisher (2 ltrs capacity) for control room | ELEC | Supply | SMR40089 | 4620 | EA | 9240
171 | 4 | Sup TrollyMounted Co2 (6.5Kgs) Cylinders(IS-2878) | ELEC | Supply | SMR40087 | 9240 | EA | 36960
172 | 6 | Supply of Safety Helmet of standard make | ELEC | Supply | SMR40071 | 231 | EA | 1386
173 | 8 | Supply of LC Boards | ELEC | Supply | SMR40072 | 116 | EA | 928
174 | 4 | Supply of Gum Boots(Pairs) | ELEC | Supply | SMR40073 | 693 | EA | 2772
175 | 1 | Supply of 5000v megger | ELEC | Supply | SMR40074 | 13860 | EA | 13860
176 | 1 | Supply of Earth megger (1000v) | ELEC | Supply | SMR40075 | 8085 | EA | 8085
177 | 1 | Supply of Digital clamp meter. | ELEC | Supply | SMR40076 | 2888 | EA | 2888
178 | 1 | Name board of the 33/11kV Sub-Station(As per Standard Specification) Sup 33/11kv S.S Permanent name board | ELEC | Supply | SMR40086 | 10238 | EA | 10238
179 | 800 | Supply of Hot dip galvanized/zinc coated bolts & nuts including spring washers, pack washers and flat washers etc. | ELEC | Supply | SMR12488 | 90 | KG | 72000
180 | 2 | Fabrication of poles-Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | ELEC | labour | SWR10642 | 512.55 | EA | 1025.1
181 | 1 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-RS Joists 150x75/175 x 85 mm | ELEC | labour | SWR10346 | 1934 | EA | 1934
182 | 5760 | S-Supply of RS Joist Grider Pole (150x150mm) | ELEC | Supply | SMR12302 | 59.25 | KG | 341280
183 | 1000 | S-Supply of RS Joist Pole (175x85mm) | ELEC | Supply | SMR12303 | 60.75 | KG | 60750
184 | 5063 | S- Supply of MS Channel 100x50mm | ELEC | Supply | SMR22745 | 57.45 | KGS | 290869.35
185 | 13 | S-Supply of 33KV 800A DB Break AB Switch | ELEC | Supply | SMR12315 | 40658.78 | EA | 528564.14
186 | 8680 | S-Supply of RS Joist Grider Pole (150x150mm) | ELEC | Supply | SMR12302 | 59.25 | KG | 514290
187 | 4642 | S- Supply of MS Channel 100x50mm | ELEC | Supply | SMR22745 | 57.45 | KGS | 266682.9
188 | 17 | S-Supply of 11KV 800A DB Break AB Switch | ELEC | Supply | SMR12316 | 30847.46 | EA | 524406.82
189 | 3 | S-Supply of 11KV 400A DB Break AB Switch | ELEC | Supply | SMR12317 | 18150 | EA | 54450
190 | 3045 | S-Supply of MS Flat 75x8mm | ELEC | Supply | SMR12321 | 56.42 | KG | 171798.9
191 | 2666 | S-Supply of MS Flat 50x6mm | ELEC | Supply | SMR12322 | 56.5 | KG | 150629
192 | 750 | S-Supply of RS Joist Pole (175x85mm) | ELEC | Supply | SMR12303 | 60.75 | KG | 45562.5
193 | 1 | S-Supply of 11KV 200A Tilting Type AB Switch | ELEC | Supply | SMR12318 | 8991 | EA | 8991
194 | 1 | S-Supply of 11KV HG FuseSet for StationTransformer | ELEC | Supply | SMR12324 | 1974 | EA | 1974
195 | 1 | S-Supply of LT Distribution Box (SMC) | ELEC | Supply | SMR25200 | 7797 | EA | 7797
196 | 2 | S-Supply of 11KV 3x185 Heat Shble O/d End Term Kit | ELEC | Supply | SMR25201 | 1182.97 | EA | 2365.94
197 | 40 | S-Supply of LT XLPE Cable 1C 150 sqmm | ELEC | Supply | SMR25203 | 114.83 | M | 4593.2
198 | 100 | Supply of LT XLPE Cable 31/2C185sqmm. | ELEC | supply | SMR25204 | 547 | M | 54700
199 | 4 | Loading of LT AB Cable 3X16+25 Sqmm | ELEC | labour | SWR11702 | 200 | DR | 800
200 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
201 | 4 | Un loading of LT AB Cable 3X16+25 Sqmm | ELEC | labour | SWR11713 | 204 | DR | 816
202 | 8 | survey line&cabl inc peg mark&tree clear | ELEC | labour | SWR22092 | 765 | KM | 6120
203 | 8 | Paving out and stringing of conductor by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location-100 Sqmm Single Circuit (3 Conductors) | ELEC | labour | SWR10366 | 13856.7 | KM | 110853.6
204 | 160 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M Ex of Hard pit w/o blast 0.75X0.9X1.95M | ELEC | labour | SWR11040 | 990.68 | EA | 158508.8
205 | 160 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Errection of 11 M long PSCC pole | ELEC | labour | SWR10978 | 4336.85 | EA | 693896
206 | 49.75 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 327305.25
207 | 160 | Painting of poles-Numbering of poles incl. cost of paint | ELEC | labour | SWR10378 | 32 | EA | 5120
208 | 60 | Excavation of pits in all soils except hard rock requiring blasting-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") 1.05 cum | ELEC | labour | SWR10107 | 700 | EA | 42000
209 | 60 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Erec of 9.1 Mts PSCC poles for stuts | ELEC | labour | SWR11083 | 2400 | EA | 144000
210 | 24.3 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 159869.7
211 | 40 | Formation of Cut points - Formation of Cut point for 11 KV Single Circuit line excluding pole erection and stays Formatn of Horiz Cut point for 11KV line | ELEC | labour | SWR10653 | 1435.81 | EA | 57432.4
212 | 300 | Supply of earthing pipe with materials S-GI Bolts & Nuts,Washers etc., | ELEC | supply | SMR11488 | 117.5 | KG | 35250
213 | 8 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 26397.6
214 | 8 | LOADING of Conductor drums | ELEC | labour | SWR10191 | 202 | EA | 1616
215 | 8 | UNLOADING of Conductor drums | ELEC | labour | SWR10509 | 100 | EA | 800
216 | 50 | Loading of 33 KV Pin insulators | ELEC | labour | SWR10211 | 3 | CRT | 150
217 | 50 | Un loading of 33 KV Pin insulators | ELEC | labour | SWR10529 | 3 | CRT | 150
218 | 15 | Loading of 33 KV Metal parts | ELEC | labour | SWR10618 | 65 | BAG | 975
219 | 15 | Un loading of 33 KV Metal parts | ELEC | labour | SWR10632 | 65 | BAG | 975
220 | 460 | Excavation & laying of UG Cable (Double Run) Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, Along the CC / BT multi layer road requiring compressor-33 KV 3x400 Sqmm Cable | ELEC | labour | SWR11980 | 1388.84 | M | 638866.4
221 | 460 | Laying of 2nd cable in excavated trench | ELEC | labour | SWR10988 | 204.1 | M | 93886
222 | 40 | Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-33 KV 3x400 Sqmm Cable | ELEC | labour | SWR12004 | 323.85 | M | 12954
223 | 12 | Cost of Pipes and slabs-Supply of 6" B class GI pipe | ELEC | supply | SMR40081 | 1044 | M | 12528
224 | 30 | Cost of Pipes and slabs-Supply of 250 mm Hume pipe of class NP3 with compresive strength of 35N/mm2 for 28 days curing,barewall thickness of 30mm,1.25kG linear/meter and withstanding capability of 22.50KN/linear meter as per IS 458-1993. | ELEC | supply | SMR40077 | 363 | M | 10890
225 | 5 | Cost of Pipes and slabs-Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters , CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | ELEC | supply | SMR40085 | 484 | EA | 2420
226 | 8 | Making of Outdoor/Indoor End Making 33 KV 3x400 Sqmm Cable Out Door/Indoor end termination TerminationOD/Idoor end termination 33kv 3x400 xlpe | ELEC | labour | SWR10387 | 2764.76 | EA | 22118.08
227 | 2 | UG Cables Joints 33 KV 3x400 Sqmm Cable Straight through joint 33kv 3x400 xlpe | ELEC | labour | SWR10382 | 5700.78 | EA | 11401.56
228 | 3 | Fabrication & erection of Channels -Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to theRS-Joist poles excluding cost of Mild Steel and transportcharges to substation site, including erection. Fabrication of struc.with welding. | ELEC | labour | SWR10869 | 3426 | TO | 10278
229 | 50 | Supply of earthing pipe with materials-Supply of GI wire No 8 | ELEC | supply | SMR11486 | 105 | KG | 5250
230 | 2 | Supply of earthing pipe with materials-Supply of CI eath pipe with 80mm dia,2.0 M Length | ELEC | labour | SMR11483 | 2789 | EA | 5578
231 | 2 | Providing of Earthing-Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | ELEC | labour | SWR10357 | 1234.2 | EA | 2468.4
232 | 2 | Providing of RCC collar to earth pit-Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINES-Providing of RCC collar | ELEC | labour | SWR10359 | 386 | EA | 772
233 | 40 | Supply of earthing pipe with materials-Supply of GI Flat 25X3 mm | ELEC | supply | SMR11485 | 105 | KG | 4200
234 | 20 | Supply of Danger boards with clamps | ELEC | supply | SMR40070 | 116 | EA | 2320
235 | 5 | S&E-Smart RFID marker | ELEC | labour | SWR25089 | 2745 | EA | 13725
236 | 4 | Load-11/33KV XLPE UG Cable for all sizes | ELEC | labour | SWR11230 | 1024 | DR | 4096
237 | 2 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 6599.4
238 | 4 | Unload-11/33KV XLPE UG Cable for all sizes | ELEC | labour | SWR11231 | 1024 | DR | 4096
239 | 60 | Supply of PSCC Pole 9.1Mtr 280KG | ELEC | supply | SMR25233 | 3109.41 | EA | 186564.6
240 | 1600 | Supply of Materials -- Supply of MS Channel 100X50mm | ELEC | supply | SMR22745 | 57.45 | KGS | 91920
241 | 1000 | Supply of MS Angle 65x65x6 | ELEC | supply | SMR25207 | 57.25 | KG | 57250
242 | 400 | Supply of Materials -- Supply of MS Flat 75x8 mm | ELEC | supply | SMR12321 | 56.42 | KG | 22568
243 | 8 | UG Cables Joints : Making of Outdoor/Indoor End Termination -- Supply 33KV 3x400Sqmm Outdoor | ELEC | supply | SMR22222 | 4554 | EA | 36432
244 | 2 | UG Cables Joints : Making of Straight through joints -- Supply of 33KV 3x400SQmm Straight Through Joint Kit | ELEC | supply | SMR22223 | 24151 | EA | 48302
245 | 160 | Supply of PSCC Pole 11Mtr 365KG | ELEC | supply | SMR25236 | 5399 | EA | 863840
246 | 120 | Supply of 33KV V-Cross Arm without Clamps | ELEC | supply | SMR25229 | 1678 | EA | 201360
247 | 9 | survey line&cabl inc peg mark&tree clear | ELEC | labour | SWR22092 | 765 | KM | 6885
248 | 9 | Paving out and stringing of conductor by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location-55 Sqmm Single Circuit (3 Conductors) | ELEC | labour | SWR10365 | 9454.81 | KM | 85093.29
249 | 175 | Excavation of pits in all soils except hard rock requiring blasting-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") 1.05 cum | ELEC | labour | SWR10107 | 700 | EA | 122500
250 | 50 | Excavation of pits in hard rock requiring blasting. (other than SS)-9.1Mtrs PSCC Pole 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | ELEC | labour | SWR10112 | 1770 | EA | 88500
251 | 213 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-9.1 M long PSCC pole | ELEC | labour | SWR10343 | 2400 | EA | 511200
252 | 33.29 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 219014.91
253 | 225 | Painting of poles-Numbering of poles incl. cost of paint | ELEC | labour | SWR10378 | 32 | EA | 7200
254 | 80 | Excavation of pits in all soils except hard rock requiring blasting-Stud Poles 0.6 M x 0.9 M x 1.5 M | ELEC | labour | SWR10106 | 645 | EA | 51600
255 | 80 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-8.0 m long PSCC poles for Strut | ELEC | labour | SWR21590 | 1500 | EA | 120000
256 | 32.4 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 213159.6
257 | 40 | Formation of Cut points - Formation of Cut point for 11 KV Single Circuit line excluding pole erection and stays Formatn of Horiz Cut point for 11KV line | ELEC | labour | SWR10653 | 1435.81 | EA | 57432.4
258 | 350 | Supply of earthing pipe with materials S-GI Bolts & Nuts,Washers etc., | ELEC | supply | SMR11488 | 117.5 | KG | 41125
259 | 9 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 29697.3
260 | 9 | LOADING of Conductor drums | ELEC | labour | SWR10191 | 202 | EA | 1818
261 | 9 | UNLOADING of Conductor drums | ELEC | labour | SWR10509 | 100 | EA | 900
262 | 6 | Supply of earthing pipe with materials-Supply of CI eath pipe with 50mm dia,2.0 M Length | ELEC | supply | SMR11484 | 2441 | EA | 14646
263 | 6 | Providing of Earthing-Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | ELEC | labour | SWR10357 | 1234.2 | EA | 7405.2
264 | 6 | Providing of RCC collar to earth pit-Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINES-Providing of RCC collar | ELEC | labour | SWR10359 | 386 | EA | 2316
265 | 6 | Assembly and erection of Structure as per specification which includes fixing of top channels and cross bracings, transport of all materials from road side to the location, earthing, back filling with earth ramming etc excluding pit excavation and concreting.-11KV DP Structure with 9.1 Mtrs PSCC Poles | ELEC | labour | SWR21130 | 3363.96 | SET | 20183.76
266 | 6 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | ELEC | labour | SWR10393 | 3200 | EA | 19200
267 | 6 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | ELEC | labour | SWR10881 | 142 | EA | 852
268 | 200 | Supply of earthing pipe with materials-Supply of GI wire No 8 | ELEC | supply | SMR11486 | 105 | KG | 21000
269 | 675 | Loading of 11KV Polymer Pin Insulators with GI pins | ELEC | labour | SWR11248 | 1 | EA | 675
270 | 675 | Un loading of 11KV Polymer Pin Insulators with GI pins | ELEC | labour | SWR11249 | 1 | EA | 675
271 | 240 | Loading of 11KV Polymer Pin Insulators with GI pins | ELEC | labour | SWR11248 | 1 | EA | 240
272 | 240 | Un loading of 11KV Polymer Pin Insulators with GI pins | ELEC | labour | SWR11249 | 1 | EA | 240
273 | 6 | Loading of 11 KV Metal parts | ELEC | labour | SWR12402 | 48 | BAG | 288
274 | 6 | Un loading of 11 KV Metal parts | ELEC | labour | SWR12421 | 48 | BAG | 288
275 | 960 | Excavation & laying of UG Cable (Double Run)-Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts,-In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil/CC-11 KV 3x300 Sqmm Cable | ELEC | labour | SWR11973 | 631.06 | M | 605817.6
276 | 960 | Laying of 2nd cable in excavated trench | ELEC | labour | SWR10988 | 204.1 | M | 195936
277 | 240 | Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-11 KV 3x300 Sqmm Cable | ELEC | labour | SWR12005 | 275.4 | M | 66096
278 | 72 | Cost of Pipes and slabs-Supply of 6" B class GI pipe | ELEC | supply | SMR40081 | 1044 | M | 75168
279 | 200 | Cost of Pipes and slabs-Supply of 250 mm Hume pipe of class NP3 with compresive strength of 35N/mm2 for 28 days curing,barewall thickness of 30mm,1.25kG linear/meter and withstanding capability of 22.50KN/linear meter as per IS 458-1993. | ELEC | supply | SMR40077 | 363 | M | 72600
280 | 10 | Cost of Pipes and slabs-Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters , CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | ELEC | supply | SMR40085 | 484 | EA | 4840
281 | 5 | Load-11/33KV XLPE UG Cable for all sizes | ELEC | labour | SWR11230 | 1024 | DR | 5120
282 | 5 | Unload-11/33KV XLPE UG Cable for all sizes | ELEC | labour | SWR11231 | 1024 | DR | 5120
283 | 24 | Making of Outdoor/Indoor End Termination-Making 11 KV 3x300 Sqmm Cable Out Door/Indoor end termination | ELEC | labour. | SWR10391 | 2370.63 | EA | 56895.12
284 | 6 | UG Cables Joints Making of Straight through joints-11 KV 3x300 Sqmm Cable | ELEC | labour. | SWR10386 | 3725.45 | EA | 22352.7
285 | 1.1 | Fabrication & erection of Channels -Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to theRS-Joist poles excluding cost of Mild Steel and transportcharges to substation site, including erection. Fabrication of struc.with welding. | ELEC | labour | SWR10869 | 3426 | TO | 3768.6
286 | 50 | Supply of Danger boards with clamps | ELEC | supply | SMR40070 | 116 | EA | 5800
287 | 6 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | ELEC | labour | SWR12331 | 146.63 | EA | 879.78
288 | 10 | S&E-Smart RFID marker | ELEC | labour | SWR25089 | 2745 | EA | 27450
289 | 225 | Supply of PSCC Pole 9.1Mtr 280KG | ELEC | supply | SMR25233 | 3109.41 | EA | 699617.25
290 | 80 | Supply of PSCC Pole 8Mtr 140KG | ELEC | supply | SMR25232 | 1580 | EA | 126400
291 | 185 | supply of V X-Arm with MS Angle 65x65x6 | ELEC | supply | SMR25218 | 743 | EA | 137455
292 | 185 | S-Supply of 11KV Top Cleat for 9.1M(Vertical) | ELEC | Supply | SMR25226 | 256 | EA | 47360
293 | 80 | Supply of 11KV Horizontal Cross Arm | ELEC | supply | SMR25223 | 528 | EA | 42240
294 | 6 | Supply of Materials -- Supply of 11 kV 400 A Double break AB switch | ELEC | supply | SMR12317 | 18150 | EA | 108900
295 | 200 | Supply of Materials -- Supply of MS Flat 50x6 mm | ELEC | supply | SMR12322 | 56.5 | KG | 11300
296 | 400 | Supply of MS Angle 50x50x6 | ELEC | supply | SMR25206 | 58.15 | KG | 23260
297 | 500 | Supply of MS Channel 75x40 mm | ELEC | supply | SMR25205 | 58.45 | KG | 29225
298 | 24 | Supply of 11KV 3x300 Heat Shble O/d End Term Kit | ELEC | supply | SMR25208 | 1372.88 | EA | 32949.12
299 | 6 | Supply of 11KV 3x300 Heat Shble stright through joint Kit | ELEC | supply | SMR25210 | 4110.17 | EA | 24661.02
Sub Total: | [7 empty] | 14802221.555
Civil Labour-S-1792-13-07-01-01-001
Sl No | Estimate Quantity | Description of item | Work Type | Item Short Description | APSS / Month Cl.NumberSSR 11 & 12 | Rate (INR) | UOM | AMOUNT
1 | 32 | Leveliing the site by cutting and levelling with the help of JCB including cost,conveyance of all materials,hire chareges etc complete for finished item of work as directed by Engineer-in-charge. | Civil | Labour | SWR34179 | 2165 | Hrs | 69280
2 | 135.61 | Earth work excavation in all type of ordinary soils red earth, Hard gravelly soils, earth mixed with sand and sandy soils etc., in all conditions such as slushy and dry with initial leads and lifts for foundations. | Civil | Labour | SWR33015 | 486 | m3 | 65906.46
3 | 32.45 | Plain Cement concrete PCC (1:4:8) using 40mm HBG metal for foundations and leveling course, including cost and conveyance of all materials, labour all leads and lifts, consolidation and all operations, formwork as required, curing, etc. complete for finished item w | Civil | Labour | SWR33028 | 4811 | m3 | 156116.95
4 | 117.88 | Coursed Rubble stone (CRS) masonry 2nd sort with hard granite stones in cement mortar (1:6) for basement, including cost and conveyance of all materials, labour charges, curing, all leads and lifts, etc, complete for finished item of work. | Civil | Labour | SWR33041 | 4920 | m3 | 579969.6
5 |  | 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge
6 | 3.564 | RCC M20 Grade footing 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33098 | 9563 | m3 | 34082.532
7 | 2.28 | RCC M20 Grade Coloumn . 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33100 | 13312 | m3 | 30351.36
8 | 2.25 | RCC M20 Grade Plinth beams 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33099 | 12434 | m3 | 27976.5
9 | 3.17 | D) RCC M20 Grade Roof Beams landing beam 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33121 | 12350 | m3 | 39149.5
10 | 0.58 | e)RCC M20 Grade Lintels 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33107 | 13141 | m3 | 7621.78
11 | 2.7 | f) RCC M20 Grade Sunshades 600mm wide and 75mm thick'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33114 | 1381 | m2 | 3728.7
12 | 15.224 | g) RCC M20 Grade Roof Slab for Control Room 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33128 | 10938 | m3 | 166520.112
13 | 3 | Reinforcement steel Supplying, Cutting, bending, binding, placing in position and tying reinforcement steel in all heights including cost and conveyance of steel and binding wire etc,. With all leads and lifts, labour charges, etc., complete for finished item of work. | Civil | Labour | SWR33144 | 70687 | Ton | 212061
14 | 38.36 | Brick masonry in cement mortar CM (1:6) for superstructure using well burnt country made second class bricks of approved quality including cost and conveyance of all materials curing, scaffolding with all leads and lifts in all heights etc., complete for fin | Civil | Labour | SWR33068 | 8302 | m3 | 318464.72
15 | 2.7 | Plain Cement concrete PCC (1:2:4) using 20mm size well graded HBG metal for foundations, including cost, conveyance of all materials,labour all leads and lifts,consolidation and all operations, formwork as required, curing,etc. complete for finished item of work | Civil | Labour | SWR33030 | 6180 | m3 | 16686
16 | 606.06 | Plastering with CM 2 coats, 20 mm thick, base coat in CM (1:6), 16 mm thick and top coat in CM (1:4), 4mm thick with Dubara sponze finishing including cost of all materials, seigniorage charges, excluding conveyance charges of materials and including all operational, incidental and labour charges for mixing mortar, laying rendering smooth and thread lining, curing, rounding off junctions of wall and slab etc., complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33163 | 566 | m2 | 343029.96
17 | 349.515 | Painting with two coats of Plastic Emulsn paint over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33356 | 210 | m2 | 73398.15
18 | 200.85 | Painting with two coats of Surya Cem paint over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33329 | 85 | m2 | 17072.25
19 | 3 | Supply and Fixng of MS Name Board including cost & conveyance of all materials,labour charges etc complete for finished item of work. | Civil | Labour | SWR33421 | 4326 | m2 | 12978
20 | 1 | Geophysical Investgation charges for water point by Geologist | Civil | Labour | SWR33608 | 5000 | EA | 5000
21 |  | Drilling of 165mm bore well with machine rig including deployment and hire charges of rig and other machinery and equipment labour charges , measuring the yeild of borewell including cost and conveyance etc complete
22 | 90 | Drill-165mm Bore Well 0M to 90M | Civil | Labour | SWR33609 | 336 | M | 30240
23 | 30 | Drill-165mm Bore Well 90M to 120M | Civil | Labour | SWR34830 | 369 | M | 11070
24 | 30 | Drill-165mm Bore Well 120M to 150M | Civil | Labour | SWR34831 | 394 | M | 11820
25 | 30 | Drill-165mm Bore Well 150M to 180M | Civil | Labour | SWR34832 | 492 | M | 14760
26 | 30 | Drill-165mm Bore Well 180M to 210M | Civil | Labour | SWR34833 | 623 | M | 18690
27 | 30 | Drill-165mm Bore Well 210M to 240M | Civil | Labour | SWR34834 | 754 | M | 22620
28 | 30 | Drill-165mm Bore Well 240M to 270M | Civil | Labour | SWR34835 | 918 | M | 27540
29 | 80 | Drill-165mm Bore Well 270M and above | Civil | Labour | SWR34836 | 1082 | M | 86560
30 | 40 | Supply and fixing of 160mm dia PVC casing of A class 6Kg point pressure including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR33611 | 883 | M | 35320
31 | 1 | Supply and erecting, ISI mark submersible 5.0 HP, Single Phase 30 stages pumpset suitable for 106/156mm dia borewell including cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33640 | 48007 | EA | 48007
32 | 285 | Supply and fixing of HDPE pipe 40mm dia of 16Kg/cm2 including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR34410 | 180 | M | 51300
33 | 1 | Supply and erecting D.O.L Starter 415V , Single phase,50Hz with SS enclouserincluding cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33645 | 7854 | EA | 7854
34 | 290 | Supply of 3 Core 2.5 Sqmm Flat Copper cable of ISI for Submersible Motors of makes Finolex / Polycab / Gold Medal / Million / Payal / Sun Light / Power Flex / Fortune Art | Civil | Labour | SWR33641 | 192 | m | 55680
35 | 71 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-28.60mm OD Pipe - SDR 11 | Civil | Labour | SWR34363 | 410 | m | 29110
36 | 35 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type - 25mm NB Size | Civil | Labour | SWR34346 | 466 | EA | 16310
37 | 839.38 | Supplying and filling the substation site with borrowed gravel, watering, ramming, thoroughly complying with the standard specification. | Civil | Labour | SWR33052 | 309 | m3 | 259368.42
38 | 16.56 | Providing Design R.C.M. drop wall of 25mm thickness with cm 1:3 and 6mm dia MS bars at 150mm both ways and chicken mesh in two coats 20mm thick each plastering including cost and conveyance of all materials with leads and lifts, scaffolding and curing, labo | Civil | Labour | SWR33203 | 3141 | m2 | 52014.96
39 | 12.24 | Supply and fixing of Ms ornamental safety grill of approved design including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33310 | 2990 | m2 | 36597.6
40 | 5.91 | Supply and fixing of doors with the MT Wood frames of the door shall be made well seasoned mt wood of cross section 100x75mm. The shutter shall be made isi mark flushed door with decolam sheets pasted on both sides with PVC beading 40mm width all round.Frame shall be painted with two coats of synthetic enamel paint of approved color over one coat of primer over luppum with spary with 3 no 150mm brass hinges 1 no brass door stoper, 1 no 250mm brass aldrops. 2 no 300 mm aluminium tower bolts, 2 no 150mm brass fancy door handlers, 1 no keyless lockset with cp handel. The quoted rate shall include cost and conveyance of the meterials, fixig, labour carges, tools, handles,locking arrangementts and other fixtures & fittings for finished item work as directed by the Engineer - in- charge. | Civil | Labour | SWR33264 | 7314 | m2 | 43225.74
41 | 128.25 | Raised pointing to the exposed surfaces of CRS masonry in cm 1:3 prop. including cost and conveyance of all materials, labour charges, all leads and lifts curing etc, complete for finished item of work. | Civil | Labour | SWR33184 | 126 | m2 | 16159.5
42 | 8.64 | Supplying and fixing Aluminium sliding windows with grill and fixed glass panels using anodised aluminium extruded sections of mat finish for frames and mullions made from approved aluminium sections 62x32x1.2mm at 0.73kg/Rm providing 5mm plain glass fix | Civil | Labour | SWR33277 | 3623 | m2 | 31302.72
43 | 16.56 | Supply and laying of Ceramic floor over of CM 1:3 20 mm thick including required materials and labour charges etc complete for item of work | Civil | Labour | SWR33224 | 914 | m2 | 15135.84
44 | 121.92 | Flooring with double machine polished and hand cut Tandur blue stone 20mm thick of approved colour, quality and of minimum of 300x300mm size over a bed of cement mortar 1:3 20mm thick including cost of all materials, with all leads and lifts jointing and | Civil | Labour | SWR33219 | 789 | m2 | 96194.88
45 | 6.74 | Supply and fixing of 4" high skirting of shabad stone to the walls including cost and conveyance of all materials, labour etc for finished item of work. | Civil | Labour | SWR33236 | 878 | m2 | 5917.72
46 | 243.69 | Painting with two coats of OBD over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials labour charges etc., complete for finished item of work. | Civil | Labour | SWR33333 | 146 | m2 | 35578.74
47 | 101.17 | Providing impervious coat over RCC roof slab to requried slopes with 20mm thick in CM 1:3 mixed with approved brand of water proffing compound inclding cost and conveyance of all materials, labour charges, curing, rounding off junctions of wall and slab, all leads and lifts, etc . complete for finished item of work as directed by the Engineer - in - charge. | Civil | Labour | SWR33156 | 588 | m2 | 59487.96
48 | 60 | Supply & fixing of 25mm dia 2mm thick suSupply & fixing of 25mm dia 2mm thick surface P.V.C. pipe (ISI MARK) Concealed in wall with all required accessories including masonary work and labour charges etc.complete. | Civil | Labour | SWR33441 | 108 | m | 6480
49 | 1 | Supply & fixing TPN Distribution board w Supply & fixing TPN Distribution board with IP-42 protection (Metal Door)suitable for 3 phase ELCB/RCCB/FP Isolator as incomer and 10kA SP MCBs as out going including internal connection and labour charges for surface / flush mounting etc Complete. | Civil | Labour | SWR33526 | 11353 | EA | 11353
50 | 10 | Supply & fixing of 6A 3 pin wall plug socket with 6A switch control on a common switch board with earth continuity including wire leads,earth connection along with all labour charges etc., complete | Civil | Labour | SWR33468 | 166 | EA | 1660
51 | 6 | Supply & fixing of 16A 3 pin and 6A 3pin plug Flush type socket with indicator lamp and 16Amps fuse unit and 16Amps switch control (5 in one )duly recessed in wall with wooden deep box of 6'' x 8'' x 2 1/2'' size covered with hylam sheet earth connection and all labour charges etc., complete on wall. | Civil | Labour | SWR33470 | 449 | EA | 2694
52 | 24 | Supply and Fixing of modular switch, LP,FP,EFP Wiring with 2 runs of 14/0.3mm (1.0 sq.mm)Fire Retardant (FR) P.V.C. insulated flexible copper cable (ISI MARK) in existing pipe with 6A Flush type Switch,ceiling rose and 3mm thick hylam sheet covering to switch control box including all labour charges etc., complete for light points, bell , fan and exhaust fan points in Non-Residential Buildings. | Civil | Labour | SWR33457 | 676 | EA | 16224
53 | 12 | Supply & Fixing of 28W T5 fluorescent tube. | Civil | Labour | SWR33558 | 148 | EA | 1776
54 | 1 | Supply of 12" (300mm)ISI, 900 RPM Heavy duty exhaust fan with metallic blades with Mark of makes Crompton / Bajaj / Havells / Orient. | Civil | Labour | SWR33571 | 2192 | EA | 2192
55 | 180 | Supply and run of 2 of 22/0.3mm (1.5 sq.mm) (FR) P.V.C. insulated flexible copper cable in existing pipe for mains including all labour charges complete. | Civil | Labour | SWR33496 | 75 | m | 13500
56 | 180 | Supply and run of 2 of 36/0.3mm (2.5 sq.mm) FR P.V.C. insulated flexible copper cable in existing pipe for mains including all labour charges complete. | Civil | Labour | SWR33497 | 103 | m | 18540
57 | 12 | Supply & fixing of batten holder /slanting holder in lieu of ceiling rose of light point complete with all connection and all labour charges with 40W bulb (for new installation). | Civil | Labour | SWR33484 | 141 | EA | 1692
58 | 4 | Supply & fixing of 1200mm (48'') sweep 230v,A.C 50 Hz.Ceiling fan with 3 Blades and double ball bearings with all standared accessories. | Civil | Labour | SWR33563 | 2277 | EA | 9108
59 | 4 | Supply & fixing of Electronic Regulator for ceiling fans 900/1200/1400mm sweep including cost of material, Electrical charges complete for finished item of work | Civil | Labour | SWR33564 | 589 | EA | 2356
60 | 1 | Providing independent EARTHING by excavating a trench to a depth of 2.1M in all solid,as per size specified in the Data,using 40mm dia 'B' class GI pipe of 2.5 Mtrs length with necessary accessories with hume pipe ring duly providing staggered holes including filling with equal proportion of salt and Charcoal in layers and all labour charges etc., compiete for small quarters. | Civil | Labour | SWR33596 | 5345 | EA | 5345
61 | 35 | Supplying, laying, jointing and testing 101.6 mm SWG SP-1 pipes of ISI make conforming to ISI 651 & 4127 with airtight cement joints in CM 1.5:1 prop. Including excavation of trenches and socket pits in any soil (except rock requiring blasting) up to 1524 mm(5'0") depth and refilling with watering and tamping. | Civil | Labour | SWR34281 | 755 | m | 26425
62 | 3 | Constructing 904.0 mm (3#0#) dia brick masonry inspection chamber as per IS - 4111: Part-1:1986 with cement mortar (1:6) prop using 2nd Class Clay Bricks of 225 mm thick from approved source having a minimum crushing strength of 5 N/sq.mm including plastering with cement mortar 1:3 prop; ½# thick both inside and outside fitted with 20# dia RCC manhole covers and frames including excavating pits up to a depth of 904 mm (3'-0") in all sorts of soils (excluding rock) and laying cement concrete (1:4:8) 150 mm thick using 40 mm HBG Metal and P.C.C. 1:2:4 benching and channel 100 mm thick as per Standard specification and including cost and conveyance of all materials like cement, sand, bricks, water etc., to site, cost of seigniorage charges on all materials and all incidental and operational, labour charges like mixing cement mortar, constructing masonry, lift charges, curing etc., complete for finished item of work as per Standard specification. | Civil | Labour | SWR34296 | 8766 | EA | 26298
63 | 4 | Supply & fixing of 110 mm dia - Door Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34381 | 128 | EA | 512
64 | 4 | Supply & fixing of 110 mm dia - Plain Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34380 | 100 | EA | 400
65 | 12 | Supply & fixing of 110 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand | Civil | Labour | SWR34377 | 462 | m | 5544
66 | 18 | Supply & fixing of 90 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand | Civil | Labour | SWR34378 | 410 | m | 7380
67 | 3 | Supplying & fixing 150 mm x 100 mm SWG gully traps conforming to ISI 651 & 4127 with C.I Grating & Cost. Brick masonry in CM 1:6 prop. Intermediate chamber and fitted with 304.8 mm x 288.6mm (12"x9") C.I Frame and hinged cover | Civil | Labour | SWR34286 | 767 | EA | 2301
68 | 1 | Supplying and Fixing of European Water Closet of 1st Quality | Civil | Labour | SWR34312 | 2228 | EA | 2228
69 | 6 | Supply & fixing 15 mm angle stop cock Indian make 400 grams Seiko/ Senior/ Nice/ Senior/ Nice or equivalent | Civil | Labour | SWR34328 | 721 | EA | 4326
70 | 4 | S&F 15 mm N.P bib tap Indian make 400 grams full turn Seiko/ Senior/ Nice or equivalent | Civil | Labour | SWR34329 | 296 | EA | 1184
71 | 1 | Supplying & Fixing Indian make Flat Back Wash Hand Basin (HSW/Parryware/ Neycer) 1st quality conforming to IS:2556-Part-4:1972 with waste fittings like rubber plug, chain, 32 mm nominal size C.P. Fitting with parallel pipe thread conforming to IS:2963-1979 and fitted with 15 mm nominal bore Chromium Plated Pillar Tap of 1st quality Indian make 400 grams Seiko/ Senior/ Nice/ Esso or equivalent complete with standard CI brackets including wooden block: 550 x 400 mm - Single C.P. Pillar cock | Civil | Labour | SWR34316 | 1717 | EA | 1717
72 | 2 | Supply & fixing 38.1 mm C.P waste coupling Half or Full Thread 1st Quality Indian make Parryware or equivalent | Civil | Labour | SWR34428 | 309 | EA | 618
73 | 2 | Supply & fixing of 4" (101.6 mm ) Nahany Trap ( Without Jali with inlet)UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34387 | 134 | EA | 268
74 | 1000 | Providing & Placing on Terrace (at all floor levels) polyethylene water storage tank with Double layer approved brand & manufacture with cover and suitable locking arrangement & making necessary holes for inlet & outlets and over flow pipes but with NECESSARY fittings & base support for tanks | Civil | Labour | SWR34375 | 10 | L | 10000
75 | 2 | Supply & fixing 31.75 mm dia PVC flexible waste pipe of 914.4 mm length of Ist quality | Civil | Labour | SWR34426 | 33 | EA | 66
76 | 45 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)- 15.90mm OD Pipe - SDR 11 | Civil | Labour | SWR34361 | 239 | m | 10755
77 | 200 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-22.20mm OD Pipe - SDR 11 | Civil | Labour | SWR34362 | 313 | m | 62600
78 | 4 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type -20mm NB Size | Civil | Labour | SWR34345 | 331 | EA | 1324
79 | 1 | Supply & fixing 25.4 mm dia & 609.6 mm long aluminium anodized towel rod with brackets and aluminium screws | Civil | Labour | SWR34430 | 489 | EA | 489
80 | 36 | Plain Cement concrete PCC (1:3:6) using 40mm HBG metal for foundations and leveling course, including cost and conveyance of all materials, labour all leads and lifts, consolidation and all operations, formwork as required, curing, etc. complete for finished item w | Civil | Labour | SWR33029 | 5101 | m3 | 183636
81 | 120 | Supply&Fabrication and fixing of Welded wire mesh ( 2" x 2") of 3mm dia. with ISMC (75x40x4.4mm) and Pheriperal frame of ISA(35x35x3mm) incldg cost& conveyance painting with synthetic enamil paint two coats over a coat of red oxide primer etc complete for finished item of work.. | Civil | Labour | SWR33403 | 2310 | m2 | 277200
82 | 1 | Providing Consultancy services for arranging contour surveying with total station incuding preparation of boundary and contour levels with 2 Nos. Hard copies and soft copies complete for finished items of work | Civil | Labour | SWR33427 | 5665 | EA | 5665
83 | 222.2468 | Seigniorage Charges - Sand | Civil | Labour | SWR34470 | 40 | m3 | 8889.873
84 | 725.7496 | Seigniorage Charges - Metal | Civil | Labour | SWR34471 | 97.5 | m3 | 70760.585
85 | 839.38 | Seigniorage Charges - Gravel | Civil | Labour | SWR34472 | 30 | m3 | 25181.4
86 | 60 | Supply and fixing of RCC fencing poles of size 0.1mx0.1mx1.8m (security fencing of sub station), including cost and conveyance of all labour, materials,and hire chareges etc complete for finished item of work. | Civil | Labour | Swr33405 | 1444 | EA | 86640
| 1200 | Supply and fixing of galvanised barded wire (1 horizantal & 2 cross strands. including cost and conveyance of all labour, materials,and hire chareges etc complete for finished item of work. | Civil | Labour | Swr33408 | 16 | m | 19200
Total Rs. | [7 empty] | 4231786.512
Grand Total without GST Rs. | [7 empty] | 19034008.067

## 9. Nallagandla Huda
Name of the work: Revision estimate for "Erection of new 33/11kV Outdoor substation with 2x12.5MVA PTRs and also Construction of Control room, and other Civil works at Nallagandla HUDA in Nallagandla section of operation Gachibowli division in cybercity circle, in Master plan Sub-division 1 of WCGH Division in Rangareddy circle under T&D improvement works."
1.D.No :San no: 132, D no: 1352, Dt. 09-11-2024
2. WBS No. Supply 1798-13-04-01-01-001
Sl.No | Estimate Quantity(Only Figures) | PARTICULARS | Work Type | Item Short Description | SWR No/APSS/Morth cl.No | Rate (INR) (Upto 2 Decimals) | UOM | Amount
1 | 8 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") Exca Hard pit w/o blast 0.76X0.76X1.83M | Elecy | labour | SWR11039 | 928 | EA | 7424
2 | 8 | Excavation of pits in hard rock requiring blasting. (other than SS) 9.1Mtrs PSCC Pole 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") EXCAV. OF PIT HARD(2.6" x 2.6" x 6.0") | Elecy | labour | SWR10112 | 1770 | EA | 14160
3 | 5.76 | Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RSupply Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. Fabrication of struc.with power drilling | Elecy | labour | SWR10868 | 6852 | TO | 39467.52
4 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | Elecy | supply | SMR40009 | 2181 | TO | 12562.56
5 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | Elecy | labour | SWR10877 | 851 | TO | 4901.76
6 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | Elecy | supply | SMR40010 | 1293 | TO | 7447.68
7 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | Elecy | labour | SWR10879 | 482 | TO | 2776.32
8 | 5.76 | Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | Elecy | labour | SWR10867 | 1470 | TO | 8467.2
9 | 16 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. Erection of RS Joist 150 x 150 mm | Elecy | labour | SWR10348 | 1952.61 | EA | 31241.76
10 | 17.758 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | Elecy | labour | SWR10356 | 6579 | M3 | 116829.882
11 | 9.24 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | Elecy | labour | SWR10862 | 373 | M2 | 3446.52
12 | 16 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | Elecy | labour | SWR11089 | 48 | EA | 768
13 | 5.063 | Fabrication & erection of Channels Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RSupply Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. Fabrication of struc.with power drilling | Elecy | labour | SWR10868 | 6852 | TO | 34691.676
14 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | Elecy | supply | SMR40009 | 2181 | TO | 11042.403
15 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium. Labour for 1st coat Al. Painting. | Elecy | labour | SWR10877 | 851 | TO | 4308.613
16 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | Elecy | supply | SMR40010 | 1293 | TO | 6546.459
17 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | Elecy | labour | SWR10879 | 482 | TO | 2440.366
18 | 5.063 | Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | Elecy | labour | SWR10867 | 1470 | TO | 7442.61
19 | 13 | Erection of AB Switch and aligment complete Erection of 33 KV AB Switch including alignment and earthing | Elecy | labour | SWR10392 | 4500 | EA | 58500
20 | 38 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Note:-The requirement of 2nd coat is to be justified by the concerned Divisional Engineer /Executive Engineer before execution of this work Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elecy | labour | SWR10881 | 142 | EA | 5396
21 | 38 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch AB Switch Coil Earthing GI No. 8 Wire | Elecy | labour | SWR12331 | 146.63 | EA | 5571.94
22 | 6 | Loading of 33 KV CTs/ PTs | Elecy | labour | SWR10200 | 165 | EA | 990
23 | 6 | Un loading of 33 KV CTs/ PTs | Elecy | labour | SWR10518 | 128 | EA | 768
24 | 2 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33kv single phase PT s | Elecy | labour | SWR10401 | 1079 | SET | 2158
25 | 12 | Loading of 33 KV, 10 KA LAs Station type | Elecy | labour | SWR10266 | 41 | EA | 492
26 | 12 | Un loading of 33 KV, 10 KA LAs Station type | Elecy | labour | SWR10584 | 35 | EA | 420
27 | 4 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33 KV LAS station/Line type including earthing | Elecy | labour | SWR10396 | 880 | SET | 3520
28 | 2 | Loading of 33 KV VCBs along with Panel boards | Elecy | labour | SWR10198 | 1024 | EA | 2048
29 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Above 10 Km and upto 20 Km with Lorry for each trip Transport of Cond Drum,VCBs >10 & <20Km | Elecy | labour | SWR11861 | 3299.7 | EA | 3299.7
30 | 2 | Un loading of 33 KV VCBs along with Panel boards | Elecy | labour | SWR10516 | 1044.48 | EA | 2088.96
31 | 12.58 | Excavate-Pit for 33KV VCB | Elecy | labour | SWR23224 | 331 | M3 | 4163.98
32 | 14.52 | Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x 1.8 x 0.75 cum for VCB Plinth | Elecy | labour | SWR20685 | 5160 | M3 | 74923.2
33 | 2 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33 KV VCB with Control Panel | Elecy | labour | SWR10460 | 12500 | EA | 25000
34 | 2 | Loading and unloading of PTR on constructed plinth LOADING of 12.5 MVA PTR | Elecy | labour | SWR10614 | 12044.93 | EA | 24089.86
35 | 2 | Transport of Power transformers (0 to 100 KM) from one place to another place in GHMC Area.(excluding of loading & unloading ) Transport of 12.5MVA power transformer | Elecy | labour | SWR10855 | 27431 | EA | 54862
36 | 2 | UNLOADING of 12.5 MVA PTR | Elecy | labour | SWR10628 | 12044.93 | EA | 24089.86
37 | 700 | S/o rail poles 90/105lb (250x2N) | Elecy | supply | SMR22718 | 47.27 | KG | 33089
38 | 4 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Erection of Rail Pole 90Lbs | Elecy | labour | SWR10344 | 3510 | EA | 14040
39 | 2 | Erection of PTR on constructed plinth Erection of 12.5 MVA PTR. | Elecy | labour | SWR10929 | 51818 | EA | 103636
40 | 0.44 | Extention of 33KV Bay at 132/33KV Sub-station 33KV Bay Extn: Supply Zebra Conductor | Elecy | supply | SMR24910 | 299369 | KM | 131722.36
41 | 30 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing. | Elecy | supply | SMR11915 | 2055 | SET | 61650
42 | 30 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of I-Bolts | Elecy | supply | SMR22473 | 294 | EA | 8820
43 | 45 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 "to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating . Sup T clamp LM6 Al alloy of 12 mm, 800 A | Elecy | supply | SMR40011 | 299 | EA | 13455
44 | 6 | Bus stringing Hoisting of Insulators and hardware, stretching the conductor and stringing of 33 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bussection of 4.5mt) Hoisting post ins&hrd wr 1panther 33kv | Elecy | labour | SWR21240 | 781 | EA | 4686
45 | 218.67 | Stringing of bus with panther conductor including jumpering etc., complete to all the equipment in SS fixing to all clamps and equipment.(3 Conductors) Stringing of bus with panther conductor | Elecy | labour | SWR10404 | 327.68 | M | 71653.7856
46 | 30 | Bus stringing Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | Elecy | labour | SWR10884 | 224 | EA | 6720
47 | 75 | Labour for Fixing of all types of clamps | Elecy | labour | SWR10917 | 65 | EA | 4875
48 | 29 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Elecy | labour | SWR11039 | 928 | EA | 26912
49 | 10.12 | Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RSupply Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. Fabrication of struc.with power drilling | Elecy | labour | SWR10868 | 6852 | TO | 69342.24
50 | 10.12 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | Elecy | supply | SMR40009 | 2181 | TO | 22071.72
51 | 10.12 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | Elecy | labour | SWR10877 | 851 | TO | 8612.12
52 | 10.12 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | Elecy | supply | SMR40010 | 1293 | TO | 13085.16
53 | 10.12 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | Elecy | labour | SWR10879 | 482 | TO | 4877.84
54 | 10.12 | Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | Elecy | labour | SWR10867 | 1470 | TO | 14876.4
55 | 29 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Erection of RS Joist 150 x 150 mm | Elecy | labour | SWR10348 | 1952.61 | EA | 56625.69
56 | 32.19 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Mass concreting of supports incl. cement | Elecy | labour | SWR10356 | 6579 | M3 | 211778.01
57 | 16.75 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | Elecy | labour | SWR10862 | 373 | M2 | 6247.75
58 | 29 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. Ptg of coping with 2cts white cmnt inclu | Elecy | labour | SWR11089 | 48 | EA | 1392
59 | 5.588 | Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RSupply Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. Fabrication of struc.with power drilling | Elecy | labour | SWR10868 | 6852 | TO | 38288.976
60 | 5.588 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters ofthinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes,labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | Elecy | Supply | SMR40009 | 2181 | TO | 12187.428
61 | 5.588 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | Elecy | labour | SWR10877 | 851 | TO | 4755.388
62 | 5.588 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | Elecy | Supply | SMR40010 | 1293 | TO | 7225.284
63 | 5.588 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | Elecy | labour | SWR10879 | 482 | TO | 2693.416
64 | 5.588 | Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | Elecy | labour | SWR10867 | 1470 | TO | 8214.36
65 | 21 | Erection of 11KV 800A double throw AB Switches | Elecy | labour | SWR21277 | 3500 | EA | 73500
66 | 3 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Elecy | labour | SWR10393 | 3200 | EA | 9600
67 | 2 | Loading of 11 KV CT - PT Sets | Elecy | labour | SWR10201 | 190 | EA | 380
68 | 2 | Un loading of 11 KV CT - PT Sets | Elecy | labour | SWR10519 | 101 | EA | 202
69 | 2 | Erection of 11 KV three phase PTs | Elecy | labour | SWR10402 | 800 | SET | 1600
70 | 30 | Loading of 11 KV, 10 KA LAs Station type | Elecy | labour | SWR10264 | 32 | EA | 960
71 | 30 | Un Loading of 11 KV, 10 KA LAs Station type | Elecy | labour | SWR10582 | 32 | EA | 960
72 | 2 | Erection of 11 KV LAS station type including earthing | Elecy | labour | SWR10397 | 559 | SET | 1118
73 | 8 | Erection of 11 KV LAS line type including earthing | Elecy | labour | SWR10398 | 505 | SET | 4040
74 | 10 | Loading of 11 KV VCBs along with Panel boards | Elecy | labour | SWR10199 | 1024 | EA | 10240
75 | 5 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Transport of Cond Drum,VCBs >10 & <20Km | Elecy | labour | SWR11861 | 3299.7 | EA | 16498.5
76 | 10 | Un Loading of 11 KV VCBs along with Panel boards | Elecy | labour | SWR10517 | 1044.48 | EA | 10444.8
77 | 52 | Excavate-Pit for 33KV VCB | Elecy | labour | SWR23224 | 331 | M3 | 17212
78 | 60 | Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x 1.8 x 0.75 cum for VCB Plinth | Elecy | labour | SWR20685 | 5160 | M3 | 309600
79 | 10 | Erection of 11 KV VCB with Control Panel | Elecy | labour | SWR10461 | 12000 | EA | 120000
80 | 12 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing. | Elecy | Supply | SMR11915 | 2055 | SET | 24660
81 | 12 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367- 1961) Supply of I-Bolts | Elecy | Supply | SMR22473 | 294 | EA | 3528
82 | 45 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367- 1961) Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 " to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating . Sup T clamp LM6 Al alloy of 12 mm, 800 A | Elecy | Supply | SMR40011 | 299 | EA | 13455
83 | 2 | Bus Stringing Hoisting of Insulators and hardware, stretching the conductor and stringing of 11 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 3.5mt) Hoisting post ins&hrd wr 1panther 11kv | Elecy | labour | SWR21241 | 507 | EA | 1014
84 | 45 | Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | Elecy | labour | SWR10884 | 224 | EA | 10080
85 | 57 | Labour for Fixing of all types of clamps | Elecy | labour | SWR10917 | 65 | EA | 3705
86 | 696 | Laying of earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication 75x 8mm MS Flat / GI Flat. Laying of earth mat,excavation 75x 8mm | Elecy | labour | SWR10920 | 65 | RMT | 45240
87 | 1247 | Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) Earthing for raisers of SS Flat 50x6 mm. | Elecy | labour | SWR10919 | 41 | RMT | 51127
88 | 36 | Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Elecy | Supply | SMR11482 | 3486 | EA | 125496
89 | 36 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elecy | labour | SWR10357 | 1234.2 | EA | 44431.2
90 | 36 | Providing of RCC collar to earth pit Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINESupply Providing of RCC collar | Elecy | labour | SWR10359 | 386 | EA | 13896
91 | 2 | Supply of Copper Flexible jumper with 75 X 8 of length 250 mm at neutral of Power tranformer end and 50 X 6 of length 50mm two Nos at double neutral end duly brasing with flexible jumper of capacity of 5kA/3 sec for power transformer neutral. SupCU Flexi jumper for Power T/F Neutral | Elecy | Supply | SMR40033 | 4725 | EA | 9450
92 | 2 | Providing of double earthing for neutral with flexible copper jumpers including arrangement by fixing M.S.Channel 100x50mm. | Elecy | labour | SWR11892 | 1323 | EA | 2646
93 | 4 | Loading of LT AB Cable 3X16+25 Sqmm | Elecy | labour | SWR11702 | 200 | DR | 800
94 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Transport of Cond Drum,VCBs>10 & <20Km | Elecy | labour | SWR11861 | 3299.7 | EA | 3299.7
95 | 4 | Un loading of LT AB Cable 3X16+25 Sqmm Drum | Elecy | labour | SWR11713 | 204 | DR | 816
96 | 90 | Providing of control cable trench as per DATA-XII | Elecy | labour | SWR22093 | 3148 | RMT | 283320
97 | 3312 | Control Cable Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends . Lay-4C/10C 2.5Sqmm Control Cable | Elecy | labour | SWR11879 | 27 | M | 89424
98 | 270 | Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per specification (including cost of ferrules, lugs and glands) L-Cable Termination to Switchgear | Elecy | labour | SWR12510 | 27 | EA | 7290
99 | 4 | Supply of FRP PT Marshalling Box | Elecy | Supply | SMR40048 | 4463 | EA | 17852
100 | 4 | Erection of Marshalling boxes | Elecy | labour | SWR10940 | 374.85 | EA | 1499.4
101 | 1 | Loading of 220 V Batterry with charger | Elecy | labour | SWR11166 | 1612 | SET | 1612
102 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Transport of Cond Drum,VCBs>10 & <20Km | Elecy | labour | SWR11861 | 3299.7 | EA | 3299.7
103 | 1 | Un loading of 220 V Batterry with charger | Elecy | labour | SWR11147 | 1024 | SET | 1024
104 | 1 | Erection of 220 V, 80 AH battery in complete shape fit for charging . Conventional lead acid | Elecy | labour | swr12295 | 7666 | EA | 7666
105 | 1 | Control Panels Supply of DC Annunciation & relay panel for 10 feeder panel including the cost of LED Indiacation lamps, VAA auxilairy relays, Electronic Hooters complete as per specification. Supply of DC Anunc.relay panel 8 feeders | Elecy | Supply | SMR40044 | 42500 | EA | 42500
106 | 1 | Supply of AC Supply panel inluding providing of changeover switch, SFU, metering unit, 32 A three phase MCB, 16 A Single phase MCB complete as per specification. Supply of AC Supply panel complete | Elecy | Supply | SMR40045 | 42000 | EA | 42000
107 | 8 | Supply of stepped tubular poles single way made of steel of length 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9 mm, 2.1 mtrs with outer dia 76.1 mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79 kgf as per IS 2713. Supply 9mtrs tubular poles single way | Elecy | Supply | SMR40051 | 13913 | EA | 111304
108 | 8 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE/CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA /OSRAM /SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty Supply 90W LED fixture set | Elecy | Supply | SMR11594 | 8200 | EA | 65600
109 | 8 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") Exca Hard pit w/o blast 0.76X0.76X1.83M | Elecy | labour | SWR11039 | 928 | EA | 7424
110 | 8 | Erection of tubular poles | Elecy | labour | SWR10955 | 1379 | EA | 11032
111 | 5.27 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Mass concreting of supports incl. cement | Elecy | labour | SWR10356 | 6579 | M3 | 34671.33
112 | 8 | Fixing of LED/Metal halide complete. | Elecy | labour | SWR10956 | 1268 | EA | 10144
113 | 45 | Supply & spreading of 20mm machine crushed metal (HBG) including cost of conveneyance of all materials, labour charges etc complete for finished item of work and directed by the engineer incharge Supply & Spreading of 20mm HBG metal | Elecy | labour | SWR10860 | 2113 | M3 | 95085
114 | 2 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M Ex of Hard pit w/o blast 0.75X0.9X1.95M | Elecy | labour | SWR11040 | 990.68 | EA | 1981.36
115 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete . Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | Elecy | Supply | SMR40009 | 2181 | TO | 1635.75
116 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | Elecy | labour | SWR10877 | 851 | TO | 638.25
117 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. (*)Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | Elecy | Supply | SMR40010 | 1293 | TO | 969.75
118 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. (*) Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium Labour for 2nd coat Al. Painting. | Elecy | labour | SWR10879 | 482 | TO | 361.5
119 | 1 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Erect-12Meter Box pole | Elecy | labour | SWR11267 | 3901.37 | EA | 3901.37
120 | 2.22 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc Mass concreting of supports incl. cement | Elecy | labour | SWR10356 | 6579 | M3 | 14605.38
121 | 1.16 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | Elecy | labour | SWR10862 | 373 | M2 | 432.68
122 | 2 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. Ptg of coping with 2cts white cmnt inclu | Elecy | labour | SWR11089 | 48 | EA | 96
123 | 1 | Construction of DTR Plinth RCC Column type DTR Plinth of size 1'X1'X10',topslab 4'x4'x6" & beam size 4'X8'X8" upto 160KVA Column type DTR Plinth topslab 4'x4'x6" | Elecy | labour | SWR21843 | 25967.57 | EA | 25967.57
124 | 1 | LOADING of 50,63,75&100kva DTR | Elecy | labour | SWR10195 | 350 | EA | 350
125 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Transport of Cond Drum,VCBs>10 & <20Km | Elecy | labour | SWR11861 | 3299.7 | EA | 3299.7
126 | 1 | UNLOADING of 50,63,75&100kva DTR | Elecy | labour | SWR10513 | 280 | EA | 280
127 | 1 | Erection of DTR's including loading and Unloading DTR on the Structure/Plinth etc Erection of 3 Phase DTRs 63,75 & 100 KVA E/r 3ph DTR inclu L&Un-L,T&C on plinth | Elecy | labour | SWR20905 | 1650 | EA | 1650
128 | 1 | Erection of AB Switch and aligment complete Erection of 11KV 200A TT type AB Switch including fixing of cross angles and alignment complete | Elecy | labour | SWR20102 | 1813.49 | EA | 1813.49
129 | 1 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erect. of 11kv HG Fuseset incl earthing | Elecy | labour | SWR10395 | 740.52 | SET | 740.52
130 | 40 | Excavation & laying of UG Cable in Single Run Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders /Normal soil / CC/BT Road Lay-SR 11KV 3x185sqmm UG Cb HG/BC/CC/BT | Elecy | labour | SWR11920 | 465.46 | M | 18618.4
131 | 20 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) Raise-SR 11KV 3x185sqmm UG Cb on support | Elecy | labour | SWR11956 | 126.23 | M | 2524.6
132 | 2 | UG Cables Joints Making of Outdoor/Indoor End Termination OD/Idoor end termination 11kv 3x185 xlpe | Elecy | labour | SWR10390 | 2370.63 | EA | 4741.26
133 | 1 | Erection of LT distribution box including laying of LT cable from distribution box to LT OH line and DTR to distribution box including earthing of distribution box and crimping of lugs connecting of jumpers etc Erection of LT distribution box | Elecy | labour | SWR10674 | 1594.67 | EA | 1594.67
134 | 85 | Excavation & laying of UG Cable in Single Run Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road Lay-SR LT 3.5x95sqmm UG Cb HG/BC/CC/BT | Elecy | labour | swr11925 | 377.63 | M | 32098.55
135 | 15 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) Raise-SR LT 3.5x95sqmm UG CB ON SUPPORT | Elecy | labour | SWR11961 | 85.43 | M | 1281.45
136 | 2 | UG Cables Joints Making of Outdoor/Indoor End Termination Sup of 31/2x185Sqmm UG O/D end term kits | Elecy | supply | SMR40140 | 550 | EA | 1100
137 | 2 | UG Cables Joints Making of Outdoor/Indoor End Termination Fixing of Out Door/Indoor end termination LT 3 1/2 x185 Sqmm Cable OD/Idoor end termination LT 3 1/2 x 185 | Elecy | labour | SWR10765 | 968.9 | EA | 1937.8
138 | 1 | Supply and fixing of Substation board of size 3'x2.5' indicating the layout of switchyard Sup &fix of board ind Switchyard layout | Elecy | labour | SWR20032 | 1654 | EA | 1654
139 | 1 | Supply and fixing of safety instructions/Substation operation instruction board. Sup& fix safety inst/SS Op. inst board | Elecy | labour | SWR22090 | 2205 | EA | 2205
140 | 750 | Control Panels Supplying & fabrication erection of 6mm Checkerd plates as per the field conditions Supply,fabricati of 6mm Checkerd plates | Elecy | labour | SWR10873 | 83 | KG | 62250
141 | 1 | T & P Supply of Wall clock standard make | Elecy | Supply | SMR40059 | 578 | EA | 578
142 | 1 | Supply 10ft Aluminium Ladder | Elecy | supply | SMR12378 | 1654 | EA | 1654
143 | 1 | Sup Alluminium Ladder for indoor works | Elecy | Supply | SMR40062 | 4410 | EA | 4410
144 | 30 | T & P Painting of Name Plates for any equipmen | Elecy | labour | SWR10963 | 122 | EA | 3660
145 | 1 | T & P Supply of Taparia Tool kit of Size 20”x10”x15” with tier arrangements Tool box with locking arrangement & key containing (1) Double Ended fix Spanner sets, (Ribbed) 6 x 7, 8 x 9, 10 x 11, 12 x 13, 14 x 15, 16 x 17, 18 x19, 20 x 22, 21 x 23, 24 x 27, 25 x28, 30 x 32, (2) Double Ended Ring Spanners sets, 6 x 7 , 8 x 9, 10 x 11, 12 x 13, 14 x 15. 16 x 17 , 18 x 19, 20 x 22 , 21 x 23, 24 x 27, 25 x28, 30 x 32 mm, (3) Adjustable Spanner 305 mm length least maximum opening 35mm chrome, (4) Pipe Wrench Length 350 mm 14”, (5) Soft faced Hammer with suitable handle 2 lb, (6) Hacksaw frame with metal handle heavy duty for 12" hacksaw blade with High Speed blade, (7) Insulated Screw drivers Transparent Green Handle Set Length 6”, 8” & 12”, (8) Star Screw Driver Transparent Green Handle Length 6”, (9) Insulated Wire Cutter, (10) Insulated Cutting Plier Length 8” with cable stripper insulated with thick C. A. sleeve confirming to IS: 4378 - 1990, (11) Long Nose Plier insulated with thick C.A. sleeve generally confirming to IS:3552-1989, (12) Tester type screw driver (special with neon bulb) generally confirm to IS: 5579- 1985 Grade:II handle yellow/ green colour overall length 130 mm, (13) Insulated Crimping Plier of all Taparia make. SupTaparia Tool kit complete as per Spec | Elecy | supply | SMR40063 | 4925 | SET | 4925
146 | 1 | T & P Sup Rechargeable LED torch light of Standard make | Elecy | supply | SMR40064 | 1733 | EA | 1733
147 | 1 | T & P Sup Steel almarah(61/2 X 3ft) Godrej | Elecy | supply | SMR40061 | 9818 | EA | 9818
148 | 1 | T & P Supply of Table (3x6ft) Godrej | Elecy | supply | SMR40057 | 6050 | EA | 6050
149 | 4 | T & P Supply of S type chairs (Godrej) | Elecy | supply | SMR40058 | 924 | EA | 3696
150 | 1 | T & P Sup Angle racks(18x36.6inches) Godrej | Elecy | supply | SMR40060 | 1733 | EA | 1733
151 | 1 | T & P Supply of Hack saw (12 inches) | Elecy | supply | SMR40065 | 289 | EA | 289
152 | 4 | Sup Earth Rods (8ft) Screw & clamp type | Elecy | supply | SMR40066 | 578 | EA | 2312
153 | 2 | Supply of Hand Gloves | Elecy | supply | SMR40067 | 289 | SET | 578
154 | 12 | SupRubber mats( 6'x3')size fo indoorSS | Elecy | supply | SMR40068 | 1386 | EA | 16632
155 | 1 | Biometric Time attendence System & Telecom Sup Stand basic cell phone with charger | Elecy | supply | SMR40069 | 1386 | EA | 1386
156 | 14 | Supply of Danger boards with clamps | Elecy | supply | SMR40070 | 116 | EA | 1624
157 | 2 | Supply of Materials Fire bucket stand with 3 buckets (8 -10 ltr capacity) Sup Fire Buckets Stand with Buckets | Elecy | supply | SMR40088 | 1386 | SET | 2772
158 | 2 | Room fire extinguisher (2 ltrs capacity) for control room Sup Fire Extinguisher for Control Room | Elecy | supply | SMR40089 | 4620 | EA | 9240
159 | 4 | Sup TrollyMounted Co2 (6.5Kgs) Cylinders(ISupply 2878) | Elecy | supply | SMR40087 | 9240 | EA | 36960
160 | 6 | Supply of Safety Helmet of standard make | Elecy | supply | SMR40071 | 231 | EA | 1386
161 | 8 | Supply of LC Boards | Elecy | supply | SMR40072 | 116 | EA | 928
162 | 4 | Supply of Gum Boots (pair) | Elecy | supply | SMR40073 | 693 | EA | 2772
163 | 1 | Supply of 5000v megger | Elecy | supply | SMR40074 | 13860 | EA | 13860
164 | 1 | Supply of Earth megger (1000v) | Elecy | supply | SMR40075 | 8085 | EA | 8085
165 | 1 | Supply of Digital clamp meter. | Elecy | supply | SMR40076 | 2888 | EA | 2888
166 | 1 | Name board of the 33/11kV Sub-Station(As per Standard Specification) Sup 33/11kv S.S Permanent name board | Elecy | supply | SMR40086 | 10238 | EA | 10238
167 | 800 | Supply of Hot dip galvanized/zinc coated bolts & nuts including spring washers, pack washers and flat washers etc. Supply Hot dip gal./Zinc bolts & nuts washer | Elecy | supply | SMR12488 | 90 | KG | 72000
168 | 4 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rockboulders) 8.0Mtrs PSCC Poles 0.76 M x 0.76M x 1.52M (2.6" x 2.6" x 5.0') 0.88 cum Ex of Hard pit w/o blast 0.76X0.76X1.52M | Elecy | labour | SWR11037 | 793 | EA | 3172
169 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | Elecy | supply | SMR40009 | 2181 | TO | 2181
170 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., completeLabour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | Elecy | labour | SWR10877 | 851 | TO | 851
171 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete (*)Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | Elecy | supply | SMR40010 | 1293 | TO | 1293
172 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete (*) Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | Elecy | labour | SWR10879 | 482 | TO | 482
173 | 3.51 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Mass concreting of supports incl. cement | Elecy | labour | SWR10356 | 6579 | M3 | 23092.29
174 | 2.31 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | Elecy | labour | SWR10862 | 373 | M2 | 861.63
175 | 4 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. Ptg of coping with 2cts white cmnt inclu | Elecy | labour | SWR11089 | 48 | EA | 192
176 | 5 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Erection of RS Joists 150x75/175 x 85 mm | Elecy | labour | SWR10346 | 1934 | EA | 9670
177 | 2 | Fixing of AC/DC Panel and giving Connections to the protection equipment and Metering circuits as per the specification and standards. The 3 1/2 core 25 Sqmm power cable required from distribution box to AC/DC panel in the control room is also to be supply | Elecy | labour | SWR20025 | 7871.85 | SET | 15743.7
178 | 2 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Elecy | labour | SWR10642 | 512.55 | EA | 1025.1
179 | 5760 | Supply RS Joist Grider Pole (150x150mm) | Elecy | Supply | SMR12302 | 59.25 | KG | 341280
180 | 5063 | Supply MS Channel 100x50mm | Elecy | Supply | SMR22745 | 57.45 | KGS | 290869.35
181 | 13 | Supply 33KV 800A DB Break AB Switch | Elecy | Supply | SMR12315 | 40658.78 | EA | 528564.14
182 | 10120 | Supply RS Joist Grider Pole (150x150mm) | Elecy | Supply | SMR12302 | 59.25 | KG | 599610
183 | 5588 | Supply MS Channel 100x50mm | Elecy | Supply | SMR22745 | 57.45 | KGS | 321030.6
184 | 21 | Supply 11KV 800A DB Break AB Switch | Elecy | Supply | SMR12316 | 30847.46 | EA | 647796.66
185 | 3 | Supply 11KV 400A DB Break AB Switch | Elecy | Supply | SMR12317 | 18150 | EA | 54450
186 | 3275 | Supply MS Flat 75x8mm | Elecy | Supply | SMR12321 | 56.42 | KG | 184775.5
187 | 2995 | Supply MS Flat 50x6mm | Elecy | Supply | SMR12322 | 56.5 | KG | 169217.5
188 | 750 | Supply RS Joist Pole (175x85mm) | Elecy | Supply | SMR12303 | 60.75 | KG | 45562.5
189 | 1 | Supply 11KV 200A Tilting Type AB Switch | Elecy | Supply | SMR12318 | 8991 | EA | 8991
190 | 1 | Supply 11KV HG FuseSet for StationTransformer | Elecy | Supply | SMR12324 | 1974 | EA | 1974
191 | 1 | Supply LT Distribution Box (SMC) | Elecy | Supply | SMR25200 | 7797 | EA | 7797
192 | 2 | Supply 11KV 3x185 Heat Shble O/d End Term Kit | Elecy | Supply | SMR25201 | 1182.97 | EA | 2365.94
193 | 40 | Supply LT 1Core 120Ssqmm XLPE Al. Cable | Elecy | Supply | SMR25030 | 3118.66 | M | 124746.4
194 | 1000 | Supply RS Joist Pole (175x85mm) | Elecy | Supply | SMR12303 | 60.75 | KG | 60750
195 | 100 | Supply of LT XLPE Cable 3 1/2 C 185 | Elecy | Supply | SMR25204 | 547 | M | 54700
196 | 6.29 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) (other than SS) Earth work excav hard rock bould <3cum | Elecy | labour | SWR10856 | 1318.35 | M3 | 8292.4215
197 | 7.26 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Mass concreting of supports incl. cement | Elecy | labour | SWR10356 | 6579 | M3 | 47763.54
198 | 1.8 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | Elecy | supply | SMR40009 | 2181 | TO | 3925.8
199 | 1.8 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. (*)Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | Elecy | supply | SMR40010 | 1293 | TO | 2327.4
200 | 1.8 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., 1complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | Elecy | labour | SWR10877 | 851 | TO | 1531.8
201 | 1.8 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. (*) Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium Labour for 2nd coat Al. Painting. | Elecy | labour | SWR10879 | 482 | TO | 867.6
202 | 2 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Erection of RS Joist 150 x 150 mm | Elecy | labour | SWR10348 | 1952.61 | EA | 3905.22
203 | 895 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends . Lay-4C/10C 2.5Sqmm Control Cable | Elecy | labour | SWR11879 | 27 | M | 24165
204 | 2 | Sup MS Powder coated CT Marshalling Box | Elecy | supply | SMR40047 | 3675 | EA | 7350
205 | 2 | Erection of Marshalling boxes | Elecy | labour | SWR10940 | 374.85 | EA | 749.7
206 | 12 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing. Supply Tension HW 3Bolt 1Zebra/Pnthr 150mm | Elecy | supply | SMR11915 | 2055 | SET | 24660
207 | 32 | Laying of earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication 75x 8mm MS Flat / GI Flat. Laying of earth mat,excavation 75x 8mm | Elecy | labour | SWR10920 | 65 | RMT | 2080
208 | 5 | Supply of earthing pipe with materials Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication Supply CI Pipe earthing 100mm dia 2.75m long | Elecy | supply | SMR11482 | 3486 | EA | 17430
209 | 5 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4Mts.) duly filling with bentonite, earth , running of earth wireetc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height ERECT. OF LINESupply Providing of earthing | Elecy | labour | SWR10357 | 1234.2 | EA | 6171
210 | 5 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X0.50 M height ERECT. OF LINESupply Providing of RCC collar | Elecy | labour | SWR10359 | 386 | EA | 1930
211 | 6 | Bus Stringing Hoisting of Insulators and hardware, stretching the conductorand stringing of 33 kV bus comprising of three phases withSingle Zebra/panther conductor to a tension of 450kgs.(Bussection of 4.5mt) Hoisting post ins&hrd wr 1panther 33kv | Elecy | labour | SWR21240 | 781 | EA | 4686
212 | 200 | Cable terminations to the switch gear marshalling boxes/panelterminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per specification (including cost of ferrules, lugs and glands) Lay-Cable Terminations to Switchgear | Elecy | labour | SWR11880 | 34.43 | EA | 6886
213 | 1 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33 KV LAS station/Line type including earthing Erect of 33kv LA stn type incl earthing | Elecy | labour | SWR10396 | 880 | SET | 880
214 | 1 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33kv VCB with Control Panel | Elecy | labour | SWR10460 | 12500 | EA | 12500
215 | 7.5 | Supply of HBG metal Supply & spreading of 20mm machine crushed metal (HBG)including cost of conveneyance of all materials, labour charges etc complete for finished item of work and directed by the engineer incharge Supply & Spreading of 20mm HBG metal | Elecy | labour | SWR10860 | 2113 | M3 | 15847.5
216 | 2 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Painting of operating rods of 33kV, 11kV AB switches withpost office red colour (including cost of paint) Painting AB switch OP rods with PO red | Elecy | labour | SWR10881 | 142 | EA | 284
217 | 1 | LOADING of 33 KV VCBs&Panel boards | Elecy | labour | SWR10198 | 1024 | EA | 1024
218 | 1 | UNLOADING of 33 KV VCBs&Panel boards | Elecy | labour | SWR10516 | 1044.48 | EA | 1044.48
219 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excludingof loading unloading) Transport of Cond Drum,VCBs upto 10Km | Elecy | labour | SWR11860 | 2720.34 | EA | 2720.34
220 | 2 | Erection of 33kv ABSwitch including alignment and earthing | Elecy | labour | SWR10392 | 4500 | EA | 9000
221 | 2 | Excavation of pits in all soils except hard rock requiring blasting 12Mtrs/Spun Pole 0.92 M x 0.92M x 2.3M (3.0" x 3.0" x 7.6") 1.94 cum EXCAVATION OF PIT(3.0" x 3.0" x 7.6") | Elecy | labour | SWR10109 | 842.78 | EA | 1685.56
222 | 48 | Labour for Fixing of all types of clamps | Elecy | labour | SWR10917 | 65 | EA | 3120
223 | 20 | Stringing of bus with panther conductor including jumpering etc., complete to all the equipment in SS fixing to all clampsand equipment.(3 Conductors) Stringing of bus with panther conductor | Elecy | labour | SWR10404 | 327.68 | M | 6553.6
224 | 45 | Fabrication of materials including 2 coats of Red oxide painting Fab Back clamps with 50 x 6 mm MS Flat | Elecy | labour | SWR10320 | 15 | EA | 675
225 | 2.114 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metalincluding the cost of metal, sand, Cement and curing etc. Mass concreting of supports incl. cement | Elecy | labour | SWR10356 | 6579 | M3 | 13908.006
226 | 1.8 | Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to theRSupply Joist poles excluding cost of Mild Steel and transportcharges to substation site, including erection. Fabrication of struc.with welding. | Elecy | labour | SWR10869 | 3426 | TO | 6166.8
227 | 1000 | Supply RS Joist Grider Pole (150x150mm) | Elecy | Supply | SMR12302 | 59.25 | KG | 59250
228 | 150 | Supply MS Flat 75x8mm | Elecy | Supply | SMR12321 | 56.42 | KG | 8463
229 | 90 | Supply MS Flat 50x6mm | Elecy | Supply | SMR12322 | 56.5 | KG | 5085
230 | 800 | Supply MS Channel 100x50mm | Elecy | Supply | SMR22745 | 57.45 | KGS | 45960
231 | 2 | Supply 33KV 800A DB Break AB Switch | Elecy | Supply | SMR12315 | 40658.78 | EA | 81317.56
232 | 8 | survey line&cabl inc peg mark&tree clear | Elecy | labour | SWR22092 | 765 | KM | 6120
233 | 50 | Supply M+3 Tower GALV | Elecy | supply | SMR11683 | 140674.3 | EA | 7033715
234 | 50 | Supply of material for Extension of 3Mtrs for M+3 (Galvanized) Supply Mat. for Extn of M+3 Tower by 3M GALV | Elecy | supply | SMR11684 | 28520.64 | EA | 1426032
235 | 50 | Erect- M+3 Tower GALV | Elecy | labour | SWR11850 | 64576 | EA | 3228800
236 | 50 | Erect-Extn of 3M for M+3 Tower GALV | Elecy | labour | SWR11851 | 5168.95 | EA | 258447.5
237 | 237.6 | Earth work excavation of pits in hard murram/rock boulders Excavate-Earth in Hard Murram | Elecy | labour | SWR20959 | 1530 | M3 | 363528
238 | 4 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 12Mtrs/Spun Pole 0.92 M x 0.92M x 2.3M (3.0" x 3.0" x 7.6") Exc of Hard pit w/o blast 0.92X0.92X2.3M | Elecy | labour | SWR11041 | 1466.25 | EA | 5865
239 | 4 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. Erect-12Meter Box pole | Elecy | labour | SWR11267 | 3901.37 | EA | 15605.48
240 | 8 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. Fabrication of 175x85/150x75mm RS joist | Elecy | labour | SWR10642 | 512.55 | EA | 4100.4
241 | 8 | Painting of poles Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables Painting of RS Joist(1C RO, 2C Al.Paint) | Elecy | labour | SWR10640 | 1132 | EA | 9056
242 | 4.41 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | Elecy | labour | SWR10356 | 6579 | M3 | 29013.39
243 | 20 | Formation of Cut point for 33 KV Double circuit line excluding pole erection and stays Formation of 33kvline vertical cutpoint | Elecy | labour | SWR10466 | 3198.72 | EA | 63974.4
244 | 6.4 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | Elecy | supply | SMR40009 | 2181 | TO | 13958.4
245 | 6.4 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | Elecy | labour | SWR10877 | 851 | TO | 5446.4
246 | 6.4 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | Elecy | supply | SMR40010 | 1293 | TO | 8275.2
247 | 6.4 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | Elecy | labour | SWR10879 | 482 | TO | 3084.8
248 | 8 | Paving out and stringing of conductor by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location. 100 Sqmm Single Circuit (3 Conductors) Stringing 100sqmm 33/11kv Line 3 Cond SC | Elecy | labour | SWR10366 | 13856.7 | KM | 110853.6
249 | 480 | LOADING of 33 KV Pin insulators | Elecy | labour | SWR10211 | 3 | CRT | 1440
250 | 480 | UNLOADING of 33 KV Pin insulators | Elecy | labour | SWR10529 | 3 | CRT | 1440
251 | 8 | LOADING of 33KV Metal partSupply bag of 25no | Elecy | labour | SWR10618 | 65 | BAG | 520
252 | 4 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Above 20 Km and upto 30 Km with Lorry for each trip Transport of Cond Drum,VCBs>20 & <30Km | Elecy | labour | SWR11862 | 3691.38 | EA | 14765.52
253 | 50 | Supply GI Bolts & Nuts,Washers etc., | Elecy | supply | SMR11488 | 117.5 | KG | 5875
254 | 6 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Above 20 Km and upto 30 Km with Lorry for each trip Transport of Cond Drum,VCBs>20 & <30Km | Elecy | labour | SWR11862 | 3691.38 | EA | 22148.28
255 | 12 | Load-11/33KV XLPE UG Cable for all sizes | Elecy | labour | SWR11230 | 1024 | DR | 12288
256 | 12 | Unload-11/33KV XLPE UG Cable all sizes | Elecy | labour | SWR11231 | 1024 | DR | 12288
257 | 1700 | Excavation & laying of UG Cable (Double Run) Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, Along the CC / BT multi layer road requiring compressor 33 KV 3x400 Sqmm Cable Lay-DR 33KV 3x400sqmm UG Cb CC/BT Compsr | Elecy | labour | SWR11980 | 1388.84 | M | 2361028
258 | 1700 | Lay-2nd Cable in Excavated Trench | Elecy | labour | SWR10988 | 204.1 | M | 346970
259 | 200 | Excavation & laying of UG Cable in Single Run Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) Raise-SR 33KV 3x400sqmm UG Cb on support | Elecy | labour | SWR11954 | 135.66 | M | 27132
260 | 12 | Making of Outdoor/Indoor End Making 33 KV 3x400 Sqmm Cable Out Door/Indoor end termination TerminationOD/Idoor end termination 33kv 3x400 xlpe | Elecy | labour | SWR10387 | 2764.76 | EA | 33177.12
261 | 8 | UG Cables Joints 33 KV 3x400 Sqmm Cable Straight through joint 33kv 3x400 xlpe | Elecy | labour | SWR10382 | 5700.78 | EA | 45606.24
262 | 2 | Erection of AB Switch and aligment complete Erection of 33 KV AB Switch including alignment and earthing | Elecy | labour | SWR10392 | 4500 | EA | 9000
263 | 2 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Painting of operating rods of 33kV, 11kV AB switches withpost office red colour (including cost of paint) Painting AB switch OP rods with PO red | Elecy | labour | SWR10881 | 142 | EA | 284
264 | 8 | LOADING of Conductor drums | Elecy | labour | SWR10191 | 202 | EA | 1616
265 | 8 | UNLOADING of Conductor drums | Elecy | labour | SWR10509 | 100 | EA | 800
266 | 2 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch AB Switch Coil Earthing GI No. 8 Wire | Elecy | labour | SWR12331 | 146.63 | EA | 293.26
267 | 6.4 | Fabrication of Main and Auxiliary structures with welding using raw steel such as RS joist, M.S.Angles, Plates, Channels, including the supply and fabrication of 6mm base plate to the RSupply Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elecy | labour | SWR10869 | 3426 | TO | 21926.4
268 | 100 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 12Mtrs/Spun Pole 0.92 M x 0.92M x 2.3M (3.0" x 3.0" x 7.6") Exc of Hard pit w/o blast 0.92X0.92X2.3M | Elecy | labour | SWR11041 | 1466.25 | EA | 146625
269 | 100 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation - Spun poles 12.5 Mtrs / 12.9Mtrs PSCC Erection of Spun pole 12.5Mt | Elecy | labour | SWR10350 | 4521.66 | EA | 452166
270 | 110.89 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | Elecy | labour | SWR10356 | 6579 | M3 | 729545.31
271 | 2 | Supply 33KV 800A DB Break AB Switch | Elecy | Supply | SMR12315 | 40658.78 | EA | 81317.56
272 | 2000 | Supply RS Joist Pole (175x85mm) | Elecy | Supply | SMR12303 | 60.75 | KG | 121500
273 | 3500 | Supply MS Channel 100x50mm | Elecy | Supply | SMR22745 | 57.45 | KGS | 201075
274 | 1250 | Supply MS Flat 75x8mm | Elecy | Supply | SMR12321 | 56.42 | KG | 70525
275 | 150 | Supply MS Flat 50x6mm | Elecy | Supply | SMR12322 | 56.5 | KG | 8475
276 | 8 | Supply of 33KV3x400Sqmm Straight thr kit | Elecy | Supply | SMR22223 | 24151 | EA | 193208
277 | 12 | Supply of 33KV 3x400Sqmm O/D End Kit | Elecy | Supply | SMR22222 | 4554 | EA | 54648
278 | 100 | Supply PSCC Spun Pole 12.5Mtr | Elecy | Supply | SMR25238 | 15635.59 | EA | 1563559
279 | 1500 | Supply MS Angle 65X65X6 | Elecy | Supply | SMR25207 | 57.25 | KG | 85875
280 | 291 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M Ex of Hard pit w/o blast 0.75X0.9X1.95M | Elecy | labour | SWR11040 | 990.68 | EA | 288287.88
281 | 291 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Errection of 11 M long PSCC pole | Elecy | labour | SWR10978 | 4336.85 | EA | 1262023.35
282 | 20 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rockboulders) 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M(2.6" x 2.6" x6.0") Exca Hard pit w/o blast 0.76X0.76X1.83M | Elecy | labour | SWR11039 | 928 | EA | 18560
283 | 20 | Erection of pole in position, aligning and setting to work, fixing of cross arms andtop clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation 9.1 M long PSCC poles for Strut Erec of 9.1 Mts PSCC poles for stuts | Elecy | labour | SWR11083 | 2400 | EA | 48000
284 | 291.228 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | Elecy | labour | SWR10356 | 6579 | M3 | 1915989.012
285 | 4 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 12Mtrs/Spun Pole 0.92 M x 0.92M x 2.3M (3.0" x 3.0" x 7.6") Exc of Hard pit w/o blast 0.92X0.92X2.3M | Elecy | labour | SWR11041 | 1466.25 | EA | 5865
286 | 4 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. Erect-12Meter Box pole | Elecy | labour | SWR11267 | 3901.37 | EA | 15605.48
287 | 8 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. Fabrication of 175x85/150x75mm RS joist | Elecy | labour | SWR10642 | 512.55 | EA | 4100.4
288 | 8 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables Painting of RS Joist(1C RO, 2C Al.Paint) | Elecy | labour | SWR10640 | 1132 | EA | 9056
289 | 4.41 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | Elecy | labour | SWR10356 | 6579 | M3 | 29013.39
290 | 20 | Formation of Cut points Formation of Cut point for 11 KV Single Circuit line excluding pole erection and stays Formatn of Horiz Cut point for 11KV line | Elecy | labour | SWR10653 | 1435.81 | EA | 28716.2
291 | 2.45 | Fabrication & erection of Channels Fabrication of Main and Auxiliary structures with welding using raw steel such as RS joist, M.S.Angles, Plates, Channels, including the supply and fabrication of 6mm base plate to the RSupply Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. Fabrication of struc.with welding. | Elecy | labour | SWR10869 | 3426 | TO | 8393.7
292 | 2.45 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | Elecy | supply | SMR40009 | 2181 | TO | 5343.45
293 | 2.45 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | Elecy | labour | SWR10877 | 851 | TO | 2084.95
294 | 2.45 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | Elecy | supply | SMR40010 | 1293 | TO | 3167.85
295 | 2.45 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | Elecy | labour | SWR10879 | 482 | TO | 1180.9
296 | 5 | Paving out and stringing of conductor by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of materialfrom road side to location. 55 Sqmm Single Circuit (3 Conductors) Stringing of 55sqmm 33/11kv Line 3 Cond | Elecy | labour | SWR10365 | 9454.81 | KM | 47274.05
297 | 940 | Excavation & laying of UG Cable (Double Run) Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, Along the CC / BT multi layer road requiring compressor 11 KV 3x300 Sqmm Cable Lay-DR 11KV 3x300sqmm UG Cb CC/BT Compsr | Elecy | labour | SWR11981 | 1264.64 | M | 1188761.6
298 | 940 | Lay-2nd Cable in Excavated Trench | Elecy | labour | SWR10988 | 204.1 | M | 191854
299 | 120 | Excavation & laying of UG Cable in Single Run Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level,providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable,placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required woodencleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) 11 KV 3x300 Sqmm Cable Raise-SR 11KV 3x300sqmm UG Cb on support | Elecy | labour | SWR11955 | 144.08 | M | 17289.6
300 | 4 | Making 11 KV 3x300 Sqmm Cable Out Door/Indoor end termination OD/Idoor end termination 11kv 3x300 xlpe | Elecy | labour | SWR10391 | 2370.63 | EA | 9482.52
301 | 2 | UG Cables Joints : Straight through joint 11kv 3x300 xlpe | Elecy | labour | SWR10386 | 3725.45 | EA | 7450.9
302 | 5 | Stringing of HT AB Cable with GI Metal Parts HT AB Cable 11 KV 3x185+70 Sqmm Stringing of AB cbl 11 KV 3x185+70 Sqmm | Elecy | labour | SWR10454 | 41876.1 | KM | 209380.5
303 | 140 | Straight through joints of AB cable (each lead) Supply and ere Straight line Asmbly kits | Elecy | labour | SWR10672 | 1661 | EA | 232540
304 | 30 | Straight through joints of AB cable (each lead) Supply and ere Angle line Asmbly kits | Elecy | labour | SWR10673 | 2124 | EA | 63720
305 | 60 | End Termination of AB cable (each lead): Supply of 11KV 3x185+70sq.mm/ 3x70+70sq.mm/3x35+35sq.mm AB cable end Kits Supply of 11KV AB cable end kits | Elecy | supply | SMR11504 | 950 | SET | 57000
306 | 60 | End Termination of AB cable (each lead): 120 Sqmm to 185 Sqmm End Termnatn of AB cable 120 to 185 Sqmm | Elecy | labour | SWR10667 | 800 | EA | 48000
307 | 10 | T Branch Kit S&Erect-T-Branch kit | Elecy | labour | SWR24971 | 3215 | EA | 32150
308 | 10 | T Branch Kit Erection of Assemble Kit for 'T' Branche | Elecy | labour | SWR10671 | 1800 | EA | 18000
309 | 166 | Supply and Erection of I Hook and Suspension Hook Supply- I Hook | Elecy | supply | SMR12099 | 158 | EA | 26228
310 | 166 | Supply and Erection of I Hook and Suspension Hook Erection- I Hook | Elecy | labour | SWR12099 | 55 | EA | 9130
311 | 60 | Supply of 120 Sqmm Aluminium lugs | Elecy | supply | SMR40132 | 12.52 | EA | 751.2
312 | 5 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Elecy | labour | SWR10393 | 3200 | EA | 16000
313 | 5 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Painting of operating rods of 33kV, 11kV AB switches withpost office red colour (including cost of paint) Painting AB switch OP rods with PO red | Elecy | labour | SWR10881 | 142 | EA | 710
314 | 100 | Supply of earthing pipe with materials Supply of GI Flat 25X3 mm including material | Elecy | supply | SMR11485 | 105 | KG | 10500
315 | 10 | UNLOADING of 11 KV AB Cable (XLPE) 3 Core upto 500 Mts. Drum (including Accessories ) | Elecy | labour | SWR12431 | 438 | DR | 4380
316 | 10 | LOADING of 11 KV AB Cable (XLPE) 3 Core upto 500 Mts. Drum (including Accessories ) | Elecy | labour | SWR12413 | 584 | DR | 5840
317 | 375 | LOADING of 11kv Pin/Post/Solid Core Insulators | Elecy | labour | SWR10212 | 1 | CRT | 375
318 | 375 | UNLOADING of 33 & 11 KV Disc insulator | Elecy | labour | SWR10631 | 2 | CRT | 750
319 | 6 | LOADING of 11 KV Metal parts | Elecy | labour | SWR12402 | 48 | BAG | 288
320 | 6 | UNLOADING of 11 KV Metal parts Bag | Elecy | labour | SWR12421 | 48 | BAG | 288
321 | 9 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Above 20 Km and upto 30 Km with Lorry for each trip Transport of Cond Drum,VCBs>20 & <30Km | Elecy | labour | SWR11862 | 3691.38 | EA | 33222.42
322 | 10 | Supply of Danger boards with clamps | Elecy | supply | SMR40070 | 116 | EA | 1160
323 | 15 | Supply of earthing pipe with materials Supply CI Pipe earthing 50mm dia 2m long | Elecy | supply | SMR11484 | 2441 | EA | 36615
324 | 15 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINESupply Providing of RCC collar | Elecy | labour | SWR10359 | 386 | EA | 5790
325 | 15 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elecy | labour | SWR10357 | 1234.2 | EA | 18513
326 | 150 | Supply of earthing pipe with materials Supply of GI Flat 25X3 mm Supply Earthing GI flat 25x3 mm incl material | Elecy | supply | SMR11485 | 105 | KG | 15750
327 | 4 | Load-11/33KV XLPE UG Cable for all sizes | Elecy | labour | SWR11230 | 1024 | DR | 4096
328 | 4 | Unload-11/33KV XLPE UG Cable all sizes | Elecy | labour | SWR11231 | 1024 | DR | 4096
329 | 3 | LOADING of Conductor drums | Elecy | labour | SWR10191 | 202 | EA | 606
330 | 3 | UNLOADING of Conductor drums | Elecy | labour | SWR10509 | 100 | EA | 300
331 | 291 | Supply PSCC Pole 11Mtr 365 Kg | Elecy | Supply | SMR25236 | 5399 | EA | 1571109
332 | 20 | Supply PSCC Pole 9.1Mtr 280kg | Elecy | Supply | SMR25233 | 3109.41 | EA | 62188.2
333 | 2000 | Supply RS Joist Pole (175x85mm) | Elecy | Supply | SMR12303 | 60.75 | KG | 121500
334 | 500 | Supply MS Channel 100x50mm | Elecy | Supply | SMR22745 | 57.45 | KGS | 28725
335 | 1000 | Supply MS Channel 75x40 mm | Elecy | Supply | SMR25205 | 58.45 | KG | 58450
336 | 600 | Supply MS Angle 50x50x6 | Elecy | Supply | SMR25206 | 58.15 | KG | 34890
337 | 350 | Supply MS Flat 50x6mm | Elecy | Supply | SMR12322 | 56.5 | KG | 19775
338 | 2 | Supply 11KV 3x300 Heat Shble str thr JointKit | Elecy | Supply | SMR25210 | 4110.17 | EA | 8220.34
339 | 4 | Supply 11KV 3x300 Heat Shble O/d End Term Kit | Elecy | Supply | SMR25208 | 1372.88 | EA | 5491.52
340 | 5 | Supply 11KV 400A Conv ABSwitch with Insulator | Elecy | Supply | SMR25211 | 11754 | EA | 58770
Electrical labour | [7 empty] | 34834603.7461
WBS. No. S-1798-13-07-01-01-001(Civil)
1 | 32 | Leveliing the site by cutting and levelling with the help of JCB including cost,conveyance of all materials,hire chareges etc complete for finished item of work as directed by Engineer-in-charge. | Civil | Labour | SWR34179 | 2165 | Hrs | 69280
2 | 149.95 | Earth Work Mass Excavation (hard rock) to a depth as directed, in soils such as hard rock requiring blasting in prohibited area and all conditions such as dry, wet, slurry etc.and in dense or hard soils, disposal and depositing of excavated soil with intial lead of 10 mt and intial lift of 2m or as directed, including cost and conveyance of all materials, ramping and lifting of materials, and labour charges, hire charges of machinery, tools & plants, bailing of water ( either sub soil water, stoMts water, rain water, surface water or of any kind) if any at any stage of work until all works below ground level is finished to the satisfaction ,and from work such as shoring, timbering, strutting with required supports etc. for the work and removal of form work after completion of work etc all complete as directed by the engineer-incharge. | Civil | Labour | SWR33018 | 1440 | cum | 215928
3 | 115.65 | Earth work excavation in all type of soils red earth, Hard gravelly soils, earth mixed with sand and sandy soils etc., in all conditions such as slushy and dry with initial leads and lifts for foundations. Ordinary Soil | Civil | Labour | SWR33015 | 486 | cum | 56205.9
4 | 22.79 | Plain Cement contrete (1:4:8) using 40 mm metal with concrete Mixture. All work upto Plinth level including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete as directed by Engineer incharge of the work | Civil | Labour | SWR33028 | 4737 | cum | 107956.23
5 | 108.3 | Coursed Rubble stone masonry 2nd sort with hard granite stones in cement mortar (1:6) for basement, including cost and conveyance of all materials, labour charges, curing, all leads and lifts, etc, complete for finished item of work. | Civil | Labour | SWR33041 | 4867 | cum | 527096.1
6 |  | RCC M20 Grade nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials labour scaffolding, centering, machine mixing, vibrating, curing all leads and lifts, in all positions of the building but excludi
7 | 1.09 | RCC M20 Grade Footing | Civil | Labour | SWR33098 | 9488 | cum | 10341.92
8 | 1.58 | RCC M20 Grade Column | Civil | Labour | SWR33100 | 13237 | cum | 20914.46
9 | 1.15 | RCC M20 Grade plinth beam | Civil | Labour | SWR33099 | 12359 | cum | 14212.85
10 | 0.46 | Supplying, Cutting, bending, binding, placing in position and tying reinforcement steel in all heights including cost and conveyance of steel and binding wire etc,. With all leads and lifts, labour charges, etc., complete for finished item of work. | Civil | Labour | SWR33144 | 70687 | MT | 32516.02
11 | 66.71 | Brick masonry in cement mortar (1:6) for superstructure using well burnt country made second class bricks of approved quality including cost and conveyance of all materials curing, scaffolding with all leads and lifts in all heights etc., complete for finished item of work | Civil | Labour | SWR33068 | 8269 | cum | 551624.99
12 | 6.98 | Plain Cement concrete (1:2:4) using 20mm size well graded HBG metal for foundations, including cost, conveyance of all materials,labour all leads and lifts,consolidation and all operations, formwork as required, curing,etc. complete for finished item of work | Civil | Labour | SWR33030 | 6106 | cum | 42619.88
13 | 630.95 | Plastering with two coats, 1st coat in cm1:5 16mm thick and 2nd coat in cm 1:4 4mm thick, total 20mm thick for superstructure walls, ceiling, sunshades, Beams, etc., with sponge finishing including cost and conveyance of all materials all leads & lifts e | Civil | Labour | SWR33163 | 562 | Sqm | 354593.9
14 | 27 | Painting with two coats of ACE paint over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33356 | 210 | Sqm | 5670
15 | 781.85 | Painting with two coats of Surya Cem paint over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33329 | 85 | sqm | 66457.25
16 | 380 | Manufacturing, Supplying and fixing of MS grill for (Gate and raillings) of approved design as per drawings, including cost and conveyance of all materials, labour charges etc.,complete for finished item of work as directed by the Engineer- in-charge. | Civil | Labour | SWR33145 | 128 | Kgs | 48640
17 | 3 | Supply and Fixng of MS Name Board including cost & conveyance of all materials,labour charges etc complete for finished item of work. | Civil | Labour | SWR33421 | 4326 | sqm | 12978
18 | 1 | Geophysical Investgation charges for water point by Geologist | Civil | Labour | SWR33608 | 5000 | EA | 5000
19 |  | Drilling of 165mm bore well with machine rig including deployment and hire charges of rig and other machinery and equipment labour charges , measuring the yeild of borewell including cost and conveyance etc complete
20 | 90 | Drill-165mm Bore Well 0 to 90 | Civil | Labour | SWR33609 | 336 | M | 30240
21 | 30 | Drill-165mm Bore Well 90M to 120M | Civil | Labour | SWR34830 | 369 | M | 11070
22 | 30 | Drill-165mm Bore Well 120M to 150M | Civil | Labour | SWR34831 | 394 | M | 11820
23 | 30 | Drill-165mm Bore Well 150M to 180M | Civil | Labour | SWR34832 | 492 | M | 14760
24 | 30 | Drill-165mm Bore Well 180M to 210M | Civil | Labour | SWR34833 | 623 | M | 18690
25 | 30 | Drill-165mm Bore Well 210M to 240M | Civil | Labour | SWR34834 | 754 | M | 22620
26 | 30 | Drill-165mm Bore Well 240M to 270M | Civil | Labour | SWR34835 | 918 | M | 27540
27 | 90 | Drill-165mm Bore Well 270M and above | Civil | Labour | SWR34836 | 1082 | M | 97380
28 | 40 | Supply and fixing of 160mm dia PVC casing of A class 6Kg point pressure including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR33611 | 883 | M | 35320
29 | 1 | Supply and erecting, ISI mark submersible 5.0 HP, Single Phase 30 stages pumpset suitable for 106/156mm dia borewell including cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33640 | 48007 | EA | 48007
30 | 310 | Supply and fixing of HDPE pipe 40mm dia of 16Kg/cm2 including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR34410 | 180 | M | 55800
31 | 1 | Supply and erecting D.O.L Starter 415V , Single phase,50Hz with SS enclouserincluding cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33645 | 7854 | EA | 7854
32 | 315 | Supply of 3 Core 2.5 Sqmm Flat Copper cable of ISI for Submersible Motors of makes Finolex / Polycab / Gold Medal / Million / Payal / Sun Light / Power Flex / Fortune Art | Civil | Labour | SWR33641 | 192 | M | 60480
33 | 6 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-28.60mm OD Pipe - SDR 11 | Civil | Labour | SWR34363 | 410 | M | 2460
34 | 1 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type - 25mm NB Size | Civil | Labour | SWR34346 | 466 | EA | 466
35 | 64.95 | Earth work excavation in all type of soils red earth, Hard gravelly soils, earth mixed with sand and sandy soils etc., in all conditions such as slushy and dry with initial leads and lifts for foundations. | Civil | Labour | SWR33015 | 486 | Cum | 31565.7
36 | 13.54 | Plain Cement concrete (1:4:8) using 40mm HBG metal for foundations and leveling course, including cost and conveyance of all materials, labour all leads and lifts, consolidation and all operations, formwork as required, curing, etc. complete for finished item w | Civil | Labour | SWR33028 | 4737 | Cum | 64138.98
37 | 26.08 | Coursed Rubble stone masonry 2nd sort with hard granite stones in cement mortar (1:6) for basement, including cost and conveyance of all materials, labour charges, curing, all leads and lifts, etc, complete for finished item of work. | Civil | Labour | SWR33041 | 4867 | Cum | 126931.36
38 | 51.88 | Supplying and filling the substation site with borrowed gravel, watering, ramming, thoroughly complying with the standard specification. | Civil | Labour | SWR33052 | 309 | Cum | 16030.92
39 |  | RCC M20 Grade nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials labour scaffolding, centering, machine mixing, vibrating, curing all leads and lifts, in all positions of the building but excludi
40 | 3.56 | a) RCC M20 Grade Column Footings | Civil | Labour | SWR33098 | 9488 | Cum | 33777.28
41 | 2.28 | b)RCC M20 Grade Columns | Civil | Labour | SWR33100 | 13237 | Cum | 30180.36
42 | 2.25 | c)RCC M20 Grade Plinth Beams Long wall | Civil | Labour | SWR33099 | 12359 | Cum | 27807.75
43 | 3.17 | D) RCC M20 Grade Roof Beams landing beam | Civil | Labour | SWR33121 | 12275 | Cum | 38911.75
44 | 0.58 | e) RCC M20 Grade Lintels doors | Civil | Labour | SWR33107 | 13067 | Cum | 7578.86
45 | 2.7 | f) RCC M20 Grade Sunshades 600mm wide and 75mm thick | Civil | Labour | SWR33114 | 1375 | Sqm | 3712.5
46 | 15.22 | g) RCC M20 Grade Roof Slab for Control Room | Civil | Labour | SWR33128 | 10863 | Cum | 165334.86
47 | 3 | Supplying, Cutting, bending, binding, placing in position and tying reinforcement steel in all heights including cost and conveyance of steel and binding wire etc,. With all leads and lifts, labour charges, etc., complete for finished item of work. | Civil | Labour | SWR33144 | 70687 | MT | 212061
48 | 38.36 | Brick masonry in cement mortar (1:6) for superstructure using well burnt country made second class bricks of approved quality including cost and conveyance of all materials curing, scaffolding with all leads and lifts in all heights etc., complete for fin | Civil | Labour | SWR33068 | 8269 | Cum | 317198.84
49 | 517.26 | Plastering with two coats, 1st coat in cm1:5 16mm thick and 2nd coat in cm 1:4 4mm thick, total 20mm thick for superstructure walls, ceiling, sunshades, Beams, etc., with sponge finishing including cost and conveyance of all materials all leads & lifts e | Civil | Labour | SWR33163 | 562 | Sqm | 290700.12
50 | 16.56 | Providing Design R.C. drop wall of 25mm thickness with cm 1:3 and 6mm dia MS bars at 150mm both ways and chicken mesh in two coats 20mm thick each plastering including cost and conveyance of all materials with leads and lifts, scaffolding and curing, labo | Civil | Labour | SWR33203 | 3082 | Sqm | 51037.92
51 | 12.24 | Supply and fixing of Ms ornamental safety grill of approved design including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33310 | 2990 | sqm | 36597.6
52 | 5.91 | Supply and fixing of doors with the frames of the door shall be made well seasoned mt wood of cross section 100x75mm. The shutter shall be made isi mark flushed door with decolam sheets pasted on both sides with PVC beading 40mm width all round.Frame shall be painted with two coats of synthetic enamel paint of approved color over one coat of primer over luppum with spary with 3 no 150mm brass hinges 1 no brass door stoper, 1 no 250mm brass aldrops. 2 no 300 mm aluminium tower bolts, 2 no 150mm brass fancy door handlers, 1 no keyless lockset with cp handel. The quoted rate shall include cost and conveyance of the meterials, fixig, labour carges, tools, handles,locking arrangementts and other fixtures & fittings for finished item work as directed by the Engineer - in- charge. | Civil | Labour | SWR33264 | 7314 | Sqm | 43225.74
53 | 20.25 | Raised pointing to the exposed surfaces of CRS masonry in cm 1:3 prop. including cost and conveyance of all materials, labour charges, all leads and lifts curing etc, complete for finished item of work. | Civil | Labour | SWR33184 | 125 | sqm | 2531.25
54 | 8.64 | Supplying and fixing Aluminium sliding windows with grill and fixed glass panels using anodised aluminium extruded sections of mat finish for frames and mullions made from approved aluminium sections 62x32x1.2mm at 0.73kg/Rm providing 5mm plain glass fix | Civil | Labour | SWR33277 | 3623 | sqm | 31302.72
55 | 16.56 | Supply and laying of Ceramic floor over of CM 1:3 20 mm thick including required materials and labour charges etc complete for item of work | Civil | Labour | SWR33224 | 914 | Sqm | 15135.84
56 | 121.92 | Flooring with double machine polished and hand cut Tandur blue stone 20mm thick of approved colour, quality and of minimum of 300x300mm size over a bed of cement mortar 1:3 20mm thick including cost of all materials, with all leads and lifts jointing and | Civil | Labour | SWR33219 | 787 | Sqm | 95951.04
57 | 6.74 | Supply and fixing of 4" high skirting of shabad stone to the walls including cost and conveyance of all materials, labour etc for finished item of work. | Civil | Labour | SWR33236 | 876 | Sqm | 5904.24
58 | 243.69 | Painting with two coats of OBD over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials labour charges etc., complete for finished item of work. | Civil | Labour | SWR33333 | 146 | Sqm | 35578.74
59 | 349.52 | Painting with two coats of ACE paint over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33356 | 210 | Sqm | 73399.2
60 | 101.17 | Providing impervious coat over RCC roof slab to requried slopes with 20mm thick in CM 1:3 mixed with approved brand of water proffing compound inclding cost and conveyance of all materials, labour charges, curing, rounding off junctions of wall and slab, all leads and lifts, etc . complete for finished item of work as directed by the Engineer - in - charge. | Civil | Labour | SWR33156 | 584 | sqm | 59083.28
61 | 60 | Supply & fixing of 25mm dia 2mm thick suSupply & fixing of 25mm dia 2mm thick surface P.V.C. pipe (ISI MARK) Concealed in wall with all required accessories including masonary work and labour charges etc.complete. | Civil | Labour | SWR33441 | 108 | Rmt | 6480
62 | 1 | Supply & fixing TPN Distribution board w Supply & fixing TPN Distribution board with IP-42 protection (Metal Door)suitable for 3 phase ELCB/RCCB/FP Isolator as incomer and 10kA SP MCBs as out going including internal connection and labour charges for surface / flush mounting etc Complete. | Civil | Labour | SWR33526 | 11353 | EA | 11353
63 | 10 | Supply & fixing of 6A 3 pin wall plug so Supply & fixing of 6A 3 pin wall plug socket with 6A switch control on a common switch board with earth continuity including wire leads,earth connection along with all labour charges etc., complete | Civil | Labour | SWR33468 | 166 | EA | 1660
64 | 6 | Supply & fixing of 16A 3 pin and 6A 3pin Supply & fixing of 16A 3 pin and 6A 3pin plug Flush type socket with indicator lamp and 16Amps fuse unit and 16Amps switch control (5 in one )duly recessed in wall with wooden deep box of 6'' x 8'' x 2 1/2'' size covered with hylam sheet earth connection and all labour charges etc., complete on wall. | Civil | Labour | SWR33470 | 449 | EA | 2694
65 | 24 | Wiring with 2 runs of 14/0.3mm (1.0 sq.m Wiring with 2 runs of 14/0.3mm (1.0 sq.mm)Fire Retardant (FR) P.V.C. insulated flexible copper cable (ISI MARK) in existing pipe with 6A Flush type Switch,ceiling rose and 3mm thick hylam sheet covering to switch control box including all labour charges etc., complete for light points, bell , fan and exhaust fan points in Non-Residential Buildings. | Civil | Labour | SWR33457 | 676 | EA | 16224
66 | 12 | Supply & Fixing of 28W T5 fluorescent tube. | Civil | Labour | SWR33558 | 148 | EA | 1776
67 | 1 | Supply of 12" (300mm)ISI, 900 RPM Heavy duty exhaust fan with metallic blades with Mark of makes Crompton / Bajaj / Havells / Orient. | Civil | Labour | SWR33571 | 2192 | EA | 2192
68 | 180 | Supply and run of 2 of 22/0.3mm (1.5 sq.mm) (FR) P.V.C. insulated flexible copper cable in existing pipe for mains including all labour charges complete. | Civil | Labour | SWR33496 | 75 | M | 13500
69 | 180 | Supply and run of 2 of 36/0.3mm (2.5 sq.mm) FR P.V.C. insulated flexible copper cable in existing pipe for mains including all labour charges complete. | Civil | Labour | SWR33497 | 103 | M | 18540
70 | 12 | Supply & fixing of batten holder /slanting holder in lieu of ceiling rose of light point complete with all connection and all labour charges with 40W bulb (for new installation). | Civil | Labour | SWR33484 | 141 | EA | 1692
71 | 4 | Supply & fixing of 1200mm (48'') sweep 230v,A.C 50 Hz.Ceiling fan with 3 Blades and double ball bearings with all standared accessories. | Civil | Labour | SWR33563 | 2277 | EA | 9108
72 | 4 | Supply & fixing of Electronic Regulator for ceiling fans 900/1200/1400mm sweep including cost of material, Electrical charges complete for finished item of work | Civil | Labour | SWR33564 | 589 | EA | 2356
73 | 1 | Providing independent EARTHING by excavating a trench to a depth of 2.1M in all solid,as per size specified in the Data,using 40mm dia 'B' class GI pipe of 2.5 Mtrs length with necessary accessories with hume pipe ring duly providing staggered holes including filling with equal proportion of salt and Charcoal in layers and all labour charges etc., compiete for small quarters. | Civil | Labour | SWR33596 | 5345 | EA | 5345
74 | 35 | Supplying, laying, jointing and testing 101.6 mm SWG SP-1 pipes of ISI make conforming to ISI 651 & 4127 with airtight cement joints in CM 1.5:1 prop. Including excavation of trenches and socket pits in any soil (except rock requiring blasting) up to 1524 mm(5'0") depth and refilling with watering and tamping. | Civil | Labour | SWR34281 | 755 | M | 26425
75 | 3 | Constructing 904.0 mm (3#0#) dia brick masonry inspection chamber as per IS - 4111: Part-1:1986 with cement mortar (1:6) prop using 2nd Class Clay Bricks of 225 mm thick from approved source having a minimum crushing strength of 5 N/sq.mm including plastering with cement mortar 1:3 prop; ½# thick both inside and outside fitted with 20# dia RCC manhole covers and frames including excavating pits up to a depth of 904 mm (3'-0") in all sorts of soils (excluding rock) and laying cement concrete (1:4:8) 150 mm thick using 40 mm HBG Metal and P.C.C. 1:2:4 benching and channel 100 mm thick as per Standard specification and including cost and conveyance of all materials like cement, sand, bricks, water etc., to site, cost of seigniorage charges on all materials and all incidental and operational, labour charges like mixing cement mortar, constructing masonry, lift charges, curing etc., complete for finished item of work as per Standard specification. | Civil | Labour | SWR34296 | 8766 | EA | 26298
76 | 4 | Supply & fixing of 110 mm dia - Door Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34381 | 128 | EA | 512
77 | 4 | Supply & fixing of 110 mm dia - Plain Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34380 | 100 | EA | 400
78 | 12 | Supply & fixing of 110 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand | Civil | Labour | SWR34377 | 462 | M | 5544
79 | 18 | Supply & fixing of 90 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand | Civil | Labour | SWR34378 | 410 | M | 7380
80 | 3 | Supplying & fixing 150 mm x 100 mm SWG gully traps conforming to ISI 651 & 4127 with C.I Grating & Cost. Brick masonry in CM 1:6 prop. Intermediate chamber and fitted with 304.8 mm x 288.6mm (12"x9") C.I Frame and hinged cover | Civil | Labour | SWR34286 | 767 | EA | 2301
81 | 1 | Supplying and Fixing of European Water Closet of 1st Quality | Civil | Labour | SWR34314 | 2228 | EA | 2228
82 | 6 | Supply & fixing 12.7 mm NP stop cock Indian make 400 grams Seiko/ Senior/ Nice/ Senior/ Nice or equivalent | Civil | Labour | SWR34328 | 721 | EA | 4326
83 | 4 | S&F 12.7 mm N.P bib tap Indian make 400 grams Seiko/ Senior/ Nice or equivalent | Civil | Labour | SWR34329 | 296 | EA | 1184
84 | 1 | Supplying & Fixing Indian make Flat Back Wash Hand Basin (HSW/Parryware/ Neycer) 1st quality conforming to IS:2556-Part-4:1972 with waste fittings like rubber plug, chain, 32 mm nominal size C.P. Fitting with parallel pipe thread conforming to IS:2963-1979 and fitted with 15 mm nominal bore Chromium Plated Pillar Tap of 1st quality Indian make 400 grams Seiko/ Senior/ Nice/ Esso or equivalent complete with standard CI brackets including wooden block: 550 x 400 mm - Single C.P. Pillar cock | Civil | Labour | SWR34316 | 1717 | EA | 1717
85 | 2 | Supply & fixing 38.1 mm C.P waste coupling Half or Full Thread 1st Quality Indian make Parryware or equivalent | Civil | Labour | SWR34428 | 309 | EA | 618
86 | 2 | Supply & fixing of 4" (101.6 mm ) Nahany Trap ( Without Jali with inlet)UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34387 | 134 | EA | 268
87 | 1000 | Providing & Placing on Terrace (at all floor levels) polyethylene water storage tank with Double layer approved brand & manufacture with cover and suitable locking arrangement & making necessary holes for inlet & outlets and over flow pipes but with NECESSARY fittings & base support for tanks | Civil | Labour | SWR34375 | 10 | L | 10000
88 | 2 | Supply & fixing 31.75 mm dia PVC flexible waste pipe of 914.4 mm length of Ist quality | Civil | Labour | SWR34426 | 33 | EA | 66
89 | 45 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)- 15.90mm OD Pipe - SDR 11 | Civil | Labour | SWR34361 | 239 | M | 10755
90 | 40 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-22.20mm OD Pipe - SDR 11 | Civil | Labour | SWR34362 | 313 | M | 12520
91 | 65 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-28.60mm OD Pipe - SDR 11 | Civil | Labour | SWR34363 | 410 | M | 26650
92 | 4 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type - 25mm NB Size | Civil | Labour | SWR34346 | 466 | EA | 1864
93 | 4 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type -20mm NB Size | Civil | Labour | SWR34345 | 331 | EA | 1324
94 | 1 | Supply & fixing 25.4 mm dia & 609.6 mm long aluminium anodized towel rod with brackets and aluminium screws | Civil | Labour | SWR34430 | 489 | EA | 489
95 | 85.51 | Earth work excavation in all type of soils red earth, Hard gravelly soils, earth mixed with sand and sandy soils etc., in all conditions such as slushy and dry with initial leads and lifts for foundations. Ordinary Soil | Civil | Labour | SWR33015 | 486 | cum | 41557.86
96 | 18.91 | Plain Cement concrete (1:4:8) using 40mm HBG metal for foundations and leveling course, including cost and conveyance of all materials, labour all leads and lifts, consolidation and all operations, formwork as required, curing, etc. complete for finished item w | Civil | Labour | SWR33028 | 4737 | cum | 89576.67
97 | 91.8 | Coursed Rubble stone masonry 2nd sort with hard granite stones in cement mortar (1:6) for basement, including cost and conveyance of all materials, labour charges, curing, all leads and lifts, etc, complete for finished item of work. | Civil | Labour | SWR33041 | 4867 | cum | 446790.6
98 | 36 | Plain Cement concrete (1:3:6) using 40mm HBG metal for foundations and leveling course, including cost and conveyance of all materials, labour all leads and lifts, consolidation and all operations, formwork as required, curing, etc. complete for finished item w | Civil | Labour | SWR33029 | 5027 | cum | 180972
99 | 108 | Raised pointing to the exposed surfaces of CRS masonry in cm 1:3 prop. including cost and conveyance of all materials, labour charges, all leads and lifts curing etc, complete for finished item of work. | Civil | Labour | SWR33184 | 125 | sq.mm | 13500
100 | 787.5 | Supplying and filling the substation site with borrowed gravel, watering, ramming, thoroughly complying with the standard specification. | Civil | Labour | SWR33052 | 309 | cum | 243337.5
101 | 88.8 | Plastering with two coats, 1st coat in cm1:5 16mm thick and 2nd coat in cm 1:4 4mm thick, total 20mm thick for superstructure walls, ceiling, sunshades, Beams, etc., with sponge finishing including cost and conveyance of all materials all leads & lifts e | Civil | Labour | SWR33163 | 562 | sq.mm | 49905.6
102 | 200.85 | Painting with two coats of Surya Cem paint over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33329 | 85 | sq.mm | 17072.25
103 | 120 | Supply&Fabrication and fixing of Welded wire mesh ( 2" x 2") of 3mm dia. with ISMC (75x40x4.4mm) and Pheriperal frame of ISA(35x35x3mm) incldg cost& conveyance painting with synthetic enamil paint two coats over a coat of red oxide primer etc complete for finished item of work.. | Civil | Labour | SWR33403 | 2310 | sq.mm | 277200
104 | 160 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-22.20mm OD Pipe - SDR 11 | Civil | Labour | SWR34362 | 313 | rmt | 50080
105 | 30 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type - 25mm NB Size | Civil | Labour | SWR34346 | 466 | EA | 13980
106 | 1 | Providing Consultancy services for arranging contour surveying with total station incuding preparation of boundary and contour levels with 2 Nos. Hard copies and soft copies complete for finished items of work | Civil | Labour | SWR33427 | 5665 | EA | 5665
107 | 425.08 | Seigniorage Charges - Sand | Civil | Labour | SWR34470 | 40 | cum | 17003.2
108 | 1434.28 | Seigniorage Charges - Metal | Civil | Labour | SWR34471 | 97.5 | cum | 139842.3
109 | 839.38 | Seigniorage Charges - Gravel | Civil | Labour | SWR34472 | 30 | cum | 25181.4
110 | 60 | Supply and fixing of RCC fencing poles of size 0.1mx0.1mx1.8m (security fencing of sub station), including cost and conveyance of all labour, materials,and hire chareges etc complete for finished item of work. | Civil | Labour | SWR33405 | 1444 | EA | 86640
111 | 1200 | Supply and fixing of galvanised barded wire (1 horizantal & 2 cross strands. including cost and conveyance of all labour, materials,and hire chareges etc complete for finished item of work. | Civil | Labour | SWR33408 | 16 | M | 19200
[5 empty] | Civil labour |  |  | 6355513.73
[5 empty] | Electrical and Civil labour |  |  | 41190117.4761
[5 empty] | Grand Total Rs. |  |  | 47545631.2061
total Electrical+ civil schedule amount without GST | [7 empty] | #REF!
with GST | [7 empty] | #REF!

## 10. Laxmiguda Housing Colony
"Name of the work: Estimate for erection of new 33/11kV outdoor sub-station at Laxmiguda Housing Board Colony with 2x8 MVA PTRs and connected 33kV, 11kV Lines in Rajendranagar (M) of Rajendranagar Division of ECGH Division in masterplan"
WBS No. S-1795-13-03-02-01-001
Sl No | Estimate Quantity | Description of item | Work Type | Item Short Description | APSS / Month Cl.NumberSSR 11 & 12 | Rate (INR) | UOM | AMOUNT
1 | 16 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | ELEC | Labour | SWR11039 | 928 | EA | 14848
2 | 5.76 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ELEC | Labour | SWR10868 | 6852 | TO | 39467.52
3 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELEC | supply | SMR40009 | 2181 | TO | 12562.56
4 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELEC | labour | SWR10877 | 851 | TO | 4901.76
5 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELEC | supply | SMR40010 | 1293 | TO | 7447.68
6 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELEC | labour | SWR10879 | 482 | TO | 2776.32
7 | 5.76 | Fabrication & erection of Channels-Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ELEC | labour | SWR10867 | 1470 | TO | 8467.2
8 | 16 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-R.S. Joists 150 x 150 mm | ELEC | labour | SWR10348 | 1952.61 | EA | 31241.76
9 | 17.758 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 116829.882
10 | 9.24 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ELEC | labour | SWR10862 | 373 | M2 | 3446.52
11 | 16 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | ELEC | labour | SWR11089 | 48 | EA | 768
12 | 4 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-8.0Mtrs PSCC Poles 0.76 M x 0.76M x 1.52M (2.6" x 2.6" x 5.0') 0.88 cum | ELEC | labour | SWR11037 | 793 | EA | 3172
13 | 1 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ELEC | Labour | SWR10868 | 6852 | TO | 6852
14 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELEC | supply | SMR40009 | 2181 | TO | 2181
15 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELEC | labour | SWR10877 | 851 | TO | 851
16 | 1 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELEC | supply | SMR40010 | 1293 | TO | 1293
17 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELEC | labour | SWR10879 | 482 | TO | 482
18 | 1 | Fabrication & erection of Channels-Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ELEC | labour | SWR10867 | 1470 | TO | 1470
19 | 4 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Box pole 12 Mtr | ELEC | labour | SWR11267 | 3901.37 | EA | 15605.48
20 | 2.65 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 17434.35
21 | 2.31 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ELEC | labour | SWR10862 | 373 | M2 | 861.63
22 | 4 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | ELEC | labour | SWR11089 | 48 | EA | 192
23 | 5.063 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ELEC | labour | SWR10868 | 6852 | TO | 34691.676
24 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELEC | supply | SMR40009 | 2181 | TO | 11042.403
25 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELEC | labour | SWR10877 | 851 | TO | 4308.613
26 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELEC | labour | SMR40010 | 1293 | TO | 6546.459
27 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELEC | labour | SWR10879 | 482 | TO | 2440.366
28 | 5.063 | Fabrication & erection of Channels-Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ELEC | labour | SWR10867 | 1470 | TO | 7442.61
29 | 13 | Erection of AB Switch and aligment complete Erection of 33 KV AB Switch including alignment and earthing | ELEC | labour | SWR10392 | 4500 | EA | 58500
30 | 34 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Note:-The requirement of 2nd coat is to be justified by the concerned Divisional Engineer /Executive Engineer before execution of this work Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | ELEC | labour | SWR10881 | 142 | EA | 4828
31 | 34 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | ELEC | labour | SWR12331 | 146.63 | EA | 4985.42
32 | 6 | Loading of 33 KV CTs/ PTs | ELEC | labour | SWR10200 | 165 | EA | 990
33 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
34 | 6 | Un loading of 33 KV CTs/ PTs | ELEC | labour | SWR10518 | 128 | EA | 768
35 | 2 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33kv single phase PT s | ELEC | labour | SWR10401 | 1079 | SET | 2158
36 | 12 | Loading of 33 KV, 10 KA LAs Station typ | ELEC | labour | SWR10266 | 41 | EA | 492
37 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
38 | 12 | Un loading of 33 KV, 10 KA LAs Station type | ELEC | labour | SWR10584 | 35 | EA | 420
39 | 4 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33 KV LAS station/Line type including earthing | ELEC | labour | SWR10396 | 880 | SET | 3520
40 | 2 | Loading of 33 KV VCBs along with Panel boards | ELEC | labour | SWR10198 | 1024 | EA | 2048
41 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
42 | 2 | Un loading of 33 KV VCBs along with Panel boards | ELEC | labour | SWR10516 | 1044.48 | EA | 2088.96
43 | 12.584 | Excavate-Pit for 33KV VCB | ELEC | labour | SWR23224 | 331 | M3 | 4165.304
44 | 14.52 | Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x 1.8 x 0.75 cum for VCB Plinth | ELEC | labour | SWR20685 | 5160 | M3 | 74923.2
45 | 2 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33 KV VCB with Control Panel | ELEC | labour | SWR10460 | 12500 | EA | 25000
46 | 2 | Loading and unloading of PTR on constructed plinth-Loading of 8MVA PTR | ELEC | labour | SWR10613 | 5805.84 | EA | 11611.68
47 | 2 | Transport of Power transformers (0 to 100 KM) from one place to another place in GHMC Area.(excluding of loading & unloading )-8MVA power transformer | ELEC | labour | SWR10854 | 21945 | EA | 43890
48 | 2 | Loading and unloading of PTR on constructed plinth-Unloading of 8MVA PTR | ELEC | labour | SWR10627 | 5805.84 | EA | 11611.68
49 | 700 | S/o rail poles 90/105lb (250x2N) | ELEC | supply | SMR22718 | 47.27 | KG | 33089
50 | 14 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Rail pole 90 lbs | ELEC | labour | SWR10344 | 3510 | EA | 49140
51 | 2 | Erection of PTR on constructed plinth-Erection of 8 MVA PTR. | ELEC | labour | SWR21321 | 49480.2 | 49480.2 | 98960.4
52 | 0.436 | Extention of 33KV Bay at 132/33KV Sub-station-Zebra condutor | ELEC | supply | SMR24910 | 299369 | 299369 | 130524.884
53 | 30 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing | ELEC | supply | SMR11915 | 2055 | 2055 | 61650
54 | 30 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of I-Bolts | ELEC | supply | SMR22473 | 294 | 294 | 8820
55 | 45 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 "to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating . Sup T clamp LM6 Al alloy of 12 mm, 800 A | ELEC | labour | SMR40011 | 299 | 299 | 13455
56 | 6 | Bus stringing Hoisting of Insulators and hardware, stretching the conductor and stringing of 33 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bussection of 4.5mt) Hoisting post ins&hrd wr 1panther 33kv | ELEC | labour | SWR21240 | 781 | 781 | 4686
57 | 84 | Stringing of bus with panther conductor including jumpering etc., complete to all the equipment in SS fixing to all clamps and equipment.(3 Conductors) | ELEC | labour | SWR10404 | 327.68 | 327.68 | 27525.12
58 | 30 | Bus stringing Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | ELEC | labour | SWR10884 | 224 | 224 | 6720
59 | 75 | Labour for Fixing of all types of clamps | ELEC | labour | SWR10917 | 65 | 65 | 4875
60 | 25 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | ELEC | labour | SWR11039 | 928 | 928 | 23200
61 | 8.68 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ELEC | labour | SWR10868 | 6852 | 6852 | 59475.36
62 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELEC | supply | SMR40009 | 2181 | 2181 | 18931.08
63 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELEC | labour | SWR10877 | 851 | 851 | 7386.68
64 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELEC | supply | SMR40010 | 1293 | 1293 | 11223.24
65 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELEC | labour | SWR10879 | 482 | 482 | 4183.76
66 | 8.68 | Fabrication & erection of Channels-Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ELEC | labour | SWR10867 | 1470 | 1470 | 12759.6
67 | 25 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-R.S. Joists 150 x 150 mm | ELEC | labour | SWR10348 | 1952.61 | 1952.61 | 48815.25
68 | 27.75 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | 6579 | 182567.25
69 | 17.91 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ELEC | labour | SWR10862 | 373 | 373 | 6680.43
70 | 25 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | ELEC | labour | SWR11089 | 48 | 48 | 1200
71 | 4.642 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ELEC | labour | SWR10868 | 6852 | 6852 | 31806.984
72 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELEC | supply | SMR40009 | 2181 | 2181 | 10124.202
73 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELEC | labour | SWR10877 | 851 | 851 | 3950.342
74 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELEC | supply | SMR40010 | 1293 | 1293 | 6002.106
75 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELEC | labour | SWR10879 | 482 | TO | 2237.444
76 | 4.642 | Fabrication & erection of Channels-Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ELEC | labour | SWR10867 | 1470 | TO | 6823.74
77 | 17 | Erection of AB Switch and aligment complete-Erection of 11KV 800A double throw AB Switches | ELEC | labour | SWR21277 | 3500 | EA | 59500
78 | 3 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | ELEC | labour | SWR10393 | 3200 | EA | 9600
79 | 2 | Loading of 11 KV CT - PT Sets | ELEC | labour | SWR10201 | 190 | EA | 380
80 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
81 | 2 | Un loading of 11 KV CT - PT Sets | ELEC | labour | SWR10519 | 101 | EA | 202
82 | 2 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc-Erection of 11 KV three phase PTs | ELEC | labour | SWR10402 | 800 | SET | 1600
83 | 24 | Loading of 11 KV, 10 KA LAs Station type | ELEC | labour | SWR10264 | 32 | EA | 768
84 | 2 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 6599.4
85 | 24 | Un loading of 11 KV, 10 KA LAs Station type | ELEC | labour | SWR10582 | 32 | EA | 768
86 | 2 | Erection of 11 KV LAS station type including earthing | ELEC | labour | SWR10397 | 559 | SET | 1118
87 | 6 | Erection of 11 KV LAS line type including earthing | ELEC | labour | SWR10398 | 505 | SET | 3030
88 | 8 | Loading of 11 KV VCBs along with Panel boards | ELEC | labour | SWR10199 | 1024 | EA | 8192
89 | 4 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 13198.8
90 | 8 | Un Loading of 11 KV VCBs along with Panel boards | ELEC | labour | SWR10517 | 1044.48 | EA | 8355.84
91 | 41.6 | Excavate-Pit for 33KV VCB | ELEC | labour | SWR23224 | 331 | M3 | 13769.6
92 | 48 | Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x 1.8 x 0.75 cum for VCB Plinth | ELEC | labour | SWR20685 | 5160 | M3 | 247680
93 | 8 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc-Erection of 11 KV VCB with Control Panel | ELEC | labour | SWR10461 | 12000 | EA | 96000
94 | 12 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing | ELEC | supply | SMR11915 | 2055 | SET | 24660
95 | 12 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of I-Bolts | ELEC | supply | SMR22473 | 294 | EA | 3528
96 | 45 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 "to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating . Sup T clamp LM6 Al alloy of 12 mm, 800 A | ELEC | supply | SMR40011 | 299 | EA | 13455
97 | 2 | Bus Stringing -Hoisting of Insulators and hardware, stretching the conductor and stringing of 11 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 3.5mt) Hoisting post ins&hrd wr 1panther 11kv | ELEC | labour | SWR21241 | 507 | EA | 1014
98 | 63 | Stringing of bus with panther conductor including jumpering etc., complete to all the equipment in SS fixing to all clamps and equipment.(3 Conductors) | ELEC | labour | SWR10404 | 327.68 | M | 20643.84
99 | 45 | Bus stringing Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | ELEC | labour | SWR10884 | 224 | EA | 10080
100 | 57 | Labour for Fixing of all types of clamps | ELEC | labour | SWR10917 | 65 | EA | 3705
101 | 584 | Laying of earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication 75x 8mm MS Flat / GI Flat. Laying of earth mat,excavation 75x 8mm | ELEC | labour | SWR10920 | 65 | RMT | 37960
102 | 1010 | Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) Earthing for raisers of SS Flat 50x6 mm. | ELEC | labour | SWR10919 | 41 | RMT | 41410
103 | 36 | Supply of earthing pipe with materials -Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | ELEC | supply | SMR11482 | 3486 | EA | 125496
104 | 36 | Providing of Earthing-Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | ELEC | labour | SWR10357 | 1234.2 | EA | 44431.2
105 | 36 | Providing of RCC collar to earth pit-Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINES-Providing of RCC collar | ELEC | labour | SWR10359 | 386 | EA | 13896
106 | 2 | Supply of Copper Flexible jumper with 75 X 8 of length 250 mm at neutral of Power tranformer end and 50 X 6 of length 50mm two Nos at double neutral end duly brasing with flexible jumper of capacity of 5kA/3 sec for power transformer neutral. SupCU Flexi jumper for Power T/F Neutral | ELEC | supply | SMR40033 | 4725 | EA | 9450
107 | 2 | Providing of earthing with various types of earth electrodes-Providing of double earthing for neutral with flexible copper jumpers including arrangement by fixing M.S.Channel 100x50mm. | ELEC | labour | SWR11892 | 1323 | EA | 2646
108 | 80 | Providing of control cable trench as per DATA-XII | ELEC | labour | SWR22093 | 3148 | RMT | 251840
109 | 3074 | Control Cable-Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends . Lay-4C/10C 2.5Sqmm Control Cable | ELEC | labour | SWR11879 | 27 | M | 82998
110 | 270 | Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per specification (including cost of ferrules, lugs and glands) | ELEC | labour | SWR12510 | 27 | EA | 7290
111 | 4 | Marshalling Box Supply of FRP PT Marshalling Box | ELEC | supply | SMR40048 | 4463 | EA | 17852
112 | 4 | Marshalling Box Erection of Marshalling boxes | ELEC | labour | SWR10940 | 374.85 | EA | 1499.4
113 | 1 | Loading of 220 V Batterry with charger | ELEC | labour | SWR11166 | 1612 | SET | 1612
114 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
115 | 1 | Un loading of 220 V Batterry with charger | ELEC | labour | SWR11147 | 1024 | SET | 1024
116 | 1 | Batteries-Erection of 220 V, 200 AH battery in complete shape fit for charging . Conventional lead acid | ELEC | labour | SWR12350 | 7666 | EA | 7666
117 | 1 | Control Panels -Supply of DC Annunciation & relay panel for 10 feeder panel including the cost of LED Indiacation lamps, VAA auxilairy relays, Electronic Hooters complete as per specification. | ELEC | supply | SMR40044 | 42500 | EA | 42500
118 | 1 | Control Panels -Supply of AC Supply panel inluding providing of changeover switch, SFU, metering unit, 32 A three phase MCB, 16 A Single phase MCB complete as per specification. Supply of AC Supply panel complete | ELEC | supply | SMR40045 | 42000 | EA | 42000
119 | 2 | Fixing of AC/DC Panel and giving Connections to the protection equipment and Metering circuits as per the specification and standards. The 3 1/2 core 25 Sqmm power cable required from distribution box to AC/DC panel in the control room is also to be supply | ELEC | labour | SWR20025 | 7871.85 | SET | 15743.7
120 | 8 | Yard lightning-Supply of stepped tubular poles single way made of steel of length 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9 mm, 2.1 mtrs with outer dia 76.1 mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79 kgf as per IS 2713 | ELEC | supply | SMR40051 | 13913 | EA | 111304
121 | 8 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE/CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA /OSRAM /SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty S-90W LED fixture set | ELEC | labour | SMR11594 | 8200 | EA | 65600
122 | 8 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | ELEC | labour | SWR11039 | 928 | EA | 7424
123 | 8 | Erection of tubular poles | ELEC | labour | SWR10955 | 1379 | EA | 11032
124 | 5.27 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 34671.33
125 | 8 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE/CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA /OSRAM /SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty. Fixing of Metal halide lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5 GI pipe complete Fixing of LED/Metal halide complete. | ELEC | labour | SWR10956 | 1268 | EA | 10144
126 | 45 | Supply of HBG metal-Supply & spreading of 20mm machine crushed metal (HBG) including cost of conveneyance of all materials, labour charges etc complete for finished item of work and directed by the engineer incharge | ELEC | labour | SWR10860 | 2113 | M3 | 95085
127 | 2 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M Ex of Hard pit w/o blast 0.75X0.9X1.95M | ELEC | labour | SWR11040 | 990.68 | EA | 1981.36
128 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELEC | Supply | SMR40009 | 2181 | TO | 1635.75
129 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELEC | labour | SWR10877 | 851 | TO | 638.25
130 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELEC | Supply | SMR40010 | 1293 | TO | 969.75
131 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELEC | labour | SWR10879 | 482 | TO | 361.5
132 | 1 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Box pole 12 Mtr | ELEC | labour | SWR11267 | 3901.37 | EA | 3901.37
133 | 2.22 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 14605.38
134 | 1.16 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ELEC | labour | SWR10862 | 373 | M2 | 432.68
135 | 2 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | ELEC | labour | SWR11089 | 48 | EA | 96
136 | 1 | Construction of DTR Plinth-RCC Column type DTR Plinth of size 1'X1'X10',topslab 4'x4'x6" & beam size 4'X8'X8" upto 160KVA | ELEC | labour | SWR21843 | 25967.57 | EA | 25967.57
137 | 1 | Loading of 50,63, 75 & 100 KVA DTR | ELEC | labour | SWR10195 | 350 | EA | 350
138 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
139 | 1 | Un loading of 50,63, 75 & 100 KVA DTR | ELEC | labour | SWR10513 | 280 | EA | 280
140 | 1 | Erection of DTR's including loading and Unloading DTR on the Structure/Plinth etc-Erection of 3 Phase DTRs 63,75 & 100 KVA | ELEC | labour | SWR20905 | 1650 | EA | 1650
141 | 1 | Erection of AB Switch and aligment complete Erection of 11KV 200A TT type AB Switch including fixing of cross angles and alignment complete | ELEC | labour | SWR20102 | 1813.49 | EA | 1813.49
142 | 1 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erect. of 11kv HG Fuseset incl earthing | ELEC | labour | SWR10395 | 740.52 | SET | 740.52
143 | 40 | Excavation & laying of UG Cable in Single Run Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.-In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road-11KV 3x185 Sqmm Cable | ELEC | labour | SWR11920 | 465.46 | M | 18618.4
144 | 2 | Making of Outdoor/Indoor End Termination Making 11 KV 3x185 Sqmm Cable Out Door/Indoor end termination | ELEC | labour | SWR10390 | 2370.63 | EA | 4741.26
145 | 1 | Erection of LT distribution box including laying of LT cable from distribution box to LT OH line and DTR to distribution box including earthing of distribution box and crimping of lugs connecting of jumpers etc | ELEC | labour | SWR10674 | 1594.67 | EA | 1594.67
146 | 85 | LAYING OF 33KV, 11KV UG CABLE Excavation & laying of UG Cable in Single Run Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road-LT 3 1/2 x 185 Sqmm Cable | ELEC | labour | SWR11923 | 377.63 | M | 32098.55
147 | 15 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-LT 3 1/2 x 185 Sqmm Cable | ELEC | labour | SWR11959 | 85.43 | M | 1281.45
148 | 2 | UG Cables Joints :-Making of Outdoor/Indoor End Termination -Supply & fixing of Oout Door/Indoor end termination LT 3 1/2 x 185 Sqmm Cable | ELEC | labour | SWR10765 | 968.9 | EA | 1937.8
149 | 1 | Supply and fixing of Substation board of size 3'x2.5' indicating the layout of switchyard Sup &fix of board ind Switchyard layout | ELEC | labour | SWR20032 | 1654 | EA | 1654
150 | 1 | Supply and fixing of safety instructions/Substation operation instruction board. Sup& fix safety inst/SS Op. inst board | ELEC | labour | SWR22090 | 2205 | EA | 2205
151 | 750 | Control Panels Supplying & fabrication erection of 6mm Checkerd plates as per the field conditions Supply,fabricati of 6mm Checkerd plates | ELEC | Labour | SWR10873 | 83 | KG | 62250
152 | 1 | T & P Supply of Wall clock standard make | ELEC | Supply | SMR40059 | 578 | EA | 578
153 | 1 | S-10ft Aluminium Ladder | ELEC | Supply | SMR12378 | 1654 | EA | 1654
154 | 1 | Sup Alluminium Ladder for indoor works | ELEC | Supply | SMR40062 | 4410 | EA | 4410
155 | 30 | T & P Painting of Name Plates for any equipmen | ELEC | labour | SWR10963 | 122 | EA | 3660
156 | 1 | T & P Supply of Taparia Tool kit of Size 20”x10”x15” with tier arrangements Tool box with locking arrangement & key containing (1) Double Ended fix Spanner sets, (Ribbed) 6 x 7, 8 x 9, 10 x 11, 12 x 13, 14 x 15, 16 x 17, 18 x19, 20 x 22, 21 x 23, 24 x 27, 25 x28, 30 x 32, (2) Double Ended Ring Spanners sets, 6 x 7 , 8 x 9, 10 x 11, 12 x 13, 14 x 15. 16 x 17 , 18 x 19, 20 x 22 , 21 x 23, 24 x 27, 25 x28, 30 x 32 mm, (3) Adjustable Spanner 305 mm length least maximum opening 35mm chrome, (4) Pipe Wrench Length 350 mm 14”, (5) Soft faced Hammer with suitable handle 2 lb, (6) Hacksaw frame with metal handle heavy duty for 12" hacksaw blade with High Speed blade, (7) Insulated Screw drivers Transparent Green Handle Set Length 6”, 8” & 12”, (8) Star Screw Driver Transparent Green Handle Length 6”, (9) Insulated Wire Cutter, (10) Insulated Cutting Plier Length 8” with cable stripper insulated with thick C. A. sleeve confirming to IS: 4378 - 1990, (11) Long Nose Plier insulated with thick C.A. sleeve generally confirming to IS:3552-1989, (12) Tester type screw driver (special with neon bulb) generally confirm to IS: 5579- 1985 Grade:II handle yellow/ green colour overall length 130 mm, (13) Insulated Crimping Plier of all Taparia make. SupTaparia Tool kit complete as per Spec | ELEC | Supply | SMR40063 | 4925 | SET | 4925
157 | 1 | T & P Sup Rechargeable LED torch light of Standard make | ELEC | Supply | SMR40064 | 1733 | EA | 1733
158 | 1 | T & P-Steel almarah(61/2 X 3ft) Godrej | ELEC | Supply | SMR40061 | 9818 | EA | 9818
159 | 1 | T & P-Table (3x6ft) Godrej | ELEC | Supply | SMR40057 | 6050 | EA | 6050
160 | 4 | T & P-S type chairs (Godrej) | ELEC | Supply | SMR40058 | 924 | EA | 3696
161 | 1 | T & P Sup Angle racks(18x36.6inches) Godrej | ELEC | Supply | SMR40060 | 1733 | EA | 1733
162 | 1 | T & P Supply of Hack saw (12 inches) | ELEC | Supply | SMR40065 | 289 | EA | 289
163 | 4 | Sup Earth Rods (8ft) Screw & clamp type | ELEC | Supply | SMR40066 | 578 | EA | 2312
164 | 2 | Supply of Hand Gloves | ELEC | Supply | SMR40067 | 289 | SET | 578
165 | 12 | SupRubber mats( 6'x3')size fo indoorSS | ELEC | Supply | SMR40068 | 1386 | EA | 16632
166 | 1 | Biometric Time attendence System & Telecom Sup Stand basic cell phone with charger | ELEC | Supply | SMR40069 | 1386 | EA | 1386
167 | 14 | Supply of Danger boards with clamps | ELEC | Supply | SMR40070 | 116 | EA | 1624
168 | 20 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-11 KV 3x185 Sqmm Cable | ELEC | Labour | SWR11956 | 126.23 | M | 2524.6
169 | 2 | Supply of Materials -Fire bucket stand with 3 buckets (8 -10 ltr capacity) | ELEC | Supply | SMR40088 | 1386 | SET | 2772
170 | 2 | Room fire extinguisher (2 ltrs capacity) for control room | ELEC | Supply | SMR40089 | 4620 | EA | 9240
171 | 4 | Sup TrollyMounted Co2 (6.5Kgs) Cylinders(IS-2878) | ELEC | Supply | SMR40087 | 9240 | EA | 36960
172 | 6 | Supply of Safety Helmet of standard make | ELEC | Supply | SMR40071 | 231 | EA | 1386
173 | 8 | Supply of LC Boards | ELEC | Supply | SMR40072 | 116 | EA | 928
174 | 4 | Supply of Gum Boots(Pairs) | ELEC | Supply | SMR40073 | 693 | EA | 2772
175 | 1 | Supply of 5000v megger | ELEC | Supply | SMR40074 | 13860 | EA | 13860
176 | 1 | Supply of Earth megger (1000v) | ELEC | Supply | SMR40075 | 8085 | EA | 8085
177 | 1 | Supply of Digital clamp meter. | ELEC | Supply | SMR40076 | 2888 | EA | 2888
178 | 1 | Name board of the 33/11kV Sub-Station(As per Standard Specification) Sup 33/11kv S.S Permanent name board | ELEC | Supply | SMR40086 | 10238 | EA | 10238
179 | 800 | Supply of Hot dip galvanized/zinc coated bolts & nuts including spring washers, pack washers and flat washers etc. | ELEC | Supply | SMR12488 | 90 | KG | 72000
180 | 2 | Fabrication of poles-Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | ELEC | labour | SWR10642 | 512.55 | EA | 1025.1
181 | 1 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-RS Joists 150x75/175 x 85 mm | ELEC | labour | SWR10346 | 1934 | EA | 1934
182 | 5760 | S-Supply of RS Joist Grider Pole (150x150mm) | ELEC | Supply | SMR12302 | 59.25 | KG | 341280
183 | 1000 | S-Supply of RS Joist Pole (175x85mm) | ELEC | Supply | SMR12303 | 60.75 | KG | 60750
184 | 5063 | S- Supply of MS Channel 100x50mm | ELEC | Supply | SMR22745 | 57.45 | KGS | 290869.35
185 | 13 | S-Supply of 33KV 800A DB Break AB Switch | ELEC | Supply | SMR12315 | 40658.78 | EA | 528564.14
186 | 8680 | S-Supply of RS Joist Grider Pole (150x150mm) | ELEC | Supply | SMR12302 | 59.25 | KG | 514290
187 | 4642 | S- Supply of MS Channel 100x50mm | ELEC | Supply | SMR22745 | 57.45 | KGS | 266682.9
188 | 17 | S-Supply of 11KV 800A DB Break AB Switch | ELEC | Supply | SMR12316 | 30847.46 | EA | 524406.82
189 | 3 | S-Supply of 11KV 400A DB Break AB Switch | ELEC | Supply | SMR12317 | 18150 | EA | 54450
190 | 3045 | S-Supply of MS Flat 75x8mm | ELEC | Supply | SMR12321 | 56.42 | KG | 171798.9
191 | 2666 | S-Supply of MS Flat 50x6mm | ELEC | Supply | SMR12322 | 56.5 | KG | 150629
192 | 750 | S-Supply of RS Joist Pole (175x85mm) | ELEC | Supply | SMR12303 | 60.75 | KG | 45562.5
193 | 1 | S-Supply of 11KV 200A Tilting Type AB Switch | ELEC | Supply | SMR12318 | 8991 | EA | 8991
194 | 1 | S-Supply of 11KV HG FuseSet for StationTransformer | ELEC | Supply | SMR12324 | 1974 | EA | 1974
195 | 1 | S-Supply of LT Distribution Box (SMC) | ELEC | Supply | SMR25200 | 7797 | EA | 7797
196 | 2 | S-Supply of 11KV 3x185 Heat Shble O/d End Term Kit | ELEC | Supply | SMR25201 | 1182.97 | EA | 2365.94
197 | 40 | S-Supply of LT XLPE Cable 1C 150 sqmm | ELEC | Supply | SMR25203 | 114.83 | M | 4593.2
198 | 100 | Supply of LT XLPE Cable 31/2C185sqmm. | ELEC | Supply | SMR25204 | 547 | M | 54700
199 | 4 | Loading of LT AB Cable 3X16+25 Sqmm | Elec | labour | SWR11702 | 200 | DR | 800
200 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | Elec | labour | SWR11861 | 3299.7 | EA | 3299.7
201 | 4 | Un loading of LT AB Cable 3X16+25 Sqmm | Elec | labour | SWR11713 | 204 | DR | 816
202 | 5 | survey line&cabl inc peg mark&tree clear | Elec | labour | SWR22092 | 765 | KM | 3825
203 | 5 | Paving out and stringing of conductor by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location-100 Sqmm Single Circuit (3 Conductors) | Elec | labour | SWR10366 | 13856.7 | KM | 69283.5
204 | 100 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M Ex of Hard pit w/o blast 0.75X0.9X1.95M | Elec | labour | SWR11040 | 990.68 | EA | 99068
205 | 100 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Errection of 11 M long PSCC pole | Elec | labour | SWR10978 | 4336.85 | EA | 433685
206 | 35.652 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | Elec | labour | SWR10356 | 6579 | M3 | 234554.508
207 | 100 | Painting of poles-Numbering of poles incl. cost of paint | Elec | labour | SWR10378 | 32 | EA | 3200
208 | 40 | Excavation of pits in all soils except hard rock requiring blasting-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") 1.05 cum | Elec | labour | SWR10107 | 700 | EA | 28000
209 | 40 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Erec of 9.1 Mts PSCC poles for stuts | Elec | labour | SWR11083 | 2400 | EA | 96000
210 | 21 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | Elec | labour | SWR10356 | 6579 | M3 | 138159
211 | 25 | Formation of Cut points - Formation of Cut point for 11 KV Single Circuit line excluding pole erection and stays Formatn of Horiz Cut point for 11KV line | Elec | labour | SWR10653 | 1435.81 | EA | 35895.25
212 | 200 | Supply of earthing pipe with materials S-GI Bolts & Nuts,Washers etc., | Elec | supply | SMR11488 | 117.5 | KG | 23500
213 | 4 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 50 Km and upto 80 Km with Lorry for each trip | Elec | labour | SWR11864 | 5290.74 | EA | 21162.96
214 | 5 | LOADING of Conductor drums | Elec | labour | SWR10191 | 202 | EA | 1010
215 | 5 | UNLOADING of Conductor drums | Elec | labour | SWR10509 | 100 | EA | 500
216 | 30 | Loading of 33 KV Pin insulators | Elec | labour | SWR10211 | 3 | CRT | 90
217 | 30 | Un loading of 33 KV Pin insulators | Elec | labour | SWR10529 | 3 | CRT | 90
218 | 10 | Loading of 33 KV Metal parts | Elec | labour | SWR10618 | 65 | BAG | 650
219 | 10 | Un loading of 33 KV Metal parts | Elec | labour | SWR10632 | 65 | BAG | 650
220 | 440 | Excavation & laying of UG Cable (Double Run) Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, Along the CC / BT multi layer road requiring compressor-33 KV 3x400 Sqmm Cable | Elec | labour | SWR11980 | 1388.84 | M | 611089.6
221 | 440 | Laying of 2nd cable in excavated trench | Elec | labour | SWR10988 | 204.1 | M | 89804
222 | 60 | Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-33 KV 3x400 Sqmm Cable | Elec | labour | SWR12004 | 323.85 | M | 19431
223 | 12 | Cost of Pipes and slabs-Supply of 6" B class GI pipe | Elec | supply | SMR40081 | 1044 | M | 12528
224 | 30 | Cost of Pipes and slabs-Supply of 250 mm Hume pipe of class NP3 with compresive strength of 35N/mm2 for 28 days curing,barewall thickness of 30mm,1.25kG linear/meter and withstanding capability of 22.50KN/linear meter as per IS 458-1993. | Elec | supply | SMR40077 | 363 | M | 10890
225 | 6 | Cost of Pipes and slabs-Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters , CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | Elec | supply | SMR40085 | 484 | EA | 2904
226 | 4 | Load-11/33KV XLPE UG Cable for all sizes | Elec | labour | SWR11230 | 1024 | DR | 4096
227 | 4 | Unload-11/33KV XLPE UG Cable for all sizes | Elec | labour | SWR11231 | 1024 | DR | 4096
228 | 8 | Making of Outdoor/Indoor End Making 33 KV 3x400 Sqmm Cable Out Door/Indoor end termination TerminationOD/Idoor end termination 33kv 3x400 xlpe | Elec | labour | SWR10387 | 2764.76 | EA | 22118.08
229 | 2 | UG Cables Joints 33 KV 3x400 Sqmm Cable Straight through joint 33kv 3x400 xlpe | Elec | labour | SWR10382 | 5700.78 | EA | 11401.56
230 | 1.7 | Fabrication & erection of Channels -Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to theRS-Joist poles excluding cost of Mild Steel and transportcharges to substation site, including erection. Fabrication of struc.with welding. | Elec | labour | SWR10869 | 3426 | TO | 5824.2
231 | 50 | Supply of earthing pipe with materials-Supply of GI wire No 8 | Elec | supply | SMR11486 | 105 | KG | 5250
232 | 2 | Supply of earthing pipe with materials-Supply of CI eath pipe with 80mm dia,2.0 M Length | Elec | labour | SMR11483 | 2789 | EA | 5578
233 | 2 | Providing of Earthing-Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elec | labour | SWR10357 | 1234.2 | EA | 2468.4
234 | 2 | Providing of RCC collar to earth pit-Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINES-Providing of RCC collar | Elec | labour | SWR10359 | 386 | EA | 772
235 | 40 | Supply of earthing pipe with materials-Supply of GI Flat 25X3 mm | Elec | supply | SMR11485 | 105 | KG | 4200
236 | 20 | Supply of Danger boards with clamps | Elec | supply | SMR40070 | 116 | EA | 2320
237 | 6 | S&E-Smart RFID marker | Elec | labour | SWR25089 | 2745 | EA | 16470
238 | 40 | Supply of PSCC Pole 9.1Mtr 280KG | Elec | supply | SMR25233 | 3109.41 | EA | 124376.4
239 | 1000 | Supply of Materials -- Supply of MS Channel 100X50mm | Elec | supply | SMR22745 | 57.45 | KGS | 57450
240 | 500 | Supply of MS Angle 65x65x6 | Elec | supply | SMR25207 | 57.25 | KG | 28625
241 | 200 | Supply of Materials -- Supply of MS Flat 75x8 mm | Elec | supply | SMR12321 | 56.42 | KG | 11284
242 | 8 | UG Cables Joints : Making of Outdoor/Indoor End Termination -- Supply 33KV 3x400Sqmm Outdoor | Elec | supply | SMR22222 | 4554 | EA | 36432
243 | 2 | UG Cables Joints : Making of Straight through joints -- Supply of 33KV 3x400SQmm Straight Through Joint Kit | Elec | supply | SMR22223 | 24151 | EA | 48302
244 | 100 | Supply of PSCC Pole 11Mtr 365KG | Elec | supply | SMR25236 | 5399 | EA | 539900
245 | 75 | Supply of 33KV V-Cross Arm without Clamps | Elec | supply | SMR25229 | 1678 | EA | 125850
246 | 9 | survey line&cabl inc peg mark&tree clear | Elec | labour | SWR22092 | 765 | KM | 6885
247 | 9 | Paving out and stringing of conductor by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location-55 Sqmm Single Circuit (3 Conductors) | Elec | labour | SWR10365 | 9454.81 | KM | 85093.29
248 | 175 | Excavation of pits in all soils except hard rock requiring blasting-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") 1.05 cum | Elec | labour | SWR10107 | 700 | EA | 122500
249 | 50 | Excavation of pits in hard rock requiring blasting. (other than SS)-9.1Mtrs PSCC Pole 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Elec | labour | SWR10112 | 1770 | EA | 88500
250 | 213 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Erec of 9.1 Mts PSCC poles for stuts | Elec | labour | SWR11083 | 2400 | EA | 511200
251 | 37.8 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | Elec | labour | SWR10356 | 6579 | M3 | 248686.2
252 | 225 | Painting of poles-Numbering of poles incl. cost of paint | Elec | labour | SWR10378 | 32 | EA | 7200
253 | 80 | Excavation of pits in all soils except hard rock requiring blasting-Stud Poles 0.6 M x 0.9 M x 1.5 M | Elec | labour | SWR10106 | 645 | EA | 51600
254 | 80 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-8.0 m long PSCC poles for Strut | Elec | labour | SWR21590 | 1500 | EA | 120000
255 | 32 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | Elec | labour | SWR10356 | 6579 | M3 | 210528
256 | 40 | Formation of Cut points - Formation of Cut point for 11 KV Single Circuit line excluding pole erection and stays Formatn of Horiz Cut point for 11KV line | Elec | labour | SWR10653 | 1435.81 | EA | 57432.4
257 | 350 | Supply of earthing pipe with materials S-GI Bolts & Nuts,Washers etc., | Elec | supply | SMR11488 | 117.5 | KG | 41125
258 | 4 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 50 Km and upto 80 Km with Lorry for each trip | Elec | labour | SWR11864 | 5290.74 | EA | 21162.96
259 | 4 | LOADING of Conductor drums | Elec | labour | SWR10191 | 202 | EA | 808
260 | 4 | UNLOADING of Conductor drums | Elec | labour | SWR10509 | 100 | EA | 400
261 | 6 | Supply of earthing pipe with materials-Supply of CI eath pipe with 50mm dia,2.0 M Length | Elec | supply | SMR11484 | 2441 | EA | 14646
262 | 6 | Providing of Earthing-Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elec | labour | SWR10357 | 1234.2 | EA | 7405.2
263 | 6 | Providing of RCC collar to earth pit-Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINES-Providing of RCC collar | Elec | labour | SWR10359 | 386 | EA | 2316
264 | 6 | Assembly and erection of Structure as per specification which includes fixing of top channels and cross bracings, transport of all materials from road side to the location, earthing, back filling with earth ramming etc excluding pit excavation and concreting.-11KV DP Structure with 9.1 Mtrs PSCC Poles | Elec | labour | SWR21130 | 3363.96 | SET | 20183.76
265 | 6 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Elec | labour | SWR10393 | 3200 | EA | 19200
266 | 6 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elec | labour | SWR10881 | 142 | EA | 852
267 | 50 | Supply of earthing pipe with materials-Supply of GI wire No 8 | Elec | supply | SMR11486 | 105 | KG | 5250
268 | 675 | Loading of 11KV Polymer Pin Insulators with GI pins | Elec | labour | SWR11248 | 1 | EA | 675
269 | 675 | Un loading of 11KV Polymer Pin Insulators with GI pins | Elec | labour | SWR11249 | 1 | EA | 675
270 | 240 | Loading of 11KV Polymer Pin Insulators with GI pins | Elec | labour | SWR11248 | 1 | EA | 240
271 | 240 | Un loading of 11KV Polymer Pin Insulators with GI pins | Elec | labour | SWR11249 | 1 | EA | 240
272 | 6 | Loading of 11 KV Metal parts | Elec | labour | SWR12402 | 48 | BAG | 288
273 | 6 | Un loading of 11 KV Metal parts | Elec | labour | SWR12421 | 48 | BAG | 288
274 | 960 | Laying of 2nd cable in excavated trench | Elec | labour | SWR10988 | 204.1 | M | 195936
275 | 72 | Cost of Pipes and slabs-Supply of 6" B class GI pipe | Elec | supply | SMR40081 | 1044 | M | 75168
276 | 200 | Cost of Pipes and slabs-Supply of 250 mm Hume pipe of class NP3 with compresive strength of 35N/mm2 for 28 days curing,barewall thickness of 30mm,1.25kG linear/meter and withstanding capability of 22.50KN/linear meter as per IS 458-1993. | Elec | supply | SMR40077 | 363 | M | 72600
277 | 6 | Cost of Pipes and slabs-Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters , CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | Elec | supply | SMR40085 | 484 | EA | 2904
278 | 5 | Load-11/33KV XLPE UG Cable for all sizes | Elec | labour | SWR11230 | 1024 | DR | 5120
279 | 5 | Unload-11/33KV XLPE UG Cable for all sizes | Elec | labour | SWR11231 | 1024 | DR | 5120
280 | 1.1 | Fabrication & erection of Channels -Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to theRS-Joist poles excluding cost of Mild Steel and transportcharges to substation site, including erection. Fabrication of struc.with welding. | Elec | labour | SWR10869 | 3426 | TO | 3768.6
281 | 50 | Supply of Danger boards with clamps | Elec | supply | SMR40070 | 116 | EA | 5800
282 | 6 | S&E-Smart RFID marker | Elec | labour | SWR25089 | 2745 | EA | 16470
283 | 960 | Excavation & laying of UG Cable (Double Run)-Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts,-In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil/CC-11 KV 3x300 Sqmm Cable | Elec | labour | SWR11973 | 631.06 | M | 605817.6
284 | 240 | Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-11 KV 3x300 Sqmm Cable | Elec | labour | SWR12005 | 275.4 | M | 66096
285 | 6 | UG Cables Joints Making of Straight through joints-11 KV 3x300 Sqmm Cable | Elec | labour. | SWR10386 | 3725.45 | EA | 22352.7
286 | 24 | Making of Outdoor/Indoor End Termination-Making 11 KV 3x300 Sqmm Cable Out Door/Indoor end termination | Elec | labour. | SWR10391 | 2370.63 | EA | 56895.12
287 | 225 | Supply of PSCC Pole 9.1Mtr 280KG | Elec | supply | SMR25233 | 3109.41 | EA | 699617.25
288 | 80 | Supply of PSCC Pole 8Mtr 140KG | Elec | supply | SMR25232 | 1580 | EA | 126400
289 | 185 | Supply of 33KV V X- Arm with MS Channel 75x40 | Elec | supply | SMR25219 | 561 | EA | 103785
290 | 185 | Supply of 11KV Top Cleant for 9.1M(Vertical) | Elec | supply | SMR25226 | 256 | EA | 47360
291 | 80 | Supply of 11KV Horizontal Cross Arm | Elec | supply | SMR25223 | 528 | EA | 42240
292 | 6 | Supply of Materials -- Supply of 11 kV 400 A Double break AB switch | Elec | supply | SMR12317 | 18150 | EA | 108900
293 | 200 | Supply of Materials -- Supply of MS Flat 50x6 mm | Elec | supply | SMR12322 | 56.5 | KG | 11300
294 | 400 | Supply of MS Angle 50x50x6 | Elec | supply | SMR25206 | 58.15 | KG | 23260
295 | 500 | Supply of MS Channel 75x40 mm | Elec | supply | SMR25205 | 58.45 | KG | 29225
296 | 5 | LOADING of Conductor drums | Elec | labour | SWR10191 | 202 | EA | 1010
297 | 5 | UNLOADING of Conductor drums | Elec | labour | SWR10509 | 100 | EA | 500
298 | 24 | Supply of 11KV 3x300 Heat Shble O/d End Term Kit | Elec | supply | SMR25208 | 1372.88 | EA | 32949.12
299 | 6 | Supply of 11KV 3x300 Heat Shble stright through joint Kit | Elec | supply | SMR25210 | 4110.17 | EA | 24661.02
Electrical Labour | [7 empty] | 13606191.793
Civil labour - WBS. No. S-1795-13-07-01-01-001
Sl.No. | Estimate Quantity (only Figures) | Item Detailed Specification Description | Work Type eg. Earth Work, Electrical works. etc (upto 200 Characters) | Item Short Description (upto 100 Characters) | APSS / Morth Cl. Number (upto 200 Characters) | Rate (INR) (Upto 2 Decimals ) | UOM (upto 50 Characters) | Amount
1 | 32 | Leveliing the site by cutting and levelling with the help of JCB including cost,conveyance of all materials,hire chareges etc complete for finished item of work as directed by Engineer-in-charge. | Civil | Labour | SWR34179 | 2165 | Hrs | 69280
2 | 135.61 | Earth work excavation in all type of ordinary soils red earth, Hard gravelly soils, earth mixed with sand and sandy soils etc., in all conditions such as slushy and dry with initial leads and lifts for foundations. | Civil | Labour | SWR33015 | 486 | m3 | 65906.46
3 | 32.45 | Plain Cement concrete PCC (1:4:8) using 40mm HBG metal for foundations and leveling course, including cost and conveyance of all materials, labour all leads and lifts, consolidation and all operations, formwork as required, curing, etc. complete for finished item w | Civil | Labour | SWR33028 | 4794 | m3 | 155565.3
4 | 117.88 | Coursed Rubble stone (CRS) masonry 2nd sort with hard granite stones in cement mortar (1:6) for basement, including cost and conveyance of all materials, labour charges, curing, all leads and lifts, etc, complete for finished item of work. | Civil | Labour | SWR33041 | 4908 | m3 | 578555.04
5 |  | 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge
6 | 3.564 | RCC M20 Grade footing 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33098 | 9546 | m3 | 34021.944
7 | 2.28 | RCC M20 Grade Coloumn . 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33100 | 13295 | m3 | 30312.6
8 | 2.25 | RCC M20 Grade Plinth beams 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33099 | 12416 | m3 | 27936
9 | 3.17 | D) RCC M20 Grade Roof Beams landing beam 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33121 | 12333 | m3 | 39095.61
10 | 0.58 | e)RCC M20 Grade Lintels 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33107 | 13124 | m3 | 7611.92
11 | 2.7 | f) RCC M20 Grade Sunshades 600mm wide and 75mm thick'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33114 | 1380 | m2 | 3726
12 | 15.224 | g) RCC M20 Grade Roof Slab for Control Room 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33128 | 10920 | m3 | 166246.08
13 | 3 | Reinforcement steelSupplying, Cutting, bending, binding, placing in position and tying reinforcement steel in all heights including cost and conveyance of steel and binding wire etc,. With all leads and lifts, labour charges, etc., complete for finished item of work. | Civil | Labour | SWR33144 | 70687 | Ton | 212061
14 | 38.36 | Brick masonry in cement mortar CM (1:6) for superstructure using well burnt country made second class bricks of approved quality including cost and conveyance of all materials curing, scaffolding with all leads and lifts in all heights etc., complete for fin | Civil | Labour | SWR33068 | 8295 | m3 | 318196.2
15 | 2.7 | Plain Cement concrete PCC (1:2:4) using 20mm size well graded HBG metal for foundations, including cost, conveyance of all materials,labour all leads and lifts,consolidation and all operations, formwork as required, curing,etc. complete for finished item of work | Civil | Labour | SWR33030 | 6163 | m3 | 16640.1
16 | 606.06 | Plastering with CM 2 coats, 20 mm thick, base coat in CM (1:6), 16 mm thick and top coat in CM (1:4), 4mm thick with Dubara sponze finishing including cost of all materials, seigniorage charges, excluding conveyance charges of materials and including all operational, incidental and labour charges for mixing mortar, laying rendering smooth and thread lining, curing, rounding off junctions of wall and slab etc., complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33163 | 565 | m2 | 342423.9
17 | 349.515 | Painting with two coats of Plastic Emulsn paint over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33356 | 210 | m2 | 73398.15
18 | 200.85 | Painting with two coats of Surya Cem paint over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33329 | 85 | m2 | 17072.25
19 | 3 | Supply and Fixng of MS Name Board including cost & conveyance of all materials,labour charges etc complete for finished item of work. | Civil | Labour | SWR33421 | 4326 | m2 | 12978
20 | 1 | Geophysical Investgation charges for water point by Geologist | Civil | Labour | SWR33608 | 5000 | EA | 5000
21 |  | Drilling of 165mm bore well with machine rig including deployment and hire charges of rig and other machinery and equipment labour charges , measuring the yeild of borewell including cost and conveyance etc complete
22 | 90 | Drill-165mm Bore Well 0 to 90 | Civil | Labour | SWR33609 | 336 | M | 30240
23 | 30 | Drill-165mm Bore Well 90M to 120M | Civil | Labour | SWR34830 | 369 | M | 11070
24 | 30 | Drill-165mm Bore Well 120M to 150M | Civil | Labour | SWR34831 | 394 | M | 11820
25 | 30 | Drill-165mm Bore Well 150M to 180M | Civil | Labour | SWR34832 | 492 | M | 14760
26 | 30 | Drill-165mm Bore Well 180M to 210M | Civil | Labour | SWR34833 | 623 | M | 18690
27 | 30 | Drill-165mm Bore Well 210M to 240M | Civil | Labour | SWR34834 | 754 | M | 22620
28 | 30 | Drill-165mm Bore Well 240M to 270M | Civil | Labour | SWR34835 | 918 | M | 27540
29 | 80 | Drill-165mm Bore Well 270M and above | Civil | Labour | SWR34836 | 1082 | M | 86560
30 | 40 | Supply and fixing of 160mm dia PVC casing of A class 6Kg point pressure including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR33611 | 883 | M | 35320
31 | 1 | Supply and erecting, ISI mark submersible 5.0 HP, Single Phase 30 stages pumpset suitable for 106/156mm dia borewell including cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33640 | 48007 | EA | 48007
32 | 290 | Supply and fixing of HDPE pipe 40mm dia of 16Kg/cm2 including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR34410 | 180 | M | 52200
33 | 1 | Supply and erecting D.O.L Starter 415V , Single phase,50Hz with SS enclouserincluding cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33645 | 7854 | EA | 7854
34 | 310 | Supply of 3 Core 2.5 Sqmm Flat Copper cable of ISI for Submersible Motors of makes Finolex / Polycab / Gold Medal / Million / Payal / Sun Light / Power Flex / Fortune Art | Civil | Labour | SWR33641 | 192 | m | 59520
35 | 71 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-28.60mm OD Pipe - SDR 11 | Civil | Labour | SWR34363 | 410 | m | 29110
36 | 35 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type - 25mm NB Size | Civil | Labour | SWR34346 | 466 | EA | 16310
37 | 839.38 | Supplying and filling the substation site with borrowed gravel, watering, ramming, thoroughly complying with the standard specification. | Civil | Labour | SWR33052 | 309 | m3 | 259368.42
38 | 16.56 | Providing Design R.C.M. drop wall of 25mm thickness with cm 1:3 and 6mm dia MS bars at 150mm both ways and chicken mesh in two coats 20mm thick each plastering including cost and conveyance of all materials with leads and lifts, scaffolding and curing, labo | Civil | Labour | SWR33203 | 3127 | m2 | 51783.12
39 | 12.24 | Supply and fixing of Ms ornamental safety grill of approved design including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33310 | 2990 | m2 | 36597.6
40 | 5.91 | Supply and fixing of doors with the MT Wood frames of the door shall be made well seasoned mt wood of cross section 100x75mm. The shutter shall be made isi mark flushed door with decolam sheets pasted on both sides with PVC beading 40mm width all round.Frame shall be painted with two coats of synthetic enamel paint of approved color over one coat of primer over luppum with spary with 3 no 150mm brass hinges 1 no brass door stoper, 1 no 250mm brass aldrops. 2 no 300 mm aluminium tower bolts, 2 no 150mm brass fancy door handlers, 1 no keyless lockset with cp handel. The quoted rate shall include cost and conveyance of the meterials, fixig, labour carges, tools, handles,locking arrangementts and other fixtures & fittings for finished item work as directed by the Engineer - in- charge. | Civil | Labour | SWR33264 | 7314 | m2 | 43225.74
41 | 128.25 | Raised pointing to the exposed surfaces of CRS masonry in cm 1:3 prop. including cost and conveyance of all materials, labour charges, all leads and lifts curing etc, complete for finished item of work. | Civil | Labour | SWR33184 | 126 | m2 | 16159.5
42 | 8.64 | Supplying and fixing Aluminium sliding windows with grill and fixed glass panels using anodised aluminium extruded sections of mat finish for frames and mullions made from approved aluminium sections 62x32x1.2mm at 0.73kg/Rm providing 5mm plain glass fix | Civil | Labour | SWR33277 | 3623 | m2 | 31302.72
43 | 16.56 | Supply and laying of Ceramic floor over of CM 1:3 20 mm thick including required materials and labour charges etc complete for item of work | Civil | Labour | SWR33224 | 914 | m2 | 15135.84
44 | 121.92 | Flooring with double machine polished and hand cut Tandur blue stone 20mm thick of approved colour, quality and of minimum of 300x300mm size over a bed of cement mortar 1:3 20mm thick including cost of all materials, with all leads and lifts jointing and | Civil | Labour | SWR33219 | 788 | m2 | 96072.96
45 | 6.74 | Supply and fixing of 4" high skirting of shabad stone to the walls including cost and conveyance of all materials, labour etc for finished item of work. | Civil | Labour | SWR33236 | 878 | m2 | 5917.72
46 | 243.69 | Painting with two coats of OBD over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials labour charges etc., complete for finished item of work. | Civil | Labour | SWR33333 | 146 | m2 | 35578.74
47 | 101.17 | Providing impervious coat over RCC roof slab to requried slopes with 20mm thick in CM 1:3 mixed with approved brand of water proffing compound inclding cost and conveyance of all materials, labour charges, curing, rounding off junctions of wall and slab, all leads and lifts, etc . complete for finished item of work as directed by the Engineer - in - charge. | Civil | Labour | SWR33156 | 587 | m2 | 59386.79
48 | 60 | Supply & fixing of 25mm dia 2mm thick suSupply & fixing of 25mm dia 2mm thick surface P.V.C. pipe (ISI MARK) Concealed in wall with all required accessories including masonary work and labour charges etc.complete. | Civil | Labour | SWR33441 | 108 | m | 6480
49 | 1 | Supply & fixing TPN Distribution board w Supply & fixing TPN Distribution board with IP-42 protection (Metal Door)suitable for 3 phase ELCB/RCCB/FP Isolator as incomer and 10kA SP MCBs as out going including internal connection and labour charges for surface / flush mounting etc Complete. | Civil | Labour | SWR33526 | 11353 | EA | 11353
50 | 10 | Supply & fixing of 6A 3 pin wall plug socket with 6A switch control on a common switch board with earth continuity including wire leads,earth connection along with all labour charges etc., complete | Civil | Labour | SWR33468 | 166 | EA | 1660
51 | 6 | Supply & fixing of 16A 3 pin and 6A 3pin plug Flush type socket with indicator lamp and 16Amps fuse unit and 16Amps switch control (5 in one )duly recessed in wall with wooden deep box of 6'' x 8'' x 2 1/2'' size covered with hylam sheet earth connection and all labour charges etc., complete on wall. | Civil | Labour | SWR33470 | 449 | EA | 2694
52 | 24 | Supply and Fixing of modular switch, LP,FP,EFP Wiring with 2 runs of 14/0.3mm (1.0 sq.mm)Fire Retardant (FR) P.V.C. insulated flexible copper cable (ISI MARK) in existing pipe with 6A Flush type Switch,ceiling rose and 3mm thick hylam sheet covering to switch control box including all labour charges etc., complete for light points, bell , fan and exhaust fan points in Non-Residential Buildings. | Civil | Labour | SWR33457 | 676 | EA | 16224
53 | 12 | Supply & Fixing of 28W T5 fluorescent tube. | Civil | Labour | SWR33558 | 148 | EA | 1776
54 | 1 | Supply of 12" (300mm)ISI, 900 RPM Heavy duty exhaust fan with metallic blades with Mark of makes Crompton / Bajaj / Havells / Orient. | Civil | Labour | SWR33571 | 2192 | EA | 2192
55 | 180 | Supply and run of 2 of 22/0.3mm (1.5 sq.mm) (FR) P.V.C. insulated flexible copper cable in existing pipe for mains including all labour charges complete. | Civil | Labour | SWR33496 | 75 | m | 13500
56 | 180 | Supply and run of 2 of 36/0.3mm (2.5 sq.mm) FR P.V.C. insulated flexible copper cable in existing pipe for mains including all labour charges complete. | Civil | Labour | SWR33497 | 103 | m | 18540
57 | 12 | Supply & fixing of batten holder /slanting holder in lieu of ceiling rose of light point complete with all connection and all labour charges with 40W bulb (for new installation). | Civil | Labour | SWR33484 | 141 | EA | 1692
58 | 4 | Supply & fixing of 1200mm (48'') sweep 230v,A.C 50 Hz.Ceiling fan with 3 Blades and double ball bearings with all standared accessories. | Civil | Labour | SWR33563 | 2277 | EA | 9108
59 | 4 | Supply & fixing of Electronic Regulator for ceiling fans 900/1200/1400mm sweep including cost of material, Electrical charges complete for finished item of work | Civil | Labour | SWR33564 | 589 | EA | 2356
60 | 1 | Providing independent EARTHING by excavating a trench to a depth of 2.1M in all solid,as per size specified in the Data,using 40mm dia 'B' class GI pipe of 2.5 Mtrs length with necessary accessories with hume pipe ring duly providing staggered holes including filling with equal proportion of salt and Charcoal in layers and all labour charges etc., compiete for small quarters. | Civil | Labour | SWR33596 | 5345 | EA | 5345
61 | 35 | Supplying, laying, jointing and testing 101.6 mm SWG SP-1 pipes of ISI make conforming to ISI 651 & 4127 with airtight cement joints in CM 1.5:1 prop. Including excavation of trenches and socket pits in any soil (except rock requiring blasting) up to 1524 mm(5'0") depth and refilling with watering and tamping. | Civil | Labour | SWR34281 | 755 | m | 26425
62 | 3 | Constructing 904.0 mm (3#0#) dia brick masonry inspection chamber as per IS - 4111: Part-1:1986 with cement mortar (1:6) prop using 2nd Class Clay Bricks of 225 mm thick from approved source having a minimum crushing strength of 5 N/sq.mm including plastering with cement mortar 1:3 prop; ½# thick both inside and outside fitted with 20# dia RCC manhole covers and frames including excavating pits up to a depth of 904 mm (3'-0") in all sorts of soils (excluding rock) and laying cement concrete (1:4:8) 150 mm thick using 40 mm HBG Metal and P.C.C. 1:2:4 benching and channel 100 mm thick as per Standard specification and including cost and conveyance of all materials like cement, sand, bricks, water etc., to site, cost of seigniorage charges on all materials and all incidental and operational, labour charges like mixing cement mortar, constructing masonry, lift charges, curing etc., complete for finished item of work as per Standard specification. | Civil | Labour | SWR34296 | 8766 | EA | 26298
63 | 4 | Supply & fixing of 110 mm dia - Door Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34381 | 128 | EA | 512
64 | 4 | Supply & fixing of 110 mm dia - Plain Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34380 | 100 | EA | 400
65 | 12 | Supply & fixing of 110 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand | Civil | Labour | SWR34377 | 462 | m | 5544
66 | 18 | Supply & fixing of 90 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand | Civil | Labour | SWR34378 | 410 | m | 7380
67 | 3 | Supplying & fixing 150 mm x 100 mm SWG gully traps conforming to ISI 651 & 4127 with C.I Grating & Cost. Brick masonry in CM 1:6 prop. Intermediate chamber and fitted with 304.8 mm x 288.6mm (12"x9") C.I Frame and hinged cover | Civil | Labour | SWR34286 | 767 | EA | 2301
68 | 1 | Supplying and Fixing of European Water Closet of 1st Quality | Civil | Labour | SWR34312 | 2228 | EA | 2228
69 | 6 | Supply & fixing 15 mm angle stop cock Indian make 400 grams Seiko/ Senior/ Nice/ Senior/ Nice or equivalent | Civil | Labour | SWR34328 | 721 | EA | 4326
70 | 4 | S&F 15 mm N.P bib tap Indian make 400 grams full turn Seiko/ Senior/ Nice or equivalent | Civil | Labour | SWR34329 | 296 | EA | 1184
71 | 1 | Supplying & Fixing Indian make Flat Back Wash Hand Basin (HSW/Parryware/ Neycer) 1st quality conforming to IS:2556-Part-4:1972 with waste fittings like rubber plug, chain, 32 mm nominal size C.P. Fitting with parallel pipe thread conforming to IS:2963-1979 and fitted with 15 mm nominal bore Chromium Plated Pillar Tap of 1st quality Indian make 400 grams Seiko/ Senior/ Nice/ Esso or equivalent complete with standard CI brackets including wooden block: 550 x 400 mm - Single C.P. Pillar cock | Civil | Labour | SWR34316 | 1717 | EA | 1717
72 | 2 | Supply & fixing 38.1 mm C.P waste coupling Half or Full Thread 1st Quality Indian make Parryware or equivalent | Civil | Labour | SWR34428 | 309 | EA | 618
73 | 2 | Supply & fixing of 4" (101.6 mm ) Nahany Trap ( Without Jali with inlet)UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34387 | 134 | EA | 268
74 | 1000 | Providing & Placing on Terrace (at all floor levels) polyethylene water storage tank with Double layer approved brand & manufacture with cover and suitable locking arrangement & making necessary holes for inlet & outlets and over flow pipes but with NECESSARY fittings & base support for tanks | Civil | Labour | SWR34375 | 10 | L | 10000
75 | 2 | Supply & fixing 31.75 mm dia PVC flexible waste pipe of 914.4 mm length of Ist quality | Civil | Labour | SWR34426 | 33 | EA | 66
76 | 45 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)- 15.90mm OD Pipe - SDR 11 | Civil | Labour | SWR34361 | 239 | m | 10755
77 | 200 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-22.20mm OD Pipe - SDR 11 | Civil | Labour | SWR34362 | 313 | m | 62600
78 | 4 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type -20mm NB Size | Civil | Labour | SWR34345 | 331 | EA | 1324
79 | 1 | Supply & fixing 25.4 mm dia & 609.6 mm long aluminium anodized towel rod with brackets and aluminium screws | Civil | Labour | SWR34430 | 489 | EA | 489
80 | 36 | Plain Cement concrete PCC (1:3:6) using 40mm HBG metal for foundations and leveling course, including cost and conveyance of all materials, labour all leads and lifts, consolidation and all operations, formwork as required, curing, etc. complete for finished item w | Civil | Labour | SWR33029 | 5084 | m3 | 183024
81 | 120 | Supply&Fabrication and fixing of Welded wire mesh ( 2" x 2") of 3mm dia. with ISMC (75x40x4.4mm) and Pheriperal frame of ISA(35x35x3mm) incldg cost& conveyance painting with synthetic enamil paint two coats over a coat of red oxide primer etc complete for finished item of work.. | Civil | Labour | SWR33403 | 2310 | m2 | 277200
82 | 1 | Providing Consultancy services for arranging contour surveying with total station incuding preparation of boundary and contour levels with 2 Nos. Hard copies and soft copies complete for finished items of work | Civil | Labour | SWR33427 | 5665 | EA | 5665
83 | 222.2468 | Seigniorage Charges - Sand | Civil | Labour | SWR34470 | 40 | m3 | 8889.873
84 | 725.7496 | Seigniorage Charges - Metal | Civil | Labour | SWR34471 | 97.5 | m3 | 70760.585
85 | 839.38 | Seigniorage Charges - Gravel | Civil | Labour | SWR34472 | 30 | m3 | 25181.4
86 | 60 | Supply and fixing of RCC fencing poles of size 0.1mx0.1mx1.8m (security fencing of sub station), including cost and conveyance of all labour, materials,and hire chareges etc complete for finished item of work. | Civil | Labour | Swr33405 | 1444 | EA | 86640
87 | 1200 | Supply and fixing of galvanised barded wire (1 horizantal & 2 cross strands. including cost and conveyance of all labour, materials,and hire chareges etc complete for finished item of work. | Civil | Labour | Swr33408 | 16 | m | 19200
Civil labour | [7 empty] | 4232092.562
Electrical and Civil labour |  |  | 18% GST Rs. |  |  |  |  | 17838284.355

## 11. RDO Office
Name of the work: Estimate for erection of new 33/11kV outdoor sub-station at RDO Office with 2x8MVA PTRs and connected 33kV, 11kV Lines at RDO Office in Rajendranagar (M) in ECGH Division/Masterplan/RR Circle
WBS No. S-1796-13-03-02-01-001
Sl No | Estimate Quantity | Description of item | Work Type | Item Short Description | APSS / Month Cl.NumberSSR 11 & 12 | Rate (INR) | UOM | AMOUNT
1 | 16 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | ELEC | Labour | SWR11039 | 928 | EA | 14848
2 | 5.76 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ELEC | Labour | SWR10868 | 6852 | TO | 39467.52
3 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELEC | supply | SMR40009 | 2181 | TO | 12562.56
4 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELEC | labour | SWR10877 | 851 | TO | 4901.76
5 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELEC | supply | SMR40010 | 1293 | TO | 7447.68
6 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELEC | labour | SWR10879 | 482 | TO | 2776.32
7 | 5.76 | Fabrication & erection of Channels-Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ELEC | labour | SWR10867 | 1470 | TO | 8467.2
8 | 16 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-R.S. Joists 150 x 150 mm | ELEC | labour | SWR10348 | 1952.61 | EA | 31241.76
9 | 17.758 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 116829.882
10 | 9.24 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ELEC | labour | SWR10862 | 373 | M2 | 3446.52
11 | 16 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | ELEC | labour | SWR11089 | 48 | EA | 768
12 | 4 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-8.0Mtrs PSCC Poles 0.76 M x 0.76M x 1.52M (2.6" x 2.6" x 5.0') 0.88 cum | ELEC | labour | SWR11037 | 793 | EA | 3172
13 | 1 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ELEC | Labour | SWR10868 | 6852 | TO | 6852
14 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELEC | supply | SMR40009 | 2181 | TO | 2181
15 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELEC | labour | SWR10877 | 851 | TO | 851
16 | 1 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELEC | supply | SMR40010 | 1293 | TO | 1293
17 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELEC | labour | SWR10879 | 482 | TO | 482
18 | 1 | Fabrication & erection of Channels-Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ELEC | labour | SWR10867 | 1470 | TO | 1470
19 | 4 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Box pole 12 Mtr | ELEC | labour | SWR11267 | 3901.37 | EA | 15605.48
20 | 2.65 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 17434.35
21 | 2.31 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ELEC | labour | SWR10862 | 373 | M2 | 861.63
22 | 4 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | ELEC | labour | SWR11089 | 48 | EA | 192
23 | 5.063 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ELEC | labour | SWR10868 | 6852 | TO | 34691.676
24 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELEC | supply | SMR40009 | 2181 | TO | 11042.403
25 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELEC | labour | SWR10877 | 851 | TO | 4308.613
26 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELEC | labour | SMR40010 | 1293 | TO | 6546.459
27 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELEC | labour | SWR10879 | 482 | TO | 2440.366
28 | 5.063 | Fabrication & erection of Channels-Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ELEC | labour | SWR10867 | 1470 | TO | 7442.61
29 | 13 | Erection of AB Switch and aligment complete Erection of 33 KV AB Switch including alignment and earthing | ELEC | labour | SWR10392 | 4500 | EA | 58500
30 | 34 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Note:-The requirement of 2nd coat is to be justified by the concerned Divisional Engineer /Executive Engineer before execution of this work Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | ELEC | labour | SWR10881 | 142 | EA | 4828
31 | 34 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | ELEC | labour | SWR12331 | 146.63 | EA | 4985.42
32 | 6 | Loading of 33 KV CTs/ PTs | ELEC | labour | SWR10200 | 165 | EA | 990
33 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
34 | 6 | Un loading of 33 KV CTs/ PTs | ELEC | labour | SWR10518 | 128 | EA | 768
35 | 2 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33kv single phase PT s | ELEC | labour | SWR10401 | 1079 | SET | 2158
36 | 12 | Loading of 33 KV, 10 KA LAs Station typ | ELEC | labour | SWR10266 | 41 | EA | 492
37 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
38 | 12 | Un loading of 33 KV, 10 KA LAs Station type | ELEC | labour | SWR10584 | 35 | EA | 420
39 | 4 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33 KV LAS station/Line type including earthing | ELEC | labour | SWR10396 | 880 | SET | 3520
40 | 2 | Loading of 33 KV VCBs along with Panel boards | ELEC | labour | SWR10198 | 1024 | EA | 2048
41 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
42 | 2 | Un loading of 33 KV VCBs along with Panel boards | ELEC | labour | SWR10516 | 1044.48 | EA | 2088.96
43 | 12.584 | Excavate-Pit for 33KV VCB | ELEC | labour | SWR23224 | 331 | M3 | 4165.304
44 | 14.52 | Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x 1.8 x 0.75 cum for VCB Plinth | ELEC | labour | SWR20685 | 5160 | M3 | 74923.2
45 | 2 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33 KV VCB with Control Panel | ELEC | labour | SWR10460 | 12500 | EA | 25000
46 | 2 | Loading and unloading of PTR on constructed plinth-Loading of 8MVA PTR | ELEC | labour | SWR10613 | 5805.84 | EA | 11611.68
47 | 2 | Transport of Power transformers (0 to 100 KM) from one place to another place in GHMC Area.(excluding of loading & unloading )-8MVA power transformer | ELEC | labour | SWR10854 | 21945 | EA | 43890
48 | 2 | Loading and unloading of PTR on constructed plinth-Unloading of 8MVA PTR | ELEC | labour | SWR10627 | 5805.84 | EA | 11611.68
49 | 700 | S/o rail poles 90/105lb (250x2N) | ELEC | supply | SMR22718 | 47.27 | KG | 33089
50 | 14 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Rail pole 90 lbs | ELEC | labour | SWR10344 | 3510 | EA | 49140
51 | 2 | Erection of PTR on constructed plinth-Erection of 8 MVA PTR. | ELEC | labour | SWR21321 | 49480.2 | 49480.2 | 98960.4
52 | 0.436 | Extention of 33KV Bay at 132/33KV Sub-station-Zebra condutor | ELEC | supply | SMR24910 | 299369 | 299369 | 130524.884
53 | 30 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing | ELEC | supply | SMR11915 | 2055 | 2055 | 61650
54 | 30 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of I-Bolts | ELEC | supply | SMR22473 | 294 | 294 | 8820
55 | 45 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 "to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating . Sup T clamp LM6 Al alloy of 12 mm, 800 A | ELEC | labour | SMR40011 | 299 | 299 | 13455
56 | 6 | Bus stringing Hoisting of Insulators and hardware, stretching the conductor and stringing of 33 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bussection of 4.5mt) Hoisting post ins&hrd wr 1panther 33kv | ELEC | labour | SWR21240 | 781 | 781 | 4686
57 | 84 | Stringing of bus with panther conductor including jumpering etc., complete to all the equipment in SS fixing to all clamps and equipment.(3 Conductors) | ELEC | labour | SWR10404 | 327.68 | 327.68 | 27525.12
58 | 30 | Bus stringing Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | ELEC | labour | SWR10884 | 224 | 224 | 6720
59 | 75 | Labour for Fixing of all types of clamps | ELEC | labour | SWR10917 | 65 | 65 | 4875
60 | 25 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | ELEC | labour | SWR11039 | 928 | 928 | 23200
61 | 8.68 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ELEC | labour | SWR10868 | 6852 | 6852 | 59475.36
62 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELEC | supply | SMR40009 | 2181 | 2181 | 18931.08
63 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELEC | labour | SWR10877 | 851 | 851 | 7386.68
64 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELEC | supply | SMR40010 | 1293 | 1293 | 11223.24
65 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELEC | labour | SWR10879 | 482 | 482 | 4183.76
66 | 8.68 | Fabrication & erection of Channels-Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ELEC | labour | SWR10867 | 1470 | 1470 | 12759.6
67 | 25 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-R.S. Joists 150 x 150 mm | ELEC | labour | SWR10348 | 1952.61 | 1952.61 | 48815.25
68 | 27.75 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | 6579 | 182567.25
69 | 17.91 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ELEC | labour | SWR10862 | 373 | 373 | 6680.43
70 | 25 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | ELEC | labour | SWR11089 | 48 | 48 | 1200
71 | 4.642 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ELEC | labour | SWR10868 | 6852 | 6852 | 31806.984
72 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELEC | supply | SMR40009 | 2181 | 2181 | 10124.202
73 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELEC | labour | SWR10877 | 851 | 851 | 3950.342
74 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELEC | supply | SMR40010 | 1293 | 1293 | 6002.106
75 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELEC | labour | SWR10879 | 482 | TO | 2237.444
76 | 4.642 | Fabrication & erection of Channels-Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ELEC | labour | SWR10867 | 1470 | TO | 6823.74
77 | 17 | Erection of AB Switch and aligment complete-Erection of 11KV 800A double throw AB Switches | ELEC | labour | SWR21277 | 3500 | EA | 59500
78 | 3 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | ELEC | labour | SWR10393 | 3200 | EA | 9600
79 | 2 | Loading of 11 KV CT - PT Sets | ELEC | labour | SWR10201 | 190 | EA | 380
80 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
81 | 2 | Un loading of 11 KV CT - PT Sets | ELEC | labour | SWR10519 | 101 | EA | 202
82 | 2 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc-Erection of 11 KV three phase PTs | ELEC | labour | SWR10402 | 800 | SET | 1600
83 | 24 | Loading of 11 KV, 10 KA LAs Station type | ELEC | labour | SWR10264 | 32 | EA | 768
84 | 2 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 6599.4
85 | 24 | Un loading of 11 KV, 10 KA LAs Station type | ELEC | labour | SWR10582 | 32 | EA | 768
86 | 2 | Erection of 11 KV LAS station type including earthing | ELEC | labour | SWR10397 | 559 | SET | 1118
87 | 6 | Erection of 11 KV LAS line type including earthing | ELEC | labour | SWR10398 | 505 | SET | 3030
88 | 8 | Loading of 11 KV VCBs along with Panel boards | ELEC | labour | SWR10199 | 1024 | EA | 8192
89 | 4 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 13198.8
90 | 8 | Un Loading of 11 KV VCBs along with Panel boards | ELEC | labour | SWR10517 | 1044.48 | EA | 8355.84
91 | 41.6 | Excavate-Pit for 33KV VCB | ELEC | labour | SWR23224 | 331 | M3 | 13769.6
92 | 48 | Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x 1.8 x 0.75 cum for VCB Plinth | ELEC | labour | SWR20685 | 5160 | M3 | 247680
93 | 8 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc-Erection of 11 KV VCB with Control Panel | ELEC | labour | SWR10461 | 12000 | EA | 96000
94 | 12 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing | ELEC | supply | SMR11915 | 2055 | SET | 24660
95 | 12 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of I-Bolts | ELEC | supply | SMR22473 | 294 | EA | 3528
96 | 45 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 "to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating . Sup T clamp LM6 Al alloy of 12 mm, 800 A | ELEC | supply | SMR40011 | 299 | EA | 13455
97 | 2 | Bus Stringing -Hoisting of Insulators and hardware, stretching the conductor and stringing of 11 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 3.5mt) Hoisting post ins&hrd wr 1panther 11kv | ELEC | labour | SWR21241 | 507 | EA | 1014
98 | 63 | Stringing of bus with panther conductor including jumpering etc., complete to all the equipment in SS fixing to all clamps and equipment.(3 Conductors) | ELEC | labour | SWR10404 | 327.68 | M | 20643.84
99 | 45 | Bus stringing Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | ELEC | labour | SWR10884 | 224 | EA | 10080
100 | 57 | Labour for Fixing of all types of clamps | ELEC | labour | SWR10917 | 65 | EA | 3705
101 | 584 | Laying of earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication 75x 8mm MS Flat / GI Flat. Laying of earth mat,excavation 75x 8mm | ELEC | labour | SWR10920 | 65 | RMT | 37960
102 | 1010 | Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) Earthing for raisers of SS Flat 50x6 mm. | ELEC | labour | SWR10919 | 41 | RMT | 41410
103 | 36 | Supply of earthing pipe with materials -Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | ELEC | supply | SMR11482 | 3486 | EA | 125496
104 | 36 | Providing of Earthing-Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | ELEC | labour | SWR10357 | 1234.2 | EA | 44431.2
105 | 36 | Providing of RCC collar to earth pit-Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINES-Providing of RCC collar | ELEC | labour | SWR10359 | 386 | EA | 13896
106 | 2 | Supply of Copper Flexible jumper with 75 X 8 of length 250 mm at neutral of Power tranformer end and 50 X 6 of length 50mm two Nos at double neutral end duly brasing with flexible jumper of capacity of 5kA/3 sec for power transformer neutral. SupCU Flexi jumper for Power T/F Neutral | ELEC | supply | SMR40033 | 4725 | EA | 9450
107 | 2 | Providing of earthing with various types of earth electrodes-Providing of double earthing for neutral with flexible copper jumpers including arrangement by fixing M.S.Channel 100x50mm. | ELEC | labour | SWR11892 | 1323 | EA | 2646
108 | 80 | Providing of control cable trench as per DATA-XII | ELEC | labour | SWR22093 | 3148 | RMT | 251840
109 | 3074 | Control Cable-Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends . Lay-4C/10C 2.5Sqmm Control Cable | ELEC | labour | SWR11879 | 27 | M | 82998
110 | 270 | Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per specification (including cost of ferrules, lugs and glands) | ELEC | labour | SWR12510 | 27 | EA | 7290
111 | 4 | Marshalling Box Supply of FRP PT Marshalling Box | ELEC | supply | SMR40048 | 4463 | EA | 17852
112 | 4 | Marshalling Box Erection of Marshalling boxes | ELEC | labour | SWR10940 | 374.85 | EA | 1499.4
113 | 1 | Loading of 220 V Batterry with charger | ELEC | labour | SWR11166 | 1612 | SET | 1612
114 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
115 | 1 | Un loading of 220 V Batterry with charger | ELEC | labour | SWR11147 | 1024 | SET | 1024
116 | 1 | Batteries-Erection of 220 V, 200 AH battery in complete shape fit for charging . Conventional lead acid | ELEC | labour | SWR12350 | 7666 | EA | 7666
117 | 1 | Control Panels -Supply of DC Annunciation & relay panel for 10 feeder panel including the cost of LED Indiacation lamps, VAA auxilairy relays, Electronic Hooters complete as per specification. | ELEC | supply | SMR40044 | 42500 | EA | 42500
118 | 1 | Control Panels -Supply of AC Supply panel inluding providing of changeover switch, SFU, metering unit, 32 A three phase MCB, 16 A Single phase MCB complete as per specification. Supply of AC Supply panel complete | ELEC | supply | SMR40045 | 42000 | EA | 42000
119 | 2 | Fixing of AC/DC Panel and giving Connections to the protection equipment and Metering circuits as per the specification and standards. The 3 1/2 core 25 Sqmm power cable required from distribution box to AC/DC panel in the control room is also to be supply | ELEC | labour | SWR20025 | 7871.85 | SET | 15743.7
120 | 8 | Yard lightning-Supply of stepped tubular poles single way made of steel of length 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9 mm, 2.1 mtrs with outer dia 76.1 mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79 kgf as per IS 2713 | ELEC | supply | SMR40051 | 13913 | EA | 111304
121 | 8 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE/CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA /OSRAM /SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty S-90W LED fixture set | ELEC | labour | SMR11594 | 8200 | EA | 65600
122 | 8 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | ELEC | labour | SWR11039 | 928 | EA | 7424
123 | 8 | Erection of tubular poles | ELEC | labour | SWR10955 | 1379 | EA | 11032
124 | 5.27 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 34671.33
125 | 8 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE/CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA /OSRAM /SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty. Fixing of Metal halide lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5 GI pipe complete Fixing of LED/Metal halide complete. | ELEC | labour | SWR10956 | 1268 | EA | 10144
126 | 45 | Supply of HBG metal-Supply & spreading of 20mm machine crushed metal (HBG) including cost of conveneyance of all materials, labour charges etc complete for finished item of work and directed by the engineer incharge | ELEC | labour | SWR10860 | 2113 | M3 | 95085
127 | 2 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M Ex of Hard pit w/o blast 0.75X0.9X1.95M | ELEC | labour | SWR11040 | 990.68 | EA | 1981.36
128 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELEC | Supply | SMR40009 | 2181 | TO | 1635.75
129 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELEC | labour | SWR10877 | 851 | TO | 638.25
130 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELEC | Supply | SMR40010 | 1293 | TO | 969.75
131 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELEC | labour | SWR10879 | 482 | TO | 361.5
132 | 1 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Box pole 12 Mtr | ELEC | labour | SWR11267 | 3901.37 | EA | 3901.37
133 | 2.22 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 14605.38
134 | 1.16 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ELEC | labour | SWR10862 | 373 | M2 | 432.68
135 | 2 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | ELEC | labour | SWR11089 | 48 | EA | 96
136 | 1 | Construction of DTR Plinth-RCC Column type DTR Plinth of size 1'X1'X10',topslab 4'x4'x6" & beam size 4'X8'X8" upto 160KVA | ELEC | labour | SWR21843 | 25967.57 | EA | 25967.57
137 | 1 | Loading of 50,63, 75 & 100 KVA DTR | ELEC | labour | SWR10195 | 350 | EA | 350
138 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
139 | 1 | Un loading of 50,63, 75 & 100 KVA DTR | ELEC | labour | SWR10513 | 280 | EA | 280
140 | 1 | Erection of DTR's including loading and Unloading DTR on the Structure/Plinth etc-Erection of 3 Phase DTRs 63,75 & 100 KVA | ELEC | labour | SWR20905 | 1650 | EA | 1650
141 | 1 | Erection of AB Switch and aligment complete Erection of 11KV 200A TT type AB Switch including fixing of cross angles and alignment complete | ELEC | labour | SWR20102 | 1813.49 | EA | 1813.49
142 | 1 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erect. of 11kv HG Fuseset incl earthing | ELEC | labour | SWR10395 | 740.52 | SET | 740.52
143 | 40 | Excavation & laying of UG Cable in Single Run Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.-In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road-11KV 3x185 Sqmm Cable | ELEC | labour | SWR11920 | 465.46 | M | 18618.4
144 | 20 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-11 KV 3x185 Sqmm Cable | ELEC | labour | SWR11956 | 126.23 | M | 2524.6
145 | 2 | Making of Outdoor/Indoor End Termination Making 11 KV 3x185 Sqmm Cable Out Door/Indoor end termination | ELEC | labour | SWR10390 | 2370.63 | EA | 4741.26
146 | 1 | Erection of LT distribution box including laying of LT cable from distribution box to LT OH line and DTR to distribution box including earthing of distribution box and crimping of lugs connecting of jumpers etc | ELEC | labour | SWR10674 | 1594.67 | EA | 1594.67
147 | 85 | LAYING OF 33KV, 11KV UG CABLE Excavation & laying of UG Cable in Single Run Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road-LT 3 1/2 x 185 Sqmm Cable | ELEC | labour | SWR11923 | 377.63 | M | 32098.55
148 | 15 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-LT 3 1/2 x 185 Sqmm Cable | ELEC | labour | SWR11959 | 85.43 | M | 1281.45
149 | 2 | UG Cables Joints :-Making of Outdoor/Indoor End Termination -Supply & fixing of Oout Door/Indoor end termination LT 3 1/2 x 185 Sqmm Cable | ELEC | labour | SWR10765 | 968.9 | EA | 1937.8
150 | 1 | Supply and fixing of Substation board of size 3'x2.5' indicating the layout of switchyard Sup &fix of board ind Switchyard layout | ELEC | labour | SWR20032 | 1654 | EA | 1654
151 | 1 | Supply and fixing of safety instructions/Substation operation instruction board. Sup& fix safety inst/SS Op. inst board | ELEC | labour | SWR22090 | 2205 | EA | 2205
152 | 750 | Control Panels Supplying & fabrication erection of 6mm Checkerd plates as per the field conditions Supply,fabricati of 6mm Checkerd plates | ELEC | Labour | SWR10873 | 83 | KG | 62250
153 | 1 | T & P Supply of Wall clock standard make | ELEC | Supply | SMR40059 | 578 | EA | 578
154 | 1 | S-10ft Aluminium Ladder | ELEC | Supply | SMR12378 | 1654 | EA | 1654
155 | 1 | Sup Alluminium Ladder for indoor works | ELEC | Supply | SMR40062 | 4410 | EA | 4410
156 | 30 | T & P Painting of Name Plates for any equipmen | ELEC | labour | SWR10963 | 122 | EA | 3660
157 | 1 | T & P Supply of Taparia Tool kit of Size 20”x10”x15” with tier arrangements Tool box with locking arrangement & key containing (1) Double Ended fix Spanner sets, (Ribbed) 6 x 7, 8 x 9, 10 x 11, 12 x 13, 14 x 15, 16 x 17, 18 x19, 20 x 22, 21 x 23, 24 x 27, 25 x28, 30 x 32, (2) Double Ended Ring Spanners sets, 6 x 7 , 8 x 9, 10 x 11, 12 x 13, 14 x 15. 16 x 17 , 18 x 19, 20 x 22 , 21 x 23, 24 x 27, 25 x28, 30 x 32 mm, (3) Adjustable Spanner 305 mm length least maximum opening 35mm chrome, (4) Pipe Wrench Length 350 mm 14”, (5) Soft faced Hammer with suitable handle 2 lb, (6) Hacksaw frame with metal handle heavy duty for 12" hacksaw blade with High Speed blade, (7) Insulated Screw drivers Transparent Green Handle Set Length 6”, 8” & 12”, (8) Star Screw Driver Transparent Green Handle Length 6”, (9) Insulated Wire Cutter, (10) Insulated Cutting Plier Length 8” with cable stripper insulated with thick C. A. sleeve confirming to IS: 4378 - 1990, (11) Long Nose Plier insulated with thick C.A. sleeve generally confirming to IS:3552-1989, (12) Tester type screw driver (special with neon bulb) generally confirm to IS: 5579- 1985 Grade:II handle yellow/ green colour overall length 130 mm, (13) Insulated Crimping Plier of all Taparia make. SupTaparia Tool kit complete as per Spec | ELEC | Supply | SMR40063 | 4925 | SET | 4925
158 | 1 | T & P Sup Rechargeable LED torch light of Standard make | ELEC | Supply | SMR40064 | 1733 | EA | 1733
159 | 1 | T & P-Steel almarah(61/2 X 3ft) Godrej | ELEC | Supply | SMR40061 | 9818 | EA | 9818
160 | 1 | T & P-Table (3x6ft) Godrej | ELEC | Supply | SMR40057 | 6050 | EA | 6050
161 | 4 | T & P-S type chairs (Godrej) | ELEC | Supply | SMR40058 | 924 | EA | 3696
162 | 1 | T & P Sup Angle racks(18x36.6inches) Godrej | ELEC | Supply | SMR40060 | 1733 | EA | 1733
163 | 1 | T & P Supply of Hack saw (12 inches) | ELEC | Supply | SMR40065 | 289 | EA | 289
164 | 4 | Sup Earth Rods (8ft) Screw & clamp type | ELEC | Supply | SMR40066 | 578 | EA | 2312
165 | 2 | Supply of Hand Gloves | ELEC | Supply | SMR40067 | 289 | SET | 578
166 | 12 | SupRubber mats( 6'x3')size fo indoorSS | ELEC | Supply | SMR40068 | 1386 | EA | 16632
167 | 1 | Biometric Time attendence System & Telecom Sup Stand basic cell phone with charger | ELEC | Supply | SMR40069 | 1386 | EA | 1386
168 | 14 | Supply of Danger boards with clamps | ELEC | Supply | SMR40070 | 116 | EA | 1624
169 | 2 | Supply of Materials -Fire bucket stand with 3 buckets (8 -10 ltr capacity) | ELEC | Supply | SMR40088 | 1386 | SET | 2772
170 | 2 | Room fire extinguisher (2 ltrs capacity) for control room | ELEC | Supply | SMR40089 | 4620 | EA | 9240
171 | 4 | Sup TrollyMounted Co2 (6.5Kgs) Cylinders(IS-2878) | ELEC | Supply | SMR40087 | 9240 | EA | 36960
172 | 6 | Supply of Safety Helmet of standard make | ELEC | Supply | SMR40071 | 231 | EA | 1386
173 | 8 | Supply of LC Boards | ELEC | Supply | SMR40072 | 116 | EA | 928
174 | 4 | Supply of Gum Boots(Pairs) | ELEC | Supply | SMR40073 | 693 | EA | 2772
175 | 1 | Supply of 5000v megger | ELEC | Supply | SMR40074 | 13860 | EA | 13860
176 | 1 | Supply of Earth megger (1000v) | ELEC | Supply | SMR40075 | 8085 | EA | 8085
177 | 1 | Supply of Digital clamp meter. | ELEC | Supply | SMR40076 | 2888 | EA | 2888
178 | 1 | Name board of the 33/11kV Sub-Station(As per Standard Specification) Sup 33/11kv S.S Permanent name board | ELEC | Supply | SMR40086 | 10238 | EA | 10238
179 | 800 | Supply of Hot dip galvanized/zinc coated bolts & nuts including spring washers, pack washers and flat washers etc. | ELEC | Supply | SMR12488 | 90 | KG | 72000
180 | 2 | Fabrication of poles-Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | ELEC | labour | SWR10642 | 512.55 | EA | 1025.1
181 | 1 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-RS Joists 150x75/175 x 85 mm | ELEC | labour | SWR10346 | 1934 | EA | 1934
182 | 5760 | S-Supply of RS Joist Grider Pole (150x150mm) | ELEC | Supply | SMR12302 | 59.25 | KG | 341280
183 | 1000 | S-Supply of RS Joist Pole (175x85mm) | ELEC | Supply | SMR12303 | 60.75 | KG | 60750
184 | 5063 | S- Supply of MS Channel 100x50mm | ELEC | Supply | SMR22745 | 57.45 | KGS | 290869.35
185 | 13 | S-Supply of 33KV 800A DB Break AB Switch | ELEC | Supply | SMR12315 | 40658.78 | EA | 528564.14
186 | 8680 | S-Supply of RS Joist Grider Pole (150x150mm) | ELEC | Supply | SMR12302 | 59.25 | KG | 514290
187 | 4642 | S- Supply of MS Channel 100x50mm | ELEC | Supply | SMR22745 | 57.45 | KGS | 266682.9
188 | 17 | S-Supply of 11KV 800A DB Break AB Switch | ELEC | Supply | SMR12316 | 30847.46 | EA | 524406.82
189 | 3 | S-Supply of 11KV 400A DB Break AB Switch | ELEC | Supply | SMR12317 | 18150 | EA | 54450
190 | 3045 | S-Supply of MS Flat 75x8mm | ELEC | Supply | SMR12321 | 56.42 | KG | 171798.9
191 | 2666 | S-Supply of MS Flat 50x6mm | ELEC | Supply | SMR12322 | 56.5 | KG | 150629
192 | 750 | S-Supply of RS Joist Pole (175x85mm) | ELEC | Supply | SMR12303 | 60.75 | KG | 45562.5
193 | 1 | S-Supply of 11KV 200A Tilting Type AB Switch | ELEC | Supply | SMR12318 | 8991 | EA | 8991
194 | 1 | S-Supply of 11KV HG FuseSet for StationTransformer | ELEC | Supply | SMR12324 | 1974 | EA | 1974
195 | 1 | S-Supply of LT Distribution Box (SMC) | ELEC | Supply | SMR25200 | 7797 | EA | 7797
196 | 2 | S-Supply of 11KV 3x185 Heat Shble O/d End Term Kit | ELEC | Supply | SMR25201 | 1182.97 | EA | 2365.94
197 | 40 | S-Supply of LT XLPE Cable 1C 150 sqmm | ELEC | Supply | SMR25203 | 114.83 | M | 4593.2
198 | 100 | Supply of LT XLPE Cable 31/2C185sqmm. | ELEC | Supply | SMR25204 | 547 | M | 54700
199 | 4 | Loading of LT AB Cable 3X16+25 Sqmm | ELEC | labour | SWR11702 | 200 | DR | 800
200 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELEC | labour | SWR11861 | 3299.7 | EA | 3299.7
201 | 4 | Un loading of LT AB Cable 3X16+25 Sqmm | ELEC | labour | SWR11713 | 204 | DR | 816
202 | 2 | survey line&cabl inc peg mark&tree clear | ELEC | labour | SWR22092 | 765 | KM | 1530
203 | 2 | Paving out and stringing of conductor by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location-100 Sqmm Single Circuit (3 Conductors) | ELEC | labour | SWR10366 | 13856.7 | KM | 27713.4
204 | 40 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M Ex of Hard pit w/o blast 0.75X0.9X1.95M | ELEC | labour | SWR11040 | 990.68 | EA | 39627.2
205 | 40 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Errection of 11 M long PSCC pole | ELEC | labour | SWR10978 | 4336.85 | EA | 173474
206 | 14.672 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 96527.088
207 | 40 | Painting of poles-Numbering of poles incl. cost of paint | ELEC | labour | SWR10378 | 32 | EA | 1280
208 | 16 | Excavation of pits in all soils except hard rock requiring blasting-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") 1.05 cum | ELEC | labour | SWR10107 | 700 | EA | 11200
209 | 16 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Erec of 9.1 Mts PSCC poles for stuts | ELEC | labour | SWR11083 | 2400 | EA | 38400
210 | 8.4 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 55263.6
211 | 8 | Formation of Cut points - Formation of Cut point for 11 KV Single Circuit line excluding pole erection and stays Formatn of Horiz Cut point for 11KV line | ELEC | labour | SWR10653 | 1435.81 | EA | 11486.48
212 | 50 | Supply of earthing pipe with materials S-GI Bolts & Nuts,Washers etc., | ELEC | supply | SMR11488 | 117.5 | KG | 5875
213 | 2 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 50 Km and upto 80 Km with Lorry for each trip | ELEC | labour | SWR11864 | 5290.74 | EA | 10581.48
214 | 2 | LOADING of Conductor drums | ELEC | labour | SWR10191 | 202 | EA | 404
215 | 2 | UNLOADING of Conductor drums | ELEC | labour | SWR10509 | 100 | EA | 200
216 | 15 | Loading of 33 KV Pin insulators | ELEC | labour | SWR10211 | 3 | CRT | 45
217 | 15 | Un loading of 33 KV Pin insulators | ELEC | labour | SWR10529 | 3 | CRT | 45
218 | 3 | Loading of 33 KV Metal parts | ELEC | labour | SWR10618 | 65 | BAG | 195
219 | 3 | Un loading of 33 KV Metal parts | ELEC | labour | SWR10632 | 65 | BAG | 195
220 | 710 | Excavation & laying of UG Cable (Double Run) Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, Along the CC / BT multi layer road requiring compressor-33 KV 3x400 Sqmm Cable | ELEC | labour | SWR11980 | 1388.84 | M | 986076.4
221 | 710 | Laying of 2nd cable in excavated trench | ELEC | labour | SWR10988 | 204.1 | M | 144911
222 | 40 | Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-33 KV 3x400 Sqmm Cable | ELEC | labour | SWR12004 | 323.85 | M | 12954
223 | 12 | Cost of Pipes and slabs-Supply of 6" B class GI pipe | ELEC | supply | SMR40081 | 1044 | M | 12528
224 | 30 | Cost of Pipes and slabs-Supply of 250 mm Hume pipe of class NP3 with compresive strength of 35N/mm2 for 28 days curing,barewall thickness of 30mm,1.25kG linear/meter and withstanding capability of 22.50KN/linear meter as per IS 458-1993. | ELEC | supply | SMR40077 | 363 | M | 10890
225 | 6 | Cost of Pipes and slabs-Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters , CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | ELEC | supply | SMR40085 | 484 | EA | 2904
226 | 5 | Load-11/33KV XLPE UG Cable for all sizes | ELEC | labour | SWR11230 | 1024 | DR | 5120
227 | 5 | Unload-11/33KV XLPE UG Cable for all sizes | ELEC | labour | SWR11231 | 1024 | DR | 5120
228 | 8 | Making of Outdoor/Indoor End Making 33 KV 3x400 Sqmm Cable Out Door/Indoor end termination TerminationOD/Idoor end termination 33kv 3x400 xlpe | ELEC | labour | SWR10387 | 2764.76 | EA | 22118.08
229 | 2 | UG Cables Joints 33 KV 3x400 Sqmm Cable Straight through joint 33kv 3x400 xlpe | ELEC | labour | SWR10382 | 5700.78 | EA | 11401.56
230 | 0.8 | Fabrication & erection of Channels -Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to theRS-Joist poles excluding cost of Mild Steel and transportcharges to substation site, including erection. Fabrication of struc.with welding. | ELEC | labour | SWR10869 | 3426 | TO | 2740.8
231 | 50 | Supply of earthing pipe with materials-Supply of GI wire No 8 | ELEC | supply | SMR11486 | 105 | KG | 5250
232 | 2 | Supply of earthing pipe with materials-Supply of CI eath pipe with 80mm dia,2.0 M Length | ELEC | labour | SMR11483 | 2789 | EA | 5578
233 | 2 | Providing of Earthing-Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | ELEC | labour | SWR10357 | 1234.2 | EA | 2468.4
234 | 2 | Providing of RCC collar to earth pit-Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINES-Providing of RCC collar | ELEC | labour | SWR10359 | 386 | EA | 772
235 | 40 | Supply of earthing pipe with materials-Supply of GI Flat 25X3 mm | ELEC | supply | SMR11485 | 105 | KG | 4200
236 | 20 | Supply of Danger boards with clamps | ELEC | supply | SMR40070 | 116 | EA | 2320
237 | 6 | S&E-Smart RFID marker | ELEC | labour | SWR25089 | 2745 | EA | 16470
238 | 16 | Supply of PSCC Pole 9.1Mtr 280KG | ELEC | supply | SMR25233 | 3109.41 | EA | 49750.56
239 | 500 | Supply of Materials -- Supply of MS Channel 100X50mm | ELEC | supply | SMR22745 | 57.45 | KGS | 28725
240 | 200 | Supply of MS Angle 65x65x6 | ELEC | supply | SMR25207 | 57.25 | KG | 11450
241 | 100 | Supply of Materials -- Supply of MS Flat 75x8 mm | ELEC | supply | SMR12321 | 56.42 | KG | 5642
242 | 8 | UG Cables Joints : Making of Outdoor/Indoor End Termination -- Supply 33KV 3x400Sqmm Outdoor | ELEC | supply | SMR22222 | 4554 | EA | 36432
243 | 2 | UG Cables Joints : Making of Straight through joints -- Supply of 33KV 3x400SQmm Straight Through Joint Kit | ELEC | supply | SMR22223 | 24151 | EA | 48302
244 | 40 | Supply of PSCC Pole 11Mtr 365KG | ELEC | supply | SMR25236 | 5399 | EA | 215960
245 | 32 | Supply of 33KV V-Cross Arm without Clamps | ELEC | supply | SMR25229 | 1678 | EA | 53696
246 | 9 | survey line&cabl inc peg mark&tree clear | ELEC | labour | SWR22092 | 765 | KM | 6885
247 | 9 | Paving out and stringing of conductor by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location-55 Sqmm Single Circuit (3 Conductors) | ELEC | labour | SWR10365 | 9454.81 | KM | 85093.29
248 | 175 | Excavation of pits in all soils except hard rock requiring blasting-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") 1.05 cum | ELEC | labour | SWR10107 | 700 | EA | 122500
249 | 50 | Excavation of pits in hard rock requiring blasting. (other than SS)-9.1Mtrs PSCC Pole 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | ELEC | labour | SWR10112 | 1770 | EA | 88500
250 | 213 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-9.1 M long PSCC pole | ELEC | labour | SWR10343 | 2400 | EA | 511200
251 | 37.8 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 248686.2
252 | 225 | Painting of poles-Numbering of poles incl. cost of paint | ELEC | labour | SWR10378 | 32 | EA | 7200
253 | 80 | Excavation of pits in all soils except hard rock requiring blasting-Stud Poles 0.6 M x 0.9 M x 1.5 M | ELEC | labour | SWR10106 | 645 | EA | 51600
254 | 80 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-8.0 m long PSCC poles for Strut | ELEC | labour | SWR21590 | 1500 | EA | 120000
255 | 32 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELEC | labour | SWR10356 | 6579 | M3 | 210528
256 | 40 | Formation of Cut points - Formation of Cut point for 11 KV Single Circuit line excluding pole erection and stays Formatn of Horiz Cut point for 11KV line | ELEC | labour | SWR10653 | 1435.81 | EA | 57432.4
257 | 350 | Supply of earthing pipe with materials S-GI Bolts & Nuts,Washers etc., | ELEC | supply | SMR11488 | 117.5 | KG | 41125
258 | 4 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 50 Km and upto 80 Km with Lorry for each trip | ELEC | labour | SWR11864 | 5290.74 | EA | 21162.96
259 | 4 | LOADING of Conductor drums | ELEC | labour | SWR10191 | 202 | EA | 808
260 | 4 | UNLOADING of Conductor drums | ELEC | labour | SWR10509 | 100 | EA | 400
261 | 6 | Supply of earthing pipe with materials-Supply of CI eath pipe with 50mm dia,2.0 M Length | ELEC | supply | SMR11484 | 2441 | EA | 14646
262 | 6 | Providing of Earthing-Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | ELEC | labour | SWR10357 | 1234.2 | EA | 7405.2
263 | 6 | Providing of RCC collar to earth pit-Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINES-Providing of RCC collar | ELEC | labour | SWR10359 | 386 | EA | 2316
264 | 6 | Assembly and erection of Structure as per specification which includes fixing of top channels and cross bracings, transport of all materials from road side to the location, earthing, back filling with earth ramming etc excluding pit excavation and concreting.-11KV DP Structure with 9.1 Mtrs PSCC Poles | ELEC | labour | SWR21130 | 3363.96 | SET | 20183.76
265 | 6 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | ELEC | labour | SWR10393 | 3200 | EA | 19200
266 | 6 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | ELEC | labour | SWR10881 | 142 | EA | 852
267 | 50 | Supply of earthing pipe with materials-Supply of GI wire No 8 | ELEC | supply | SMR11486 | 105 | KG | 5250
268 | 675 | Loading of 11KV Polymer Pin Insulators with GI pins | ELEC | labour | SWR11248 | 1 | EA | 675
269 | 675 | Un loading of 11KV Polymer Pin Insulators with GI pins | ELEC | labour | SWR11249 | 1 | EA | 675
270 | 240 | Loading of 11KV Polymer Pin Insulators with GI pins | ELEC | labour | SWR11248 | 1 | EA | 240
271 | 240 | Un loading of 11KV Polymer Pin Insulators with GI pins | ELEC | labour | SWR11249 | 1 | EA | 240
272 | 6 | Loading of 11 KV Metal parts | ELEC | labour | SWR12402 | 48 | BAG | 288
273 | 6 | Un loading of 11 KV Metal parts | ELEC | labour | SWR12421 | 48 | BAG | 288
274 | 960 | Laying of 2nd cable in excavated trench | ELEC | labour | SWR10988 | 204.1 | M | 195936
275 | 72 | Cost of Pipes and slabs-Supply of 6" B class GI pipe | ELEC | supply | SMR40081 | 1044 | M | 75168
276 | 200 | Cost of Pipes and slabs-Supply of 250 mm Hume pipe of class NP3 with compresive strength of 35N/mm2 for 28 days curing,barewall thickness of 30mm,1.25kG linear/meter and withstanding capability of 22.50KN/linear meter as per IS 458-1993. | ELEC | supply | SMR40077 | 363 | M | 72600
277 | 6 | Cost of Pipes and slabs-Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters , CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | ELEC | supply | SMR40085 | 484 | EA | 2904
278 | 5 | Load-11/33KV XLPE UG Cable for all sizes | ELEC | labour | SWR11230 | 1024 | DR | 5120
279 | 5 | Unload-11/33KV XLPE UG Cable for all sizes | ELEC | labour | SWR11231 | 1024 | DR | 5120
280 | 1.1 | Fabrication & erection of Channels -Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to theRS-Joist poles excluding cost of Mild Steel and transportcharges to substation site, including erection. Fabrication of struc.with welding. | ELEC | labour | SWR10869 | 3426 | TO | 3768.6
281 | 50 | Supply of Danger boards with clamps | ELEC | supply | SMR40070 | 116 | EA | 5800
282 | 6 | S&E-Smart RFID marker | ELEC | labour | SWR25089 | 2745 | EA | 16470
283 | 960 | Excavation & laying of UG Cable (Double Run)-Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts,-In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil/CC-11 KV 3x300 Sqmm Cable | ELEC | labour | SWR11973 | 631.06 | M | 605817.6
284 | 240 | Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-11 KV 3x300 Sqmm Cable | ELEC | labour | SWR12005 | 275.4 | M | 66096
285 | 6 | UG Cables Joints Making of Straight through joints-11 KV 3x300 Sqmm Cable | ELEC | labour. | SWR10386 | 3725.45 | EA | 22352.7
286 | 24 | Making of Outdoor/Indoor End Termination-Making 11 KV 3x300 Sqmm Cable Out Door/Indoor end termination | ELEC | labour. | SWR10391 | 2370.63 | EA | 56895.12
287 | 225 | Supply of PSCC Pole 9.1Mtr 280KG | ELEC | supply | SMR25233 | 3109.41 | EA | 699617.25
288 | 80 | Supply of PSCC Pole 8Mtr 140KG | ELEC | supply | SMR25232 | 1580 | EA | 126400
289 | 185 | Supply of 33KV V X- Arm with MS Channel 75x40 | ELEC | supply | SMR25219 | 561 | EA | 103785
290 | 185 | S-Supply of 11KV Top Cleat for 9.1M(Vertical) | ELEC | Supply | SMR25226 | 256 | EA | 47360
291 | 80 | Supply of 11KV Horizontal Cross Arm | ELEC | supply | SMR25223 | 528 | EA | 42240
292 | 6 | Supply of Materials -- Supply of 11 kV 400 A Double break AB switch | ELEC | supply | SMR12317 | 18150 | EA | 108900
293 | 200 | Supply of Materials -- Supply of MS Flat 50x6 mm | ELEC | supply | SMR12322 | 56.5 | KG | 11300
294 | 400 | Supply of MS Angle 50x50x6 | ELEC | supply | SMR25206 | 58.15 | KG | 23260
295 | 500 | Supply of MS Channel 75x40 mm | ELEC | supply | SMR25205 | 58.45 | KG | 29225
296 | 24 | Supply of 11KV 3x300 Heat Shble O/d End Term Kit | ELEC | supply | SMR25208 | 1372.88 | EA | 32949.12
297 | 6 | Supply of 11KV 3x300 Heat Shble stright through joint Kit | ELEC | supply | SMR25210 | 4110.17 | EA | 24661.02
Electrical labour | [7 empty] | 12789720.383
Civil labour - WBS. No. S-1796-13-07-01-01-001
Sl.No. | Estimate Quantity (only Figures) | Item Detailed Specification Description | Work Type eg. Earth Work, Electrical works. etc (upto 200 Characters) | Item Short Description (upto 100 Characters) | APSS / Morth Cl. Number (upto 200 Characters) | Rate (INR) (Upto 2 Decimals ) | UOM (upto 50 Characters) | Amount
1 | 32 | Leveliing the site by cutting and levelling with the help of JCB including cost,conveyance of all materials,hire chareges etc complete for finished item of work as directed by Engineer-in-charge. | Civil | Labour | SWR34179 | 2165 | Hrs | 69280
2 | 135.61 | Earth work excavation in all type of ordinary soils red earth, Hard gravelly soils, earth mixed with sand and sandy soils etc., in all conditions such as slushy and dry with initial leads and lifts for foundations. | Civil | Labour | SWR33015 | 486 | m3 | 65906.46
3 | 32.45 | Plain Cement concrete PCC (1:4:8) using 40mm HBG metal for foundations and leveling course, including cost and conveyance of all materials, labour all leads and lifts, consolidation and all operations, formwork as required, curing, etc. complete for finished item w | Civil | Labour | SWR33028 | 4676 | m3 | 151736.2
4 | 117.88 | Coursed Rubble stone (CRS) masonry 2nd sort with hard granite stones in cement mortar (1:6) for basement, including cost and conveyance of all materials, labour charges, curing, all leads and lifts, etc, complete for finished item of work. | Civil | Labour | SWR33041 | 4824 | m3 | 568653.12
5 |  | 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge
6 | 3.564 | RCC M20 Grade footing 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33098 | 9428 | m3 | 33601.392
7 | 2.28 | RCC M20 Grade Coloumn . 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33100 | 13177 | m3 | 30043.56
8 | 2.25 | RCC M20 Grade Plinth beams 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33099 | 12299 | m3 | 27672.75
9 | 3.17 | D) RCC M20 Grade Roof Beams landing beam 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33121 | 12215 | m3 | 38721.55
10 | 0.58 | e)RCC M20 Grade Lintels 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33107 | 13007 | m3 | 7544.06
11 | 2.7 | f) RCC M20 Grade Sunshades 600mm wide and 75mm thick'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33114 | 1371 | m2 | 3701.7
12 | 15.224 | g) RCC M20 Grade Roof Slab for Control Room 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33128 | 10803 | m3 | 164464.872
13 | 3 | Reinforcement steelSupplying, Cutting, bending, binding, placing in position and tying reinforcement steel in all heights including cost and conveyance of steel and binding wire etc,. With all leads and lifts, labour charges, etc., complete for finished item of work. | Civil | Labour | SWR33144 | 70687 | Ton | 212061
14 | 38.36 | Brick masonry in cement mortar CM (1:6) for superstructure using well burnt country made second class bricks of approved quality including cost and conveyance of all materials curing, scaffolding with all leads and lifts in all heights etc., complete for fin | Civil | Labour | SWR33068 | 8242 | m3 | 316163.12
15 | 2.7 | Plain Cement concrete PCC (1:2:4) using 20mm size well graded HBG metal for foundations, including cost, conveyance of all materials,labour all leads and lifts,consolidation and all operations, formwork as required, curing,etc. complete for finished item of work | Civil | Labour | SWR33030 | 6046 | m3 | 16324.2
16 | 606.06 | Plastering with CM 2 coats, 20 mm thick, base coat in CM (1:6), 16 mm thick and top coat in CM (1:4), 4mm thick with Dubara sponze finishing including cost of all materials, seigniorage charges, excluding conveyance charges of materials and including all operational, incidental and labour charges for mixing mortar, laying rendering smooth and thread lining, curing, rounding off junctions of wall and slab etc., complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33163 | 559 | m2 | 338787.54
17 | 349.515 | Painting with two coats of Plastic Emulsn paint over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33356 | 210 | m2 | 73398.15
18 | 200.85 | Painting with two coats of Surya Cem paint over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33329 | 85 | m2 | 17072.25
19 | 3 | Supply and Fixng of MS Name Board including cost & conveyance of all materials,labour charges etc complete for finished item of work. | Civil | Labour | SWR33421 | 4326 | m2 | 12978
20 | 1 | Geophysical Investgation charges for water point by Geologist | Civil | Labour | SWR33608 | 5000 | EA | 5000
21 |  | Drilling of 165mm bore well with machine rig including deployment and hire charges of rig and other machinery and equipment labour charges , measuring the yeild of borewell including cost and conveyance etc complete
22 | 90 | Drill-165mm Bore Well 0 to 90 | Civil | Labour | SWR33609 | 336 | M | 30240
23 | 30 | Drill-165mm Bore Well 90M to 120M | Civil | Labour | SWR34830 | 369 | M | 11070
24 | 30 | Drill-165mm Bore Well 120M to 150M | Civil | Labour | SWR34831 | 394 | M | 11820
25 | 30 | Drill-165mm Bore Well 150M to 180M | Civil | Labour | SWR34832 | 492 | M | 14760
26 | 30 | Drill-165mm Bore Well 180M to 210M | Civil | Labour | SWR34833 | 623 | M | 18690
27 | 30 | Drill-165mm Bore Well 210M to 240M | Civil | Labour | SWR34834 | 754 | M | 22620
28 | 30 | Drill-165mm Bore Well 240M to 270M | Civil | Labour | SWR34835 | 918 | M | 27540
29 | 95 | Drill-165mm Bore Well 270M and above | Civil | Labour | SWR34836 | 1082 | M | 102790
30 | 40 | Supply and fixing of 160mm dia PVC casing of A class 6Kg point pressure including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR33611 | 883 | M | 35320
31 | 1 | Supply and erecting, ISI mark submersible 5.0 HP, Single Phase 30 stages pumpset suitable for 106/156mm dia borewell including cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33640 | 48007 | EA | 48007
32 | 330 | Supply and fixing of HDPE pipe 40mm dia of 16Kg/cm2 including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR34410 | 180 | M | 59400
33 | 1 | Supply and erecting D.O.L Starter 415V , Single phase,50Hz with SS enclouserincluding cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33645 | 7854 | EA | 7854
34 | 340 | Supply of 3 Core 2.5 Sqmm Flat Copper cable of ISI for Submersible Motors of makes Finolex / Polycab / Gold Medal / Million / Payal / Sun Light / Power Flex / Fortune Art | Civil | Labour | SWR33641 | 192 | m | 65280
35 | 71 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-28.60mm OD Pipe - SDR 11 | Civil | Labour | SWR34363 | 410 | m | 29110
36 | 35 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type - 25mm NB Size | Civil | Labour | SWR34346 | 466 | EA | 16310
37 | 839.38 | Supplying and filling the substation site with borrowed gravel, watering, ramming, thoroughly complying with the standard specification. | Civil | Labour | SWR33052 | 309 | m3 | 259368.42
38 | 16.56 | Providing Design R.C.M. drop wall of 25mm thickness with cm 1:3 and 6mm dia MS bars at 150mm both ways and chicken mesh in two coats 20mm thick each plastering including cost and conveyance of all materials with leads and lifts, scaffolding and curing, labo | Civil | Labour | SWR33203 | 3035 | m2 | 50259.6
39 | 12.24 | Supply and fixing of Ms ornamental safety grill of approved design including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33310 | 2990 | m2 | 36597.6
40 | 5.91 | Supply and fixing of doors with the MT Wood frames of the door shall be made well seasoned mt wood of cross section 100x75mm. The shutter shall be made isi mark flushed door with decolam sheets pasted on both sides with PVC beading 40mm width all round.Frame shall be painted with two coats of synthetic enamel paint of approved color over one coat of primer over luppum with spary with 3 no 150mm brass hinges 1 no brass door stoper, 1 no 250mm brass aldrops. 2 no 300 mm aluminium tower bolts, 2 no 150mm brass fancy door handlers, 1 no keyless lockset with cp handel. The quoted rate shall include cost and conveyance of the meterials, fixig, labour carges, tools, handles,locking arrangementts and other fixtures & fittings for finished item work as directed by the Engineer - in- charge. | Civil | Labour | SWR33264 | 7314 | m2 | 43225.74
41 | 128.25 | Raised pointing to the exposed surfaces of CRS masonry in cm 1:3 prop. including cost and conveyance of all materials, labour charges, all leads and lifts curing etc, complete for finished item of work. | Civil | Labour | SWR33184 | 124 | m2 | 15903
42 | 8.64 | Supplying and fixing Aluminium sliding windows with grill and fixed glass panels using anodised aluminium extruded sections of mat finish for frames and mullions made from approved aluminium sections 62x32x1.2mm at 0.73kg/Rm providing 5mm plain glass fix | Civil | Labour | SWR33277 | 3623 | m2 | 31302.72
43 | 16.56 | Supply and laying of Ceramic floor over of CM 1:3 20 mm thick including required materials and labour charges etc complete for item of work | Civil | Labour | SWR33224 | 914 | m2 | 15135.84
44 | 121.92 | Flooring with double machine polished and hand cut Tandur blue stone 20mm thick of approved colour, quality and of minimum of 300x300mm size over a bed of cement mortar 1:3 20mm thick including cost of all materials, with all leads and lifts jointing and | Civil | Labour | SWR33219 | 785 | m2 | 95707.2
45 | 6.74 | Supply and fixing of 4" high skirting of shabad stone to the walls including cost and conveyance of all materials, labour etc for finished item of work. | Civil | Labour | SWR33236 | 875 | m2 | 5897.5
46 | 243.69 | Painting with two coats of OBD over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials labour charges etc., complete for finished item of work. | Civil | Labour | SWR33333 | 146 | m2 | 35578.74
47 | 101.17 | Providing impervious coat over RCC roof slab to requried slopes with 20mm thick in CM 1:3 mixed with approved brand of water proffing compound inclding cost and conveyance of all materials, labour charges, curing, rounding off junctions of wall and slab, all leads and lifts, etc . complete for finished item of work as directed by the Engineer - in - charge. | Civil | Labour | SWR33156 | 582 | m2 | 58880.94
48 | 60 | Supply & fixing of 25mm dia 2mm thick suSupply & fixing of 25mm dia 2mm thick surface P.V.C. pipe (ISI MARK) Concealed in wall with all required accessories including masonary work and labour charges etc.complete. | Civil | Labour | SWR33441 | 108 | m | 6480
49 | 1 | Supply & fixing TPN Distribution board w Supply & fixing TPN Distribution board with IP-42 protection (Metal Door)suitable for 3 phase ELCB/RCCB/FP Isolator as incomer and 10kA SP MCBs as out going including internal connection and labour charges for surface / flush mounting etc Complete. | Civil | Labour | SWR33526 | 11353 | EA | 11353
50 | 10 | Supply & fixing of 6A 3 pin wall plug socket with 6A switch control on a common switch board with earth continuity including wire leads,earth connection along with all labour charges etc., complete | Civil | Labour | SWR33468 | 166 | EA | 1660
51 | 6 | Supply & fixing of 16A 3 pin and 6A 3pin plug Flush type socket with indicator lamp and 16Amps fuse unit and 16Amps switch control (5 in one )duly recessed in wall with wooden deep box of 6'' x 8'' x 2 1/2'' size covered with hylam sheet earth connection and all labour charges etc., complete on wall. | Civil | Labour | SWR33470 | 449 | EA | 2694
52 | 24 | Supply and Fixing of modular switch, LP,FP,EFP Wiring with 2 runs of 14/0.3mm (1.0 sq.mm)Fire Retardant (FR) P.V.C. insulated flexible copper cable (ISI MARK) in existing pipe with 6A Flush type Switch,ceiling rose and 3mm thick hylam sheet covering to switch control box including all labour charges etc., complete for light points, bell , fan and exhaust fan points in Non-Residential Buildings. | Civil | Labour | SWR33457 | 676 | EA | 16224
53 | 12 | Supply & Fixing of 28W T5 fluorescent tube. | Civil | Labour | SWR33558 | 148 | EA | 1776
54 | 1 | Supply of 12" (300mm)ISI, 900 RPM Heavy duty exhaust fan with metallic blades with Mark of makes Crompton / Bajaj / Havells / Orient. | Civil | Labour | SWR33571 | 2192 | EA | 2192
55 | 180 | Supply and run of 2 of 22/0.3mm (1.5 sq.mm) (FR) P.V.C. insulated flexible copper cable in existing pipe for mains including all labour charges complete. | Civil | Labour | SWR33496 | 75 | m | 13500
56 | 180 | Supply and run of 2 of 36/0.3mm (2.5 sq.mm) FR P.V.C. insulated flexible copper cable in existing pipe for mains including all labour charges complete. | Civil | Labour | SWR33497 | 103 | m | 18540
57 | 12 | Supply & fixing of batten holder /slanting holder in lieu of ceiling rose of light point complete with all connection and all labour charges with 40W bulb (for new installation). | Civil | Labour | SWR33484 | 141 | EA | 1692
58 | 4 | Supply & fixing of 1200mm (48'') sweep 230v,A.C 50 Hz.Ceiling fan with 3 Blades and double ball bearings with all standared accessories. | Civil | Labour | SWR33563 | 2277 | EA | 9108
59 | 4 | Supply & fixing of Electronic Regulator for ceiling fans 900/1200/1400mm sweep including cost of material, Electrical charges complete for finished item of work | Civil | Labour | SWR33564 | 589 | EA | 2356
60 | 1 | Providing independent EARTHING by excavating a trench to a depth of 2.1M in all solid,as per size specified in the Data,using 40mm dia 'B' class GI pipe of 2.5 Mtrs length with necessary accessories with hume pipe ring duly providing staggered holes including filling with equal proportion of salt and Charcoal in layers and all labour charges etc., compiete for small quarters. | Civil | Labour | SWR33596 | 5345 | EA | 5345
61 | 35 | Supplying, laying, jointing and testing 101.6 mm SWG SP-1 pipes of ISI make conforming to ISI 651 & 4127 with airtight cement joints in CM 1.5:1 prop. Including excavation of trenches and socket pits in any soil (except rock requiring blasting) up to 1524 mm(5'0") depth and refilling with watering and tamping. | Civil | Labour | SWR34281 | 755 | m | 26425
62 | 3 | Constructing 904.0 mm (3#0#) dia brick masonry inspection chamber as per IS - 4111: Part-1:1986 with cement mortar (1:6) prop using 2nd Class Clay Bricks of 225 mm thick from approved source having a minimum crushing strength of 5 N/sq.mm including plastering with cement mortar 1:3 prop; ½# thick both inside and outside fitted with 20# dia RCC manhole covers and frames including excavating pits up to a depth of 904 mm (3'-0") in all sorts of soils (excluding rock) and laying cement concrete (1:4:8) 150 mm thick using 40 mm HBG Metal and P.C.C. 1:2:4 benching and channel 100 mm thick as per Standard specification and including cost and conveyance of all materials like cement, sand, bricks, water etc., to site, cost of seigniorage charges on all materials and all incidental and operational, labour charges like mixing cement mortar, constructing masonry, lift charges, curing etc., complete for finished item of work as per Standard specification. | Civil | Labour | SWR34296 | 8766 | EA | 26298
63 | 4 | Supply & fixing of 110 mm dia - Door Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34381 | 128 | EA | 512
64 | 4 | Supply & fixing of 110 mm dia - Plain Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34380 | 100 | EA | 400
65 | 12 | Supply & fixing of 110 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand | Civil | Labour | SWR34377 | 462 | m | 5544
66 | 18 | Supply & fixing of 90 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand | Civil | Labour | SWR34378 | 410 | m | 7380
67 | 3 | Supplying & fixing 150 mm x 100 mm SWG gully traps conforming to ISI 651 & 4127 with C.I Grating & Cost. Brick masonry in CM 1:6 prop. Intermediate chamber and fitted with 304.8 mm x 288.6mm (12"x9") C.I Frame and hinged cover | Civil | Labour | SWR34286 | 767 | EA | 2301
68 | 1 | Supplying and Fixing of European Water Closet of 1st Quality | Civil | Labour | SWR34312 | 2228 | EA | 2228
69 | 6 | Supply & fixing 15 mm angle stop cock Indian make 400 grams Seiko/ Senior/ Nice/ Senior/ Nice or equivalent | Civil | Labour | SWR34328 | 721 | EA | 4326
70 | 4 | S&F 15 mm N.P bib tap Indian make 400 grams full turn Seiko/ Senior/ Nice or equivalent | Civil | Labour | SWR34329 | 296 | EA | 1184
71 | 1 | Supplying & Fixing Indian make Flat Back Wash Hand Basin (HSW/Parryware/ Neycer) 1st quality conforming to IS:2556-Part-4:1972 with waste fittings like rubber plug, chain, 32 mm nominal size C.P. Fitting with parallel pipe thread conforming to IS:2963-1979 and fitted with 15 mm nominal bore Chromium Plated Pillar Tap of 1st quality Indian make 400 grams Seiko/ Senior/ Nice/ Esso or equivalent complete with standard CI brackets including wooden block: 550 x 400 mm - Single C.P. Pillar cock | Civil | Labour | SWR34316 | 1717 | EA | 1717
72 | 2 | Supply & fixing 38.1 mm C.P waste coupling Half or Full Thread 1st Quality Indian make Parryware or equivalent | Civil | Labour | SWR34428 | 309 | EA | 618
73 | 2 | Supply & fixing of 4" (101.6 mm ) Nahany Trap ( Without Jali with inlet)UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34387 | 134 | EA | 268
74 | 1000 | Providing & Placing on Terrace (at all floor levels) polyethylene water storage tank with Double layer approved brand & manufacture with cover and suitable locking arrangement & making necessary holes for inlet & outlets and over flow pipes but with NECESSARY fittings & base support for tanks | Civil | Labour | SWR34375 | 10 | L | 10000
75 | 2 | Supply & fixing 31.75 mm dia PVC flexible waste pipe of 914.4 mm length of Ist quality | Civil | Labour | SWR34426 | 33 | EA | 66
76 | 45 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)- 15.90mm OD Pipe - SDR 11 | Civil | Labour | SWR34361 | 239 | m | 10755
77 | 200 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-22.20mm OD Pipe - SDR 11 | Civil | Labour | SWR34362 | 313 | m | 62600
78 | 4 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type -20mm NB Size | Civil | Labour | SWR34345 | 331 | EA | 1324
79 | 1 | Supply & fixing 25.4 mm dia & 609.6 mm long aluminium anodized towel rod with brackets and aluminium screws | Civil | Labour | SWR34430 | 489 | EA | 489
80 | 36 | Plain Cement concrete PCC (1:3:6) using 40mm HBG metal for foundations and leveling course, including cost and conveyance of all materials, labour all leads and lifts, consolidation and all operations, formwork as required, curing, etc. complete for finished item w | Civil | Labour | SWR33029 | 4966 | m3 | 178776
81 | 120 | Supply&Fabrication and fixing of Welded wire mesh ( 2" x 2") of 3mm dia. with ISMC (75x40x4.4mm) and Pheriperal frame of ISA(35x35x3mm) incldg cost& conveyance painting with synthetic enamil paint two coats over a coat of red oxide primer etc complete for finished item of work.. | Civil | Labour | SWR33403 | 2310 | m2 | 277200
82 | 1 | Providing Consultancy services for arranging contour surveying with total station incuding preparation of boundary and contour levels with 2 Nos. Hard copies and soft copies complete for finished items of work | Civil | Labour | SWR33427 | 5665 | EA | 5665
83 | 222.2468 | Seigniorage Charges - Sand | Civil | Labour | SWR34470 | 40 | m3 | 8889.873
84 | 725.7496 | Seigniorage Charges - Metal | Civil | Labour | SWR34471 | 97.5 | m3 | 70760.585
85 | 839.38 | Seigniorage Charges - Gravel | Civil | Labour | SWR34472 | 30 | m3 | 25181.4
86 | 60 | Supply and fixing of RCC fencing poles of size 0.1mx0.1mx1.8m (security fencing of sub station), including cost and conveyance of all labour, materials,and hire chareges etc complete for finished item of work. | Civil | Labour | Swr33405 | 1444 | EA | 86640
87 | 1200 | Supply and fixing of galvanised barded wire (1 horizantal & 2 cross strands. including cost and conveyance of all labour, materials,and hire chareges etc complete for finished item of work. | Civil | Labour | Swr33408 | 16 | m | 19200
Civil labour | [7 empty] | 4231446.082
Electrical and Civil labour |  |  | 18% GST Rs. |  |  |  |  | 17021166.465

## 12.Mansoorabad
Name of the Work :- Erection of 33/11 kV Outdoor SS Mansoorabad (Peddacheruvu) with connecting 33kV and with 6 Nos. new 11 kV feeders at Peddachervu Mansoorabadin LB Nagar (M) of Saroornagar Division in ECGH Division /Master Plan/RR Circle
WBS No. S-1801-13-03-01-01-002
Sl No | Estimate Quantity | Description of item | Work Type | Item Short Description | APSS / Month Cl.NumberSSR 11 & 12 | Rate (INR) | UOM | AMOUNT
1 | 16 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | ElEC | Labour | SWR11039 | 928 | EA | 14848
2 | 5.76 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ElEC | Labour | SWR10868 | 6852 | TO | 39467.52
3 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ElEC | Supply | SMR40009 | 2181 | TO | 12562.56
4 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ElEC | Labour | SWR10877 | 851 | TO | 4901.76
5 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ElEC | Supply | SMR40010 | 1293 | TO | 7447.68
6 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ElEC | Labour | SWR10879 | 482 | TO | 2776.32
7 | 5.76 | Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ElEC | Labour | SWR10867 | 1470 | TO | 8467.2
8 | 16 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-R.S. Joists 150 x 150 mm | ElEC | Labour | SWR10348 | 1952.61 | EA | 31241.76
9 | 17.758 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ElEC | Labour | SWR10356 | 6579 | M3 | 116829.882
10 | 9.24 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ElEC | Labour | SWR10862 | 373 | M2 | 3446.52
11 | 16 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | ElEC | Labour | SWR11089 | 48 | EA | 768
12 | 4 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-8.0Mtrs PSCC Poles 0.76 M x 0.76M x 1.52M (2.6" x 2.6" x 5.0') 0.88 cum | ElEC | Labour | SWR11037 | 793 | EA | 3172
13 | 1 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ElEC | Labour | SWR10868 | 6852 | TO | 6852
14 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ElEC | Supply | SMR40009 | 2181 | TO | 2181
15 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ElEC | Labour | SWR10877 | 851 | TO | 851
16 | 1 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ElEC | Supply | SMR40010 | 1293 | TO | 1293
17 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ElEC | Labour | SWR10879 | 482 | TO | 482
18 | 1 | Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ElEC | Labour | SWR10867 | 1470 | TO | 1470
19 | 4 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Box pole 12 Mtr | ElEC | Labour | SWR11267 | 3901.37 | EA | 15605.48
20 | 2.65 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ElEC | Labour | SWR10356 | 6579 | M3 | 17434.35
21 | 2.31 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ElEC | Labour | SWR10862 | 373 | M2 | 861.63
22 | 4 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | ElEC | Labour | SWR11089 | 48 | EA | 192
23 | 5.063 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ElEC | Labour | SWR10868 | 6852 | TO | 34691.676
24 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ElEC | Supply | SMR40009 | 2181 | TO | 11042.403
25 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ElEC | Labour | SWR10877 | 851 | TO | 4308.613
26 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ElEC | Supply | SMR40010 | 1293 | TO | 6546.459
27 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ElEC | Labour | SWR10879 | 482 | TO | 2440.366
28 | 5.063 | Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ElEC | Labour | SWR10867 | 1470 | TO | 7442.61
29 | 13 | Erection of AB Switch and aligment complete Erection of 33 KV AB Switch including alignment and earthing | ElEC | Labour | SWR10392 | 4500 | EA | 58500
30 | 34 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Note:-The requirement of 2nd coat is to be justified by the concerned Divisional Engineer /Executive Engineer before execution of this work Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | ElEC | Labour | SWR10881 | 142 | EA | 4828
31 | 34 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | ElEC | Labour | SWR12331 | 146.63 | EA | 4985.42
32 | 6 | Loading of 33 KV CTs/ PTs | ElEC | Labour | SWR10200 | 165 | EA | 990
33 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ElEC | Labour | SWR11861 | 3299.7 | EA | 3299.7
34 | 6 | Un loading of 33 KV CTs/ PTs | ElEC | Labour | SWR10518 | 128 | EA | 768
35 | 2 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33kv single phase PT s | ElEC | Labour | SWR10401 | 1079 | SET | 2158
36 | 12 | Loading of 33 KV, 10 KA LAs Station typ | ElEC | Labour | SWR10266 | 41 | EA | 492
37 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ElEC | Labour | SWR11861 | 3299.7 | EA | 3299.7
38 | 12 | Un loading of 33 KV, 10 KA LAs Station type | ElEC | Labour | SWR10584 | 35 | EA | 420
39 | 4 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33 KV LAS station/Line type including earthing | ElEC | Labour | SWR10396 | 880 | SET | 3520
40 | 2 | Loading of 33 KV VCBs along with Panel boards | ElEC | Labour | SWR10198 | 1024 | EA | 2048
41 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ElEC | Labour | SWR11861 | 3299.7 | EA | 3299.7
42 | 2 | Un loading of 33 KV VCBs along with Panel boards | ElEC | Labour | SWR10516 | 1044.48 | EA | 2088.96
43 | 12.584 | Excavate-Pit for 33KV VCB | ElEC | Labour | SWR23224 | 331 | M3 | 4165.304
44 | 14.52 | Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x 1.8 x 0.75 cum for VCB Plinth | ElEC | Labour | SWR20685 | 5160 | M3 | 74923.2
45 | 2 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33 KV VCB with Control Panel | ElEC | Labour | SWR10460 | 12500 | EA | 25000
46 | 2 | Loading and unloading of PTR on constructed plinth-Loading of 8MVA PTR | ElEC | Labour | SWR10613 | 5805.84 | EA | 11611.68
47 | 2 | Transport of Power transformers (0 to 100 KM) from one place to another place in GHMC Area.(excluding of loading & unloading )-8MVA power transformer | ElEC | Labour | SWR10854 | 21945 | EA | 43890
48 | 2 | Loading and unloading of PTR on constructed plinth-Unloading of 8MVA PTR | ElEC | Labour | SWR10627 | 5805.84 | EA | 11611.68
49 | 700 | S/o rail poles 90/105lb (250x2N) | ElEC | Labour | SMR22718 | 47.27 | KG | 33089
50 | 14 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Rail pole 90 lbs | ElEC | Labour | SWR10344 | 3510 | EA | 49140
51 | 2 | Erection of PTR on constructed plinth-Erection of 8 MVA PTR. | ElEC | Labour | SWR21321 | 49480.2 | EA | 98960.4
52 | 0.436 | Extention of 33KV Bay at 132/33KV Sub-station-Zebra condutor | ElEC | Labour | SMR24910 | 299369 | KM | 130524.884
53 | 30 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing | ElEC | Supply | SMR11915 | 2055 | SET | 61650
54 | 30 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of I-Bolts | ElEC | Supply | SMR22473 | 294 | EA | 8820
55 | 45 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 "to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating . Sup T clamp LM6 Al alloy of 12 mm, 800 A | ElEC | Supply | SMR40011 | 299 | EA | 13455
56 | 6 | Bus stringing Hoisting of Insulators and hardware, stretching the conductor and stringing of 33 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bussection of 4.5mt) Hoisting post ins&hrd wr 1panther 33kv | ElEC | Labour | SWR21240 | 781 | EA | 4686
57 | 84 | Stringing of bus with panther conductor including jumpering etc., complete to all the equipment in SS fixing to all clamps and equipment.(3 Conductors) | ElEC | Labour | SWR10404 | 327.68 | M | 27525.12
58 | 30 | Bus stringing Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | ElEC | Labour | SWR10884 | 224 | EA | 6720
59 | 75 | Labour for Fixing of all types of clamps | ElEC | Labour | SWR10917 | 65 | EA | 4875
60 | 25 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | ElEC | Labour | SWR11039 | 928 | EA | 23200
61 | 8.68 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ElEC | Labour | SWR10868 | 6852 | TO | 59475.36
62 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ElEC | Supply | SMR40009 | 2181 | TO | 18931.08
63 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ElEC | Labour | SWR10877 | 851 | TO | 7386.68
64 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ElEC | Supply | SMR40010 | 1293 | TO | 11223.24
65 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ElEC | Labour | SWR10879 | 482 | TO | 4183.76
66 | 8.68 | Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ElEC | Labour | SWR10867 | 1470 | TO | 12759.6
67 | 25 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-R.S. Joists 150 x 150 mm | ElEC | Labour | SWR10348 | 1952.61 | EA | 48815.25
68 | 27.75 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ElEC | Labour | SWR10356 | 6579 | M3 | 182567.25
69 | 17.91 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ElEC | Labour | SWR10862 | 373 | M2 | 6680.43
70 | 25 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | ElEC | Labour | SWR11089 | 48 | EA | 1200
71 | 4.642 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ElEC | Labour | SWR10868 | 6852 | TO | 31806.984
72 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ElEC | Supply | SMR40009 | 2181 | TO | 10124.202
73 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ElEC | Labour | SWR10877 | 851 | TO | 3950.342
74 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ElEC | Supply | SMR40010 | 1293 | TO | 6002.106
75 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ElEC | Labour | SWR10879 | 482 | TO | 2237.444
76 | 4.642 | Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ElEC | Labour | SWR10867 | 1470 | TO | 6823.74
77 | 17 | Erection of AB Switch and aligment complete-Erection of 11KV 800A double throw AB Switches | ElEC | Labour | SWR21277 | 3500 | EA | 59500
78 | 3 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | ElEC | Labour | SWR10393 | 3200 | EA | 9600
79 | 2 | Loading of 11 KV CT - PT Sets | ElEC | Labour | SWR10201 | 190 | EA | 380
80 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ElEC | Labour | SWR11861 | 3299.7 | EA | 3299.7
81 | 2 | Un loading of 11 KV CT - PT Sets | ElEC | Labour | SWR10519 | 101 | EA | 202
82 | 2 | Erection of 11 KV three phase PTs | ElEC | Labour | SWR10402 | 800 | SET | 1600
83 | 24 | Loading of 11 KV, 10 KA LAs Station type | ElEC | Labour | SWR10264 | 32 | EA | 768
84 | 2 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ElEC | Labour | SWR11861 | 3299.7 | EA | 6599.4
85 | 24 | Un loading of 11 KV, 10 KA LAs Station type | ElEC | Labour | SWR10582 | 32 | EA | 768
86 | 2 | Erection of 11 KV LAS station type including earthing | ElEC | Labour | SWR10397 | 559 | SET | 1118
87 | 6 | Erection of 11 KV LAS line type including earthing | ElEC | Labour | SWR10398 | 505 | SET | 3030
88 | 8 | Loading of 11 KV VCBs along with Panel boards | ElEC | Labour | SWR10199 | 1024 | EA | 8192
89 | 4 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ElEC | Labour | SWR11861 | 3299.7 | EA | 13198.8
90 | 8 | Un Loading of 11 KV VCBs along with Panel boards | ElEC | Labour | SWR10517 | 1044.48 | EA | 8355.84
91 | 41.6 | Excavate-Pit for 33KV VCB | ElEC | Labour | SWR23224 | 331 | M3 | 13769.6
92 | 48 | Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x 1.8 x 0.75 cum for VCB Plinth | ElEC | Labour | SWR20685 | 5160 | M3 | 247680
93 | 8 | Erection of 11 KV VCB with Control Panel | ElEC | Labour | SWR10461 | 12000 | EA | 96000
94 | 12 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing | ElEC | Supply | SMR11915 | 2055 | SET | 24660
95 | 12 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of I-Bolts | ElEC | Supply | SMR22473 | 294 | EA | 3528
96 | 45 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 "to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating . Sup T clamp LM6 Al alloy of 12 mm, 800 A | ElEC | Supply | SMR40011 | 299 | EA | 13455
97 | 2 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 11 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 3.5mt) Hoisting post ins&hrd wr 1panther 11kv | ElEC | Labour | SWR21241 | 507 | EA | 1014
98 | 63 | Stringing of bus with panther conductor including jumpering etc., complete to all the equipment in SS fixing to all clamps and equipment.(3 Conductors) | ElEC | Labour | SWR10404 | 327.68 | M | 20643.84
99 | 45 | Bus stringing Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | ElEC | Labour | SWR10884 | 224 | EA | 10080
100 | 57 | Labour for Fixing of all types of clamps | ElEC | Labour | SWR10917 | 65 | EA | 3705
101 | 584 | Laying of earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication 75x 8mm MS Flat / GI Flat. Laying of earth mat,excavation 75x 8mm | ElEC | Labour | SWR10920 | 65 | RMT | 37960
102 | 1010 | Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) Earthing for raisers of SS Flat 50x6 mm. | ElEC | Labour | SWR10919 | 41 | RMT | 41410
103 | 36 | Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | ElEC | Supply | SMR11482 | 3486 | EA | 125496
104 | 36 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | ElEC | Labour | SWR10357 | 1234.2 | EA | 44431.2
105 | 36 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINES-Providing of RCC collar | ElEC | Labour | SWR10359 | 386 | EA | 13896
106 | 2 | Supply of Copper Flexible jumper with 75 X 8 of length 250 mm at neutral of Power tranformer end and 50 X 6 of length 50mm two Nos at double neutral end duly brasing with flexible jumper of capacity of 5kA/3 sec for power transformer neutral. SupCU Flexi jumper for Power T/F Neutral | ElEC | Supply | SMR40033 | 4725 | EA | 9450
107 | 2 | Providing of earthing with various types of earth electrodes-Providing of double earthing for neutral with flexible copper jumpers including arrangement by fixing M.S.Channel 100x50mm. | ElEC | Labour | SWR11892 | 1323 | EA | 2646
108 | 4 | Loading of LT AB Cable 3X16+25 Sqmm | ElEC | Labour | SWR11702 | 200 | DR | 800
109 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ElEC | Labour | SWR11861 | 3299.7 | EA | 3299.7
110 | 4 | Un loading of LT AB Cable 3X16+25 Sqmm | ElEC | Labour | SWR11713 | 204 | DR | 816
111 | 80 | Providing of control cable trench as per DATA-XII | ElEC | Labour | SWR22093 | 3148 | RMT | 251840
112 | 3074 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends . Lay-4C/10C 2.5Sqmm Control Cable | ElEC | Labour | SWR11879 | 27 | M | 82998
113 | 270 | Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per specification (including cost of ferrules, lugs and glands) | ElEC | Labour | SWR12510 | 27 | EA | 7290
114 | 4 | Marshalling Box Supply of FRP PT Marshalling Box | ElEC | supply | SMR40048 | 4463 | EA | 17852
115 | 4 | Marshalling Box Erection of Marshalling boxes | ElEC | Labour | SWR10940 | 374.85 | EA | 1499.4
116 | 1 | Loading of 220 V Batterry with charger | ElEC | Labour | SWR11166 | 1612 | SET | 1612
117 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ElEC | Labour | SWR11861 | 3299.7 | EA | 3299.7
118 | 1 | Un loading of 220 V Batterry with charger | ElEC | Labour | SWR11147 | 1024 | SET | 1024
119 | 1 | Batteries-Erection of 220 V, 200 AH battery in complete shape fit for | ElEC | Labour | SWR12350 | 7666 | EA | 7666
120 | 1 | Supply of DC Annunciation & relay panel for 10 feeder panel including the cost of LED Indiacation lamps, VAA auxilairy relays, Electronic Hooters complete as per specification. | ElEC | supply | SMR40044 | 42500 | EA | 42500
121 | 1 | Supply of AC Supply panel inluding providing of changeover switch, SFU, metering unit, 32 A three phase MCB, 16 A Single phase MCB complete as per specification. Supply of AC Supply panel complete | ElEC | Supply | SMR40045 | 42000 | EA | 42000
122 | 2 | Fixing of AC/DC Panel and giving Connections to the protection equipment and Metering circuits as per the specification and standards. The 3 1/2 core 25 Sqmm power cable required from distribution box to AC/DC panel in the control room is also to be supply | ElEC | Labour | SWR20025 | 7871.85 | SET | 15743.7
123 | 8 | Yard lightning-Supply of stepped tubular poles single way made of steel of length 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9 mm, 2.1 mtrs with outer dia 76.1 mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79 kgf as per IS 2713 | ElEC | Supply | SMR40051 | 13913 | EA | 111304
124 | 8 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE/CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA /OSRAM /SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty S-90W LED fixture set | ElEC | Supply | SMR11594 | 8200 | EA | 65600
125 | 8 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | ElEC | Labour | SWR11039 | 928 | EA | 7424
126 | 8 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE / CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA/OSRAM/SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty-Erection of tubular poles | ElEC | Labour | SWR10955 | 1379 | EA | 11032
127 | 5.27 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ElEC | Labour | SWR10356 | 6579 | M3 | 34671.33
128 | 8 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE/CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA /OSRAM /SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty. Fixing of Metal halide lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5 GI pipe complete Fixing of LED/Metal halide complete. | ElEC | Labour | SWR10956 | 1268 | EA | 10144
129 | 45 | Supply of HBG metal-Supply & spreading of 20mm machine crushed metal (HBG) including cost of conveneyance of all materials, labour charges etc complete for finished item of work and directed by the engineer incharge | ElEC | Supply | SWR10860 | 2113 | M3 | 95085
130 | 2 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M Ex of Hard pit w/o blast 0.75X0.9X1.95M | ElEC | Labour | SWR11040 | 990.68 | EA | 1981.36
131 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ElEC | Supply | SMR40009 | 2181 | TO | 1635.75
132 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ElEC | Labour | SWR10877 | 851 | TO | 638.25
133 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ElEC | Supply | SMR40010 | 1293 | TO | 969.75
134 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ElEC | Labour | SWR10879 | 482 | TO | 361.5
135 | 1 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Box pole 12 Mtr | ElEC | Labour | SWR11267 | 3901.37 | EA | 3901.37
136 | 2.22 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ElEC | Labour | SWR10356 | 6579 | M3 | 14605.38
137 | 1.16 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ElEC | Labour | SWR10862 | 373 | M2 | 432.68
138 | 2 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | ElEC | Labour | SWR11089 | 48 | EA | 96
139 | 1 | Construction of DTR Plinth-RCC Column type DTR Plinth of size 1'X1'X10',topslab 4'x4'x6" & beam size 4'X8'X8" upto 160KVA | ElEC | Labour | SWR21843 | 25967.57 | EA | 25967.57
140 | 1 | Loading of 50,63, 75 & 100 KVA DTR | ElEC | Labour | SWR10195 | 350 | EA | 350
141 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ElEC | Labour | SWR11861 | 3299.7 | EA | 3299.7
142 | 1 | Un loading of 50,63, 75 & 100 KVA DTR | ElEC | Labour | SWR10513 | 280 | EA | 280
143 | 1 | Erection of DTR's including loading and Unloading DTR on the Structure/Plinth etc-Erection of 3 Phase DTRs 63,75 & 100 KVA | ElEC | Labour | SWR20905 | 1650 | EA | 1650
144 | 1 | Erection of AB Switch and aligment complete Erection of 11KV 200A TT type AB Switch including fixing of cross angles and alignment complete | ElEC | Labour | SWR20102 | 1813.49 | EA | 1813.49
145 | 1 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc -- Erection of 11 KV HG Fuse set including earthing | ElEC | labour | SWR10395 | 740.52 | SET | 740.52
146 | 40 | Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.-In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road-11KV 3x185 Sqmm Cable | ElEC | Labour | SWR11920 | 465.46 | M | 18618.4
147 | 20 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-11 KV 3x185 Sqmm Cable | ElEC | Labour | SWR11956 | 126.23 | M | 2524.6
148 | 2 | UG Cables Joints Making of Outdoor/Indoor End Termination OD/Idoor end termination 11kv 3x185 xlpe | ElEC | Labour | SWR10390 | 2370.63 | EA | 4741.26
149 | 1 | Erection of LT distribution box including laying of LT cable from distribution box to LT OH line and DTR to distribution box including earthing of distribution box and crimping of lugs connecting of jumpers etc | ElEC | Labour | SWR10674 | 1594.67 | EA | 1594.67
150 | 85 | LAYING OF 33KV, 11KV UG CABLE Excavation & laying of UG Cable in Single Run Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road-LT 3 1/2 x 185 Sqmm Cable | ElEC | Labour | SWR11923 | 377.63 | M | 32098.55
151 | 15 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-LT 3 1/2 x 185 Sqmm Cable | ElEC | Labour | SWR11959 | 85.43 | M | 1281.45
152 | 2 | Supply & fixing of Oout Door/Indoor end termination LT 3 1/2 x 185 Sqmm Cable | ElEC | Labour | SWR10765 | 968.9 | EA | 1937.8
153 | 1 | Supply and fixing of Substation board of size 3'x2.5' indicating the layout of switchyard Sup &fix of board ind Switchyard layout | ElEC | Supply | SWR20032 | 1654 | EA | 1654
154 | 1 | Supply and fixing of safety instructions/Substation operation instruction board. Sup& fix safety inst/SS Op. inst board | ElEC | Supply | SWR22090 | 2205 | EA | 2205
155 | 750 | Control Panels Supplying & fabrication erection of 6mm Checkerd plates as per the field conditions Supply,fabricati of 6mm Checkerd plates | ElEC | Labour | SWR10873 | 83 | KG | 62250
156 | 1 | T & P Supply of Wall clock standard make | ElEC | Supply | SMR40059 | 578 | EA | 578
157 | 1 | S-10ft Aluminium Ladder | ElEC | Supply | SMR12378 | 1654 | EA | 1654
158 | 1 | Sup Alluminium Ladder for indoor works | ElEC | Supply | SMR40062 | 4410 | EA | 4410
159 | 30 | T & P Painting of Name Plates for any equipmen | ElEC | Labour | SWR10963 | 122 | EA | 3660
160 | 1 | T & P Supply of Taparia Tool kit of Size 20”x10”x15” with tier arrangements Tool box with locking arrangement & key containing (1) Double Ended fix Spanner sets, (Ribbed) 6 x 7, 8 x 9, 10 x 11, 12 x 13, 14 x 15, 16 x 17, 18 x19, 20 x 22, 21 x 23, 24 x 27, 25 x28, 30 x 32, (2) Double Ended Ring Spanners sets, 6 x 7 , 8 x 9, 10 x 11, 12 x 13, 14 x 15. 16 x 17 , 18 x 19, 20 x 22 , 21 x 23, 24 x 27, 25 x28, 30 x 32 mm, (3) Adjustable Spanner 305 mm length least maximum opening 35mm chrome, (4) Pipe Wrench Length 350 mm 14”, (5) Soft faced Hammer with suitable handle 2 lb, (6) Hacksaw frame with metal handle heavy duty for 12" hacksaw blade with High Speed blade, (7) Insulated Screw drivers Transparent Green Handle Set Length 6”, 8” & 12”, (8) Star Screw Driver Transparent Green Handle Length 6”, (9) Insulated Wire Cutter, (10) Insulated Cutting Plier Length 8” with cable stripper insulated with thick C. A. sleeve confirming to IS: 4378 - 1990, (11) Long Nose Plier insulated with thick C.A. sleeve generally confirming to IS:3552-1989, (12) Tester type screw driver (special with neon bulb) generally confirm to IS: 5579- 1985 Grade:II handle yellow/ green colour overall length 130 mm, (13) Insulated Crimping Plier of all Taparia make. SupTaparia Tool kit complete as per Spec | ElEC | Supply | SMR40063 | 4925 | SET | 4925
161 | 1 | T & P Sup Rechargeable LED torch light of Standard make | ElEC | Supply | SMR40064 | 1733 | EA | 1733
162 | 1 | T & P-Steel almarah(61/2 X 3ft) Godrej | ElEC | Supply | SMR40061 | 9818 | EA | 9818
163 | 1 | T & P-Table (3x6ft) Godrej | ElEC | Supply | SMR40057 | 6050 | EA | 6050
164 | 4 | T & P-S type chairs (Godrej) | ElEC | Supply | SMR40058 | 924 | EA | 3696
165 | 1 | T & P Sup Angle racks(18x36.6inches) Godrej | ElEC | Supply | SMR40060 | 1733 | EA | 1733
166 | 1 | T & P Supply of Hack saw (12 inches) | ElEC | Supply | SMR40065 | 289 | EA | 289
167 | 4 | Sup Earth Rods (8ft) Screw & clamp type | ElEC | Supply | SMR40066 | 578 | EA | 2312
168 | 2 | Supply of Hand Gloves | ElEC | Supply | SMR40067 | 289 | SET | 578
169 | 12 | SupRubber mats( 6'x3')size fo indoorSS | ElEC | Labour | SMR40068 | 1386 | EA | 16632
170 | 1 | Biometric Time attendence System & Telecom Sup Stand basic cell phone with charger | ElEC | Supply | SMR40069 | 1386 | EA | 1386
171 | 14 | Supply of Danger boards with clamps | ElEC | Supply | SMR40070 | 116 | EA | 1624
172 | 2 | Fire bucket stand with 3 buckets (8 -10 ltr capacity) | ElEC | Supply | SMR40088 | 1386 | SET | 2772
173 | 2 | Room fire extinguisher (2 ltrs capacity) for control room | ElEC | Supply | SMR40089 | 4620 | EA | 9240
174 | 4 | Sup TrollyMounted Co2 (6.5Kgs) Cylinders(IS-2878) | ElEC | Supply | SMR40087 | 9240 | EA | 36960
175 | 6 | Supply of Safety Helmet of standard make | ElEC | Supply | SMR40071 | 231 | EA | 1386
176 | 8 | Supply of LC Boards | ElEC | Supply | SMR40072 | 116 | EA | 928
177 | 4 | Supply of Gum Boots(Pair) | ElEC | Supply | SMR40073 | 693 | EA | 2772
178 | 1 | Supply of 5000v megger | ElEC | Supply | SMR40074 | 13860 | EA | 13860
179 | 1 | Supply of Earth megger (1000v) | ElEC | Supply | SMR40075 | 8085 | EA | 8085
180 | 1 | Supply of Digital clamp meter. | ElEC | Supply | SMR40076 | 2888 | EA | 2888
181 | 1 | Name board of the 33/11kV Sub-Station(As per Standard Specification) Sup 33/11kv S.S Permanent name board | ElEC | Supply | SMR40086 | 10238 | EA | 10238
182 | 800 | Supply of Hot dip galvanized/zinc coated bolts & nuts including spring washers, pack washers and flat washers etc. | ElEC | Supply | SMR12488 | 90 | KG | 72000
183 | 2 | Fabrication of poles-Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | ElEC | Labour | SWR10642 | 512.55 | EA | 1025.1
184 | 1 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-RS Joists 150x75/175 x 85 mm | ElEC | Labour | SWR10346 | 1934 | EA | 1934
185 | 5760 | Supply of Materials -- Supply of RS Joist girder Poles (150X150mm) | ElEC | Supply | SMR12302 | 59.25 | KG | 341280
186 | 1000 | Supply of Materials -- supply of RS Joist Poles (175X85mm) | ElEC | Supply | SMR12303 | 60.75 | KG | 60750
187 | 5063 | Supply of Materials -- Supply of MS Channel 100X50mm | ElEC | Supply | SMR22745 | 57.45 | KGS | 290869.35
188 | 13 | Supply of Materials -- Supply of 33 kV 800 A Double break AB switch | ElEC | Supply | SMR12315 | 40658.78 | EA | 528564.14
189 | 8680 | Supply of Materials -- Supply of RS Joist girder Poles (150X150mm) | ElEC | Supply | SMR12302 | 59.25 | KG | 514290
190 | 4642 | Supply of Materials -- Supply of MS Channel 100X50mm | ElEC | Supply | SMR22745 | 57.45 | KGS | 266682.9
191 | 17 | Supply of Materials -- Supply of 11 kV 800 A Double break AB switch | ElEC | Supply | SMR12316 | 30847.46 | EA | 524406.82
192 | 3 | Supply of Materials -- Supply of 11 kV 400 A Double break AB switch | ElEC | Supply | SMR12317 | 18150 | EA | 54450
193 | 3045 | Supply of Materials -- Supply of MS Flat 75x8 mm | ElEC | Supply | SMR12321 | 56.42 | KG | 171798.9
194 | 2666 | Supply of Materials -- Supply of MS Flat 50x6 mm | ElEC | Supply | SMR12322 | 56.5 | KG | 150629
195 | 750 | Supply of Materials -- supply of RS Joist Poles (175X85mm) | ElEC | Supply | SMR12303 | 60.75 | KG | 45562.5
196 | 1 | Supply of Materials -- Supply of 11 kV 200 A Tilting type AB switch | ElEC | Supply | SMR12318 | 8991 | EA | 8991
197 | 1 | Supply of Materials -- Supply of 11KV HG fuse set for station transformer | ElEC | Supply | SMR12324 | 1974 | EA | 1974
198 | 1 | Supply of LT Distribution Box (SMC) | ElEC | Supply | SMR25200 | 7797 | EA | 7797
199 | 2 | Supply of 11KV 3x185 Heat Shble O/d End Term Kit | ElEC | Supply | SMR25201 | 1182.97 | EA | 2365.94
200 | 40 | Supply of XLPE Cable 1 C 150 sqmm | ElEC | Supply | SMR25203 | 114.83 | M | 4593.2
201 | 100 | Supply of XLPE Cable 3 1/2 C 185 sqmm | ElEC | Supply | SMR25204 | 547 | M | 54700
202 | 2 | survey line&cabl inc peg mark&tree clear | ElEC | Labour | SWR22092 | 765 | KM | 1530
203 | 34 | Load-11/33KV XLPE UG Cable for all sizes | ElEC | Labour | SWR11230 | 1024 | DR | 34816
204 | 17 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ElEC | Labour | SWR11861 | 3299.7 | EA | 56094.9
205 | 34 | Unload-11/33KV XLPE UG Cable for all sizes | ElEC | Labour | SWR11231 | 1024 | DR | 34816
206 | 1000 | Excavation & laying of UG Cable (Double Run)-Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts-Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil/CC-33 KV 3x400 Sqmm Cable | ElEC | labour | SWR11972 | 749 | M | 749000
207 | 3700 | Excavation & laying of UG Cable (Double Run) Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, Along the CC / BT multi layer road requiring compressor-33 KV 3x400 Sqmm Cable | ElEC | Labour | SWR11980 | 1388.84 | M | 5138708
208 | 300 | Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, Across the CC/ BT road crossing multi layer road requiring compressor (excluding the cost of Hume pipe)-33 KV 3x400 Sqmm Cable | ElEC | Labour | SWR11988 | 1587.07 | M | 476121
209 | 5000 | Laying of 2nd cable in excavated trench | ElEC | Labour | SWR10988 | 204.1 | M | 1020500
210 | 50 | S&E-Smart RFID marker | ElEC | Labour | SWR25089 | 2745 | EA | 137250
211 | 34 | UG Cables Joints 33 KV 3x400 Sqmm Cable Straight through joint 33kv 3x400 xlpe | ElEC | Labour | SWR10382 | 5700.78 | EA | 193826.52
212 | 2000 | Supply of 6" B class GI pipe | ElEC | Supply | SMR40081 | 1044 | M | 2088000
213 | 300 | Cost of Pipes and slabs-supply of 6" DWC pipe | ElEC | Supply | SMR11610 | 1012 | M | 303600
214 | 600 | Cost of Pipes and slabs-Suppy of Hume pipe 9" size | ElEC | Supply | SMR40001 | 125 | M | 75000
215 | 12 | Making of Outdoor/Indoor End Making 33 KV 3x400 Sqmm Cable Out Door/Indoor end termination TerminationOD/Idoor end termination 33kv 3x400 xlpe | ElEC | Labour | SWR10387 | 2764.76 | EA | 33177.12
216 | 60 | Excavation & laying of UG Cable (Double Run) Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-33 KV 3x400 Sqmm Cable | ElEC | Labour | SWR12004 | 323.85 | M | 19431
217 | 5000 | Hard Rock Cutting-11KV-Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours. | ElEC | Labour | SWR21903 | 30 | M | 150000
218 | 50 | Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters , CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | ElEC | Supply | SMR40085 | 484 | EA | 24200
219 | 3 | Erection of AB Switch and aligment complete Erection of 33 KV AB Switch including alignment and earthing | ElEC | Labour | SWR10392 | 4500 | EA | 13500
220 | 3 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | ElEC | Labour | SWR12331 | 146.63 | EA | 439.89
221 | 3 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Note:-The requirement of 2nd coat is to be justified by the concerned Divisional Engineer /Executive Engineer before execution of this work Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | ElEC | Labour | SWR10881 | 142 | EA | 426
222 | 12 | Fabrication of poles-Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | ElEC | Labour | SWR10642 | 512.55 | EA | 6150.6
223 | 18 | Painting of poles-Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | ElEC | Labour | SWR10640 | 1132 | EA | 20376
224 | 12 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M Ex of Hard pit w/o blast 0.75X0.9X1.95M | ElEC | Labour | SWR11040 | 990.68 | EA | 11888.16
225 | 3 | Assembly and erection of Structure as per specification which includes fixing of top channels and cross bracings, transport of all materials from road side to the location, earthing, back filling with earth ramming etc excluding pit excavation and concreting-33 KV DP Structure with 175x85/150x75mm RS joist | ElEC | Labour | SWR11276 | 5670 | SET | 17010
226 | 6 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-RS Joists 150x75/175 x 85 mm | ElEC | Labour | SWR10346 | 1934 | EA | 11604
227 | 155 | Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) Earthing for raisers of SS Flat 50x6 mm. | ElEC | Labour | SWR10919 | 41 | RMT | 6355
228 | 11.282 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ElEC | Labour | SWR10356 | 6579 | M3 | 74224.278
229 | 0.37 | Mass Concreting for pole-Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | ElEC | Labour | SWR11890 | 3893 | M3 | 1440.41
230 | 0.975 | Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to theRS-Joist poles excluding cost of Mild Steel and transportcharges to substation site, including erection. Fabrication of struc.with welding. | ElEC | Labour | SWR10869 | 3426 | TO | 3340.35
231 | 6 | Supply of earthing pipe with materials-Supply of CI eath pipe with 80mm dia,2.0 M Length | ElEC | Supply | SMR11483 | 2789 | EA | 16734
232 | 6 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | ElEC | Labour | SWR10357 | 1234.2 | EA | 7405.2
233 | 6 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINES-Providing of RCC collar | ElEC | Labour | SWR10359 | 386 | EA | 2316
234 | 3 | Painting of poles-Painting of feeder name on support including cost of paint | ElEC | Labour | SWR12101 | 53 | EA | 159
235 | 30 | Supply of earthing pipe with materials S-GI Bolts & Nuts,Washers etc., | ElEC | Supply | SMR11488 | 117.5 | KG | 3525
236 | 975 | Supply of Materials -- Supply of MS Channel 100X50mm | ElEC | Supply | SMR22745 | 57.45 | KGS | 56013.75
237 | 12 | UG Cables Joints : Making of Outdoor/Indoor End Termination -- Supply 33KV 3x400Sqmm Outdoor | ElEC | supply | SMR22222 | 4554 | EA | 54648
238 | 34 | UG Cables Joints : Making of Straight through joints -- Supply of 33KV 3x400SQmm Straight Through Joint Kit | ElEC | supply | SMR22223 | 24151 | EA | 821134
239 | 3 | Supply of Materials -- Supply of 33 kV 800 A Double break AB switch | ElEC | Supply | SMR12315 | 40658.78 | EA | 121976.34
240 | 4500 | Supply of Materials -- supply of RS Joist Poles (175X85mm) | ElEC | Supply | SMR12303 | 60.75 | KG | 273375
241 | 370 | Supply of Materials -- Supply of MS Flat 50x6 mm | ElEC | Supply | SMR12322 | 56.5 | KG | 20905
242 | 45 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M Ex of Hard pit w/o blast 0.75X0.9X1.95M | ElEC | Labour | SWR11040 | 990.68 | EA | 44580.6
243 | 170 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | ElEC | Labour | SWR11039 | 928 | EA | 157760
244 | 34 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-Stud Poles 0.6 M x 0.9 M x 1.5 M (0.81 cubmic meter) | ElEC | Labour | SWR11038 | 612 | EA | 20808
245 | 45 | Erection of OH Lines including AB Cable (33KV, 11KV, LT) Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Errection of 11 M long PSCC pole | ElEC | Labour | SWR10978 | 4336.85 | EA | 195158.25
246 | 170 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-9.1 M long PSCC pole | ElEC | Labour | SWR10343 | 2400 | EA | 408000
247 | 34 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-8.0 m long PSCC poles for Strut | ElEC | Labour | SWR21590 | 1500 | EA | 51000
248 | 75.324 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ElEC | Labour | SWR10356 | 6579 | M3 | 495556.596
249 | 5 | LOADING of Conductor drums | ElEC | Labour | SWR10191 | 202 | EA | 1010
250 | 3 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ElEC | Labour | SWR11861 | 3299.7 | EA | 9899.1
251 | 5 | UNLOADING of Conductor drums | ElEC | Labour | SWR10509 | 100 | EA | 500
252 | 8.5 | Paving out and stringing of conductor by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location.-100 Sqmm Single Circuit (3 Conductors) | ElEC | labour | SWR10366 | 13856.7 | KM | 117781.95
253 | 34 | Formation of Cut point for 11 KV Single Circuit line excluding pole erection and stays Formatn of Horiz Cut point for 11KV line | ElEC | Labour | SWR10653 | 1435.81 | EA | 48817.54
254 | 215 | Painting of poles-Numbering of poles incl. cost of paint | ElEC | Labour | SWR10378 | 32 | EA | 6880
255 | 12 | Fabrication of poles-Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | ElEC | Labour | SWR10642 | 512.55 | EA | 6150.6
256 | 12 | Painting of poles-Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | ElEC | Labour | SWR10640 | 1132 | EA | 13584
257 | 6 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M Ex of Hard pit w/o blast 0.75X0.9X1.95M | ElEC | Labour | SWR11040 | 990.68 | EA | 5944.08
258 | 6 | Erection of OH Lines including AB Cable (33KV, 11KV, LT)-Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Box pole 9/10/11 Mtr | ElEC | Labour | SWR11266 | 2643.83 | EA | 15862.98
259 | 160 | Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) Earthing for raisers of SS Flat 50x6 mm. | ElEC | Labour | SWR10919 | 41 | RMT | 6560
260 | 5.64 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ElEC | Labour | SWR10356 | 6579 | M3 | 37105.56
261 | 0.186 | Mass Concreting for pole-Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | ElEC | Labour | SWR11890 | 3893 | M3 | 724.098
262 | 0.23 | Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to theRS-Joist poles excluding cost of Mild Steel and transportcharges to substation site, including erection. Fabrication of struc.with welding. | ElEC | Labour | SWR10869 | 3426 | TO | 787.98
263 | 12 | Supply of earthing pipe with materials-Supply of CI eath pipe with 80mm dia,2.0 M Length | ElEC | Supply | SMR11483 | 2789 | EA | 33468
264 | 12 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | ElEC | Labour | SWR10357 | 1234.2 | EA | 14810.4
265 | 12 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINES-Providing of RCC collar | ElEC | Labour | SWR10359 | 386 | EA | 4632
266 | 6 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | ElEC | Labour | SWR10393 | 3200 | EA | 19200
267 | 6 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | ElEC | Labour | SWR12331 | 146.63 | EA | 879.78
268 | 6 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Note:-The requirement of 2nd coat is to be justified by the concerned Divisional Engineer /Executive Engineer before execution of this work Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | ElEC | Labour | SWR10881 | 142 | EA | 852
269 | 6 | Painting of poles-Painting of feeder name on support including cost of paint | ElEC | Labour | SWR12101 | 53 | EA | 318
270 | 40 | Supply of earthing pipe with materials S-GI Bolts & Nuts,Washers etc., | ElEC | Supply | SMR11488 | 117.5 | KG | 4700
271 | 45 | Supply of PSCC Pole 11Mtr 365KG | ElEC | supply | SMR25236 | 5399 | EA | 242955
272 | 170 | Supply of PSCC Pole 9.1Mtr 280KG | ElEC | supply | SMR25233 | 3109.41 | EA | 528599.7
273 | 34 | Supply of PSCC Pole 8Mtr 140KG | ElEC | supply | SMR25232 | 1580 | EA | 53720
274 | 611 | Supply of 33KV V X- Arm with MS Channel 75x40 | ElEC | supply | SMR25219 | 561 | EA | 342771
275 | 611 | Supply of 11KV Top Cleat for 9.1M(Vertical) | ElEC | supply | SMR25226 | 256 | EA | 156416
276 | 68 | Supply of 11KV Horizontal Cross Arm | ElEC | supply | SMR25223 | 528 | EA | 35904
277 | 679 | Supply-LT/11KV MS Back Clamps | ElEC | supply | SMR25217 | 72 | SET | 48888
278 | 6 | Supply of Materials -- Supply of 11 kV 400 A Double break AB switch | ElEC | Supply | SMR12317 | 18150 | EA | 108900
279 | 3000 | Supply of Materials -- supply of RS Joist Poles (175X85mm) | ElEC | Supply | SMR12303 | 60.75 | KG | 182250
280 | 384 | Supply of Materials -- Supply of MS Flat 50x6 mm | ElEC | Supply | SMR12322 | 56.5 | KG | 21696
281 | 150 | Supply of MS Angle 50x50x6 | ElEC | supply | SMR25206 | 58.15 | KG | 8722.5
282 | 80 | Supply of MS Channel 75x40 mm | ElEC | supply | SMR25205 | 58.45 | KG | 4676
Electrical total | [7 empty] | 22122619.347
Civil labour-WBS. No. S-1801-13-07-01-01-001
Sl.No. | Estimate Quantity (only Figures) | Item Detailed Specification Description | Work Type eg. Earth Work, Electrical works. etc (upto 200 Characters) | Item Short Description (upto 100 Characters) | APSS / Morth Cl. Number (upto 200 Characters) | Rate (INR) (Upto 2 Decimals ) | UOM (upto 50 Characters) | Amount
1 | 32 | Leveliing the site by cutting and levelling with the help of JCB including cost,conveyance of all materials,hire chareges etc complete for finished item of work as directed by Engineer-in-charge. | Civil | Labour | SWR34179 | 2165 | Hrs | 69280
2 | 358.34 | Earth Work Mass Excavation (hard rock) to a depth as directed, in soils such as hard rock requiring blasting in prohibited area and all conditions such as dry, wet, slurry etc.and in dense or hard soils, disposal and depositing of excavated soil with intial lead of 10 mt and intial lift of 2m or as directed, including cost and conveyance of all materials, ramping and lifting of materials, and labour charges, hire charges of machinery, tools & plants, bailing of water ( either sub soil water, stoMts water, rain water, surface water or of any kind) if any at any stage of work until all works below ground level is finished to the satisfaction ,and from work such as shoring, timbering, strutting with required supports etc. for the work and removal of form work after completion of work etc all complete as directed by the engineer-incharge. | Civil | Labour | SWR33018 | 1440 | cum | 516009.6
3 | 294.6 | Earth work excavation in all type of ordinary soils red earth, Hard gravelly soils, earth mixed with sand and sandy soils etc., in all conditions such as slushy and dry with initial leads and lifts for foundations. Ordinary Soil | Civil | Labour | SWR33015 | 486 | cum | 143175.6
4 | 102.138 | PCC (1:4:8) using 40 mm metal with concrete Mixture. All work upto Plinth level including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete as directed by Engineer incharge of the work | Civil | Labour | SWR33028 | 4748 | cum | 484951.224
5 | 142.5 | Coursed Rubble stone CRS masonry 2nd sort with hard granite stones in cement mortar CM (1:6) for basement, including cost and conveyance of all materials, labour charges, curing, all leads and lifts, etc, complete for finished item of work. | Civil | Labour | SWR33041 | 4890 | cum | 696825
6 |  | RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge
7 | 1.09 | RCC M20 Grade Footing 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33098 | 9500 | cum | 10355
8 | 1.58 | RCC M20 Grade Column 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33100 | 13249 | cum | 20933.42
9 | 1.15 | RCC M20 Grade plinth beam 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33099 | 12371 | cum | 14226.65
10 | 0.458 | Reinforcement steel Supplying, Cutting, bending, binding, placing in position and tying reinforcement steel in all heights including cost and conveyance of steel and binding wire etc,. With all leads and lifts, labour charges, etc., complete for finished item of work. | Civil | Labour | SWR33144 | 70687 | MT | 32374.646
11 | 107.582 | Brick masonry in CM (1:6) for superstructure using well burnt country made second class bricks of approved quality including cost and conveyance of all materials curing, scaffolding with all leads and lifts in all heights etc., complete for finished item of work | Civil | Labour | SWR33068 | 8262 | cum | 888842.484
12 | 82.226 | PCC (1:2:4) using 20mm size well graded HBG metal for foundations, including cost, conveyance of all materials,labour all leads and lifts,consolidation and all operations, formwork as required, curing,etc. complete for finished item of work | Civil | Labour | SWR33030 | 6117 | cum | 502976.442
13 | 824.75 | Plastering with CM 2 coats, 20 mm thick, base coat in CM (1:6), 16 mm thick and top coat in CM (1:4), 4mm thick with Dubara sponze finishing including cost of all materials, seigniorage charges, excluding conveyance charges of materials and including all operational, incidental and labour charges for mixing mortar, laying rendering smooth and thread lining, curing, rounding off junctions of wall and slab etc., complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33163 | 561 | Sqm | 462684.75
14 | 824.75 | Painting with two coats of Plastic Emulsn paint over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33356 | 210 | Sqm | 173197.5
15 | 271.85 | Painting with two coats of Surya Cem paint over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33329 | 85 | Sqm | 23107.25
16 | 650 | Supplying and fixing Structural Steel angles channal etc.Manufacturing, Supplying and fixing of MS grill for (Gate and raillings) of approved design as per drawings, including cost and conveyance of all materials, labour charges etc.,complete for finished item of work as directed by the Engineer- in-charge. | Civil | Labour | SWR33145 | 128 | Kgs | 83200
17 | 3 | Supply and Fixng of MS Name Board including cost & conveyance of all materials,labour charges etc complete for finished item of work. | Civil | Labour | SWR33421 | 4326 | sqm | 12978
18 | 1 | Geophysical Investgation charges for water point by Geologist | Civil | Labour | SWR33608 | 5000 | Ea | 5000
19 |  | Drilling of 165mm bore well with machine rig including deployment and hire charges of rig and other machinery and equipment labour charges , measuring the yeild of borewell including cost and conveyance etc complete
20 | 90 | Drill-165mm Bore Well 0 to 90 | Civil | Labour | SWR33609 | 336 | M | 30240
21 | 30 | Drill-165mm Bore Well 90M to 120M | Civil | Labour | SWR34830 | 369 | M | 11070
22 | 30 | Drill-165mm Bore Well 120M to 150M | Civil | Labour | SWR34831 | 394 | M | 11820
23 | 30 | Drill-165mm Bore Well 150M to 180M | Civil | Labour | SWR34832 | 492 | M | 14760
24 | 30 | Drill-165mm Bore Well 180M to 210M | Civil | Labour | SWR34833 | 623 | M | 18690
25 | 30 | Drill-165mm Bore Well 210M to 240M | Civil | Labour | SWR34834 | 754 | M | 22620
26 | 30 | Drill-165mm Bore Well 240M to 270M | Civil | Labour | SWR34835 | 918 | M | 27540
27 | 150 | Drill-165mm Bore Well 270M and above | Civil | Labour | SWR34836 | 1082 | M | 162300
28 | 40 | Supply and fixing of 160mm dia PVC casing of A class 6Kg point pressure including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR33611 | 883 | M | 35320
29 | 1 | Supply and erecting, ISI mark submersible 5.0 HP, three Phase 30 stages pumpset suitable for 106/156mm dia borewell including cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33640 | 48007 | EA | 48007
30 | 370 | Supply and fixing of HDPE pipe 40mm dia of 16Kg/cm2 including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR34410 | 180 | M | 66600
31 | 1 | Supply and erecting D.O.L Starter 415V ,3 phase,50Hz with SS enclouserincluding cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33645 | 7854 | EA | 7854
32 | 450 | Supply of 3 Core 2.5 Sqmm Flat Copper cable of ISI for Submersible Motors of makes Finolex / Polycab / Gold Medal / Million / Payal / Sun Light / Power Flex / Fortune Art | Civil | Labour | SWR33641 | 192 | M | 86400
33 | 6 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-28.60mm OD Pipe - SDR 11 | Civil | Labour | SWR34363 | 410 | M | 2460
34 | 1 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type - 25mm NB Size | Civil | Labour | SWR34346 | 466 | EA | 466
35 | 72.73 | Earth work excavation in all type of ordinary soils red earth, Hard gravelly soils, earth mixed with sand and sandy soils etc., in all conditions such as slushy and dry with initial leads and lifts for foundations. | Civil | Labour | SWR33015 | 486 | Cum | 35346.78
36 | 39.53 | PCC (1:4:8) using 40mm HBG metal for foundations and leveling course, including cost and conveyance of all materials, labour all leads and lifts, consolidation and all operations, formwork as required, curing, etc. complete for finished item w | Civil | Labour | SWR33028 | 4748 | Cum | 187688.44
37 | 27.37 | CRS Coursed Rubble Stone masonry 2nd sort with hard granite stones in cement mortar (1:6) for basement, including cost and conveyance of all materials, labour charges, curing, all leads and lifts, etc, complete for finished item of work. | Civil | Labour | SWR33041 | 4890 | Cum | 133839.3
38 | 133.29 | Supplying and filling the substation site with borrowed gravel, watering, ramming, thoroughly complying with the standard specification. | Civil | Labour | SWR33052 | 339 | Cum | 45185.31
39 |  | 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge
40 | 5.346 | a) RCC M20 Grade Footings 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33098 | 9500 | Cum | 50787
41 | 3.42 | b)RCC M20 Grade Columns 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33100 | 13249 | Cum | 45311.58
42 | 4.03 | c)RCC M20 Grade Plinth Beams 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33099 | 12371 | Cum | 49855.13
43 | 3.55 | D) RCC M20 Grade Roof Beams 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33121 | 12287 | Cum | 43618.85
44 | 0.58 | e) RCC M20 Grade Lintels 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33107 | 13078 | Cum | 7585.24
45 | 2.7 | f) RCC M20 Grade Sunshades 600mm wide and 75mm thick 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33114 | 1376 | Sqm | 3715.2
46 | 19.206 | g) RCC M20 Grade Roof Slab 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33128 | 10875 | Cum | 208865.25
47 | 4.55 | reinforcement steel Supplying, Cutting, bending, binding, placing in position and tying reinforcement steel in all heights including cost and conveyance of steel and binding wire etc,. With all leads and lifts, labour charges, etc., complete for finished item of work. | Civil | Labour | SWR33144 | 70687 | MT | 321625.85
48 | 59.32 | Brick masonry in CM (1:6) for superstructure using well burnt country made second class bricks of approved quality including cost and conveyance of all materials curing, scaffolding with all leads and lifts in all heights etc., complete for fin | Civil | Labour | SWR33068 | 8262 | Cum | 490101.84
49 | 536.48 | Plastering with CM 2 coats, 20 mm thick, base coat in CM (1:6), 16 mm thick and top coat in CM (1:4), 4mm thick with Dubara sponze finishing including cost of all materials, seigniorage charges, excluding conveyance charges of materials and including all operational, incidental and labour charges for mixing mortar, laying rendering smooth and thread lining, curing, rounding off junctions of wall and slab etc., complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33163 | 561 | Sqm | 300965.28
50 | 85.68 | Providing Structural steel tube box type 60x40x4mm thick including cost and conveyance of all materials, labour charges,curing etc. complete for finished item of work and as directed by the engineer-in-charge. | Civil | Labour | SWR33146 | 147 | Kgs | 12594.96
51 | 18 | Providing Roofing with Trapezoidal/Galvalume Sheet including cost and conveyance of all materials, labour charges,curing etc. complete for finished item of work and as directed by the engineer-in-charge. | Civil | Labour | SWR33402 | 600 | Sqm | 10800
52 | 18.9 | Providing Design R.C.M. drop wall of 40mm thickness with cm 1:2 and 6mm dia MS bars at 150mm both ways and chicken mesh in two coats 20mm thick each plastering including cost and conveyance of all materials with leads and lifts, scaffolding and curing, labo | Civil | Labour | SWR33203 | 3070 | Sqm | 58023
53 | 12.24 | Supply and fixing of MS ornamental safety grill of approved design including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33310 | 2990 | Sqm | 36597.6
54 | 5.91 | Supply and fixing of doors with the MT Wood frames the door shall be made well seasoned mt wood of cross section 100x75mm. The shutter shall be made isi mark flushed door with decolam sheets pasted on both sides with PVC beading 40mm width all round.Frame shall be painted with two coats of synthetic enamel paint of approved color over one coat of primer over luppum with spary with 3 no 150mm brass hinges 1 no brass door stoper, 1 no 250mm brass aldrops. 2 no 300 mm aluminium tower bolts, 2 no 150mm brass fancy door handlers, 1 no keyless lockset with cp handel. The quoted rate shall include cost and conveyance of the meterials, fixig, labour carges, tools, handles,locking arrangementts and other fixtures & fittings for finished item work as directed by the Engineer - in- charge. | Civil | Labour | SWR33264 | 7314 | Sqm | 43225.74
55 | 20.25 | Raised pointing to the exposed surfaces of CRS masonry in cm 1:3 prop. including cost and conveyance of all materials, labour charges, all leads and lifts curing etc, complete for finished item of work. | Civil | Labour | SWR33184 | 125 | sqm | 2531.25
56 | 8.64 | Supplying and fixing Aluminium sliding windows with grill and fixed glass panels using anodised aluminium extruded sections of mat finish for frames and mullions made from approved aluminium sections 62x32x1.2mm at 0.73kg/Rm providing 5mm plain glass fix | Civil | Labour | SWR33277 | 3623 | sqm | 31302.72
57 | 16.56 | Supply and laying of Ceramic floor over of CM 1:3 20 mm thick including required materials and labour charges etc complete for item of work | Civil | Labour | SWR33224 | 914 | Sqm | 15135.84
58 | 121.92 | Flooring with double machine polished and hand cut Tandur blue stone 20mm thick of approved colour, quality and of minimum of 300x300mm size over a bed of cement mortar 1:3 20mm thick including cost of all materials, with all leads and lifts jointing and | Civil | Labour | SWR33219 | 786 | Sqm | 95829.12
59 | 6.74 | Supply and fixing of 4" high skirting of shabad stone to the walls including cost and conveyance of all materials, labour etc for finished item of work. | Civil | Labour | SWR33236 | 876 | Sqm | 5904.24
60 | 243.69 | Painting with two coats of OBD over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials labour charges etc., complete for finished item of work. | Civil | Labour | SWR33333 | 146 | Sqm | 35578.74
61 | 414.315 | Painting with two coats of Plastic emulsn paint 2 coat of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33356 | 210 | Sqm | 87006.15
62 | 129.92 | Providing impervious coat over RCC roof slab to requried slopes with 20mm thick in CM 1:3 mixed with approved brand of water proffing compound inclding cost and conveyance of all materials, labour charges, curing, rounding off junctions of wall and slab, all leads and lifts, etc . complete for finished item of work as directed by the Engineer - in - charge. | Civil | Labour | SWR33156 | 584 | Sqm | 75873.28
63 | 60 | Supply & fixing of 25mm dia 2mm thick surface P.V.C. pipe (ISI MARK) Concealed in wall with all required accessories including masonary work and labour charges etc.complete. | Civil | Labour | SWR33441 | 108 | M | 6480
64 | 1 | Supply & fixing TPNDB Distribution board with IP-42 protection (Metal Door)suitable for 3 phase ELCB/RCCB/FP Isolator as incomer and 10kA SP MCBs as out going including internal connection and labour charges for surface / flush mounting etc Complete. | Civil | Labour | SWR33526 | 11353 | EA | 11353
65 | 10 | Supply & fixing Flush type of 6A 3 pin wall plug socket with 6A switch control on a common switch board with earth continuity including wire leads,earth connection along with all labour charges etc., complete | Civil | Labour | SWR33468 | 166 | EA | 1660
66 | 6 | Supply & fixing Flush type of 16A 3 pin and 6A 3pin plug Flush type socket with indicator lamp and 16Amps fuse unit and 16Amps switch control (5 in one )duly recessed in wall with wooden deep box of 6'' x 8'' x 2 1/2'' size covered with hylam sheet earth connection and all labour charges etc., complete on wall. | Civil | Labour | SWR33470 | 449 | EA | 2694
67 | 24 | Supply and Fixing of modular switch, LP,FP,EFP,Wiring with 2 runs of 14/0.3mm (1.0 sq.mm)Fire Retardant (FR) P.V.C. insulated flexible copper cable (ISI MARK) in existing pipe with 6A Flush type Switch,ceiling rose and 3mm thick hylam sheet covering to switch control box including all labour charges etc., complete for light points, bell , fan and exhaust fan points in Non-Residential Buildings. | Civil | Labour | SWR33457 | 676 | EA | 16224
68 | 12 | Supply & Fixing of 28W T5 fluorescent tube. | Civil | Labour | SWR33558 | 148 | EA | 1776
69 | 1 | Supply of 12" (300mm)ISI, 900 RPM light duty exhaust fan with metallic blades with Mark of makes Crompton / Bajaj / Havells / Orient. | Civil | Labour | SWR33571 | 2192 | EA | 2192
70 | 180 | Supply and run of 2 of 22/0.3mm (1.5 sq.mm) (FR) P.V.C. insulated flexible copper cable in existing pipe for mains including all labour charges complete. | Civil | Labour | SWR33496 | 75 | M | 13500
71 | 180 | Supply and run of 2 of 36/0.3mm (2.5 sq.mm) FR P.V.C. insulated flexible copper cable in existing pipe for mains including all labour charges complete. | Civil | Labour | SWR33497 | 103 | M | 18540
72 | 12 | Supply & fixing of batten holder /slanting holder in lieu of ceiling rose of light point complete with all connection and all labour charges with 40W bulb (for new installation). | Civil | Labour | SWR33484 | 141 | EA | 1692
73 | 4 | Supply & fixing of 1200mm (48'') sweep 230v,A.C 50 Hz.Ceiling fan with 3 Blades and double ball bearings with all standared accessories. | Civil | Labour | SWR33563 | 2277 | EA | 9108
74 | 4 | Supply & fixing of Electronic Regulator for ceiling fans 900/1200/1400mm sweep including cost of material, Electrical charges complete for finished item of work | Civil | Labour | SWR33564 | 589 | EA | 2356
75 | 1 | Providing independent EARTHING by excavating a trench to a depth of 2.1M in all solid,as per size specified in the Data,using 40mm dia 'B' class GI pipe of 2.5 Mtrs length with necessary accessories with hume pipe ring duly providing staggered holes including filling with equal proportion of salt and Charcoal in layers and all labour charges etc., compiete for small quarters. | Civil | Labour | SWR33596 | 5345 | EA | 5345
76 | 35 | Supplying, laying, jointing and testing 101.6 mm SWG SP-1 pipes of ISI make conforming to ISI 651 & 4127 with airtight cement joints in CM 1.5:1 prop. Including excavation of trenches and socket pits in any soil (except rock requiring blasting) up to 1524 mm(5'0") depth and refilling with watering and tamping. | Civil | Labour | SWR34281 | 755 | M | 26425
77 | 3 | Constructing 904.0 mm (3#0#) dia brick masonry inspection chamber as per IS - 4111: Part-1:1986 with cement mortar (1:6) prop using 2nd Class Clay Bricks of 225 mm thick from approved source having a minimum crushing strength of 5 N/sq.mm including plastering with cement mortar 1:3 prop; ½# thick both inside and outside fitted with 20# dia RCC manhole covers and frames including excavating pits up to a depth of 904 mm (3'-0") in all sorts of soils (excluding rock) and laying cement concrete (1:4:8) 150 mm thick using 40 mm HBG Metal and P.C.C. 1:2:4 benching and channel 100 mm thick as per Standard specification and including cost and conveyance of all materials like cement, sand, bricks, water etc., to site, cost of seigniorage charges on all materials and all incidental and operational, labour charges like mixing cement mortar, constructing masonry, lift charges, curing etc., complete for finished item of work as per Standard specification. | Civil | Labour | SWR34296 | 8766 | EA | 26298
78 | 4 | Supply & fixing of 110 mm dia - Door Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34381 | 128 | EA | 512
79 | 4 | Supply & fixing of 110 mm dia - Plain Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34380 | 100 | EA | 400
80 | 12 | Supply & fixing of 110 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand | Civil | Labour | SWR34377 | 462 | M | 5544
81 | 18 | Supply & fixing of 90 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand | Civil | Labour | SWR34378 | 410 | M | 7380
82 | 3 | Supplying & fixing 150 mm x 100 mm SWG gully traps conforming to ISI 651 & 4127 with C.I Grating & Cost. Brick masonry in CM 1:6 prop. Intermediate chamber and fitted with 304.8 mm x 288.6mm (12"x9") C.I Frame and hinged cover | Civil | Labour | SWR34286 | 767 | EA | 2301
83 | 1 | Supplying and Fixing of European Water Closet of 1st Quality | Civil | Labour | SWR34314 | 2228 | EA | 2228
84 | 6 | Supply & fixing 15 mm angle stop cock Indian make 400 grams Seiko/ Senior/ Nice/ Senior/ Nice or equivalent | Civil | Labour | SWR34328 | 721 | EA | 4326
85 | 4 | S&F 15 mm N.P bib tap Indian make 400 grams full turn Seiko/ Senior/ Nice or equivalent | Civil | Labour | SWR34329 | 296 | EA | 1184
86 | 1 | Supplying & Fixing Indian make Flat Back Wash Hand Basin (HSW/Parryware/ Neycer) 1st quality conforming to IS:2556-Part-4:1972 with waste fittings like rubber plug, chain, 32 mm nominal size C.P. Fitting with parallel pipe thread conforming to IS:2963-1979 and fitted with 15 mm nominal bore Chromium Plated Pillar Tap of 1st quality Indian make 400 grams Seiko/ Senior/ Nice/ Esso or equivalent complete with standard CI brackets including wooden block: 550 x 400 mm - Single C.P. Pillar cock | Civil | Labour | SWR34316 | 1717 | EA | 1717
87 | 2 | Supply & fixing 38.1 mm C.P waste coupling Half or Full Thread 1st Quality Indian make Parryware or equivalent | Civil | Labour | SWR34428 | 309 | EA | 618
88 | 2 | Supply & fixing of 4" (101.6 mm ) Nahany Trap ( Without Jali with inlet)UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34387 | 134 | EA | 268
89 | 1000 | Providing & Placing on Terrace (at all floor levels) polyethylene water storage tank with Double layer approved brand & manufacture with cover and suitable locking arrangement & making necessary holes for inlet & outlets and over flow pipes but with NECESSARY fittings & base support for tanks | Civil | Labour | SWR34375 | 10 | L | 10000
90 | 2 | Supply & fixing 31.75 mm dia PVC flexible waste pipe of 914.4 mm length of Ist quality | Civil | Labour | SWR34426 | 33 | EA | 66
91 | 45 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)- 15.90mm OD Pipe - SDR 11 | Civil | Labour | SWR34361 | 239 | M | 10755
92 | 40 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-22.20mm OD Pipe - SDR 11 | Civil | Labour | SWR34362 | 313 | M | 12520
93 | 65 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-28.60mm OD Pipe - SDR 11 | Civil | Labour | SWR34363 | 410 | M | 26650
94 | 4 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type - 25mm NB Size | Civil | Labour | SWR34346 | 466 | EA | 1864
95 | 4 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type -20mm NB Size | Civil | Labour | SWR34345 | 331 | EA | 1324
96 | 1 | Supply & fixing 25.4 mm dia & 609.6 mm long aluminium anodized towel rod with brackets and aluminium screws | Civil | Labour | SWR34430 | 489 | EA | 489
97 | 85.51 | Earth work excavation in all type of Ordinary soils red earth, Hard gravelly soils, earth mixed with sand and sandy soils etc., in all conditions such as slushy and dry with initial leads and lifts for foundations. Ordinary Soil | Civil | Labour | SWR33015 | 486 | cum | 41557.86
98 | 18.91 | PCC (1:4:8) using 40mm HBG metal for foundations and leveling course, including cost and conveyance of all materials, labour all leads and lifts, consolidation and all operations, formwork as required, curing, etc. complete for finished item w | Civil | Labour | SWR33028 | 4748 | cum | 89784.68
99 | 91.8 | Coursed Rubble stone masonry (CRS) 2nd sort with hard granite stones in cement mortar (1:6) for basement, including cost and conveyance of all materials, labour charges, curing, all leads and lifts, etc, complete for finished item of work. | Civil | Labour | SWR33041 | 4890 | cum | 448902
100 | 36 | PCC (1:3:6) using 40mm HBG metal for foundations and leveling course, including cost and conveyance of all materials, labour all leads and lifts, consolidation and all operations, formwork as required, curing, etc. complete for finished item w | Civil | Labour | SWR33029 | 5038 | cum | 181368
101 | 108 | Raised pointing to the exposed surfaces of CRS masonry in cm 1:3 prop. including cost and conveyance of all materials, labour charges, all leads and lifts curing etc, complete for finished item of work. | Civil | Labour | SWR33184 | 125 | sq.mm | 13500
102 | 787.5 | Supplying and filling the substation site with borrowed gravel, watering, ramming, thoroughly complying with the standard specification. | Civil | Labour | SWR33052 | 339 | cum | 266962.5
103 | 88.8 | Plastering with CM 2 coats, 20 mm thick, base coat in CM (1:6), 16 mm thick and top coat in CM (1:4), 4mm thick with Dubara sponze finishing including cost of all materials, seigniorage charges, excluding conveyance charges of materials and including all operational, incidental and labour charges for mixing mortar, laying rendering smooth and thread lining, curing, rounding off junctions of wall and slab etc., complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33163 | 561 | sq.mm | 49816.8
104 | 200.85 | Painting with two coats of Surya Cem paint over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33329 | 85 | sq.mm | 17072.25
105 | 120 | Supply&Fabrication and fixing of Welded wire mesh ( 2" x 2") of 3mm dia. with ISMC (75x40x4.4mm) and Pheriperal frame of ISA(35x35x3mm) incldg cost& conveyance painting with synthetic enamil paint two coats over a coat of red oxide primer etc complete for finished item of work.. | Civil | Labour | SWR33403 | 2310 | sq.mm | 277200
106 | 160 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-22.20mm OD Pipe - SDR 11 | Civil | Labour | SWR34362 | 313 | M | 50080
107 | 30 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type - 25mm NB Size | Civil | Labour | SWR34346 | 466 | EA | 13980
108 | 1 | Providing Consultancy services for arranging contour surveying with total station incuding preparation of boundary and contour levels with 2 Nos. Hard copies and soft copies complete for finished items of work | Civil | Labour | SWR33427 | 5665 | EA | 5665
109 | 576.115 | Seigniorage Charges - Sand | Civil | Labour | SWR34470 | 40 | cum | 23044.6
110 | 1837.383 | Seigniorage Charges - Metal | Civil | Labour | SWR34471 | 97.5 | cum | 179144.8425
111 | 920.79 | Seigniorage Charges - Gravel | Civil | Labour | SWR34472 | 30 | cum | 27623.7
112 | 60 | Supply and fixing of RCC fencing poles of size 0.1mx0.1mx1.8m (security fencing of sub station), including cost and conveyance of all labour, materials,and hire chareges etc complete for finished item of work. | Civil | Labour | Swr33405 | 1444 | EA | 86640
113 | 1200 | Supply and fixing of galvanised barded wire (1 horizantal & 2 cross strands. including cost and conveyance of all labour, materials,and hire chareges etc complete for finished item of work. | Civil | Labour | Swr33408 | 16 | M | 19200
Civil labour | [7 empty] | 9148489.4885
Electrical and Civil labour |  |  |  |  | 18% GST Rs. |  |  | 31271108.8355

## 13. Sahebnagar BN Reddy
Name of the Work :- Erection of 33/11 kV Outdoor SS Sahebnagar HMWS (BN Reddy) in LB Nagar(M) with connected 33kV and 6 No.s new 11kV feeders at Sahebnagar HMWS in LB Nagar (M) in ECGH Division, Masterplan, RR Circle
WBS No. S-1802-13-03-01-01-001
Sl No | Estimate Quantity | Description of item | Work Type | Item Short Description | APSS / Month Cl.NumberSSR 11 & 12 | Rate (INR) | UOM | AMOUNT
1 | 16 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | ElEC | Labour | SWR11039 | 928 | EA | 14848
2 | 5.76 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ElEC | Labour | SWR10868 | 6852 | TO | 39467.52
3 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ElEC | Supply | SMR40009 | 2181 | TO | 12562.56
4 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ElEC | Labour | SWR10877 | 851 | TO | 4901.76
5 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ElEC | Supply | SMR40010 | 1293 | TO | 7447.68
6 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ElEC | Labour | SWR10879 | 482 | TO | 2776.32
7 | 5.76 | Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ElEC | Labour | SWR10867 | 1470 | TO | 8467.2
8 | 16 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-R.S. Joists 150 x 150 mm | ElEC | Labour | SWR10348 | 1952.61 | EA | 31241.76
9 | 17.758 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ElEC | Labour | SWR10356 | 6579 | M3 | 116829.882
10 | 9.24 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ElEC | Labour | SWR10862 | 373 | M2 | 3446.52
11 | 16 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | ElEC | Labour | SWR11089 | 48 | EA | 768
12 | 4 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-8.0Mtrs PSCC Poles 0.76 M x 0.76M x 1.52M (2.6" x 2.6" x 5.0') 0.88 cum | ElEC | Labour | SWR11037 | 793 | EA | 3172
13 | 1 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ElEC | Labour | SWR10868 | 6852 | TO | 6852
14 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ElEC | Supply | SMR40009 | 2181 | TO | 2181
15 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ElEC | Labour | SWR10877 | 851 | TO | 851
16 | 1 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ElEC | Supply | SMR40010 | 1293 | TO | 1293
17 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ElEC | Labour | SWR10879 | 482 | TO | 482
18 | 1 | Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ElEC | Labour | SWR10867 | 1470 | TO | 1470
19 | 4 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Box pole 12 Mtr | ElEC | Labour | SWR11267 | 3901.37 | EA | 15605.48
20 | 2.65 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ElEC | Labour | SWR10356 | 6579 | M3 | 17434.35
21 | 2.31 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ElEC | Labour | SWR10862 | 373 | M2 | 861.63
22 | 4 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | ElEC | Labour | SWR11089 | 48 | EA | 192
23 | 5.063 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ElEC | Labour | SWR10868 | 6852 | TO | 34691.676
24 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ElEC | Supply | SMR40009 | 2181 | TO | 11042.403
25 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ElEC | Labour | SWR10877 | 851 | TO | 4308.613
26 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ElEC | Supply | SMR40010 | 1293 | TO | 6546.459
27 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ElEC | Labour | SWR10879 | 482 | TO | 2440.366
28 | 5.063 | Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ElEC | Labour | SWR10867 | 1470 | TO | 7442.61
29 | 13 | Erection of AB Switch and aligment complete Erection of 33 KV AB Switch including alignment and earthing | ElEC | Labour | SWR10392 | 4500 | EA | 58500
30 | 34 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Note:-The requirement of 2nd coat is to be justified by the concerned Divisional Engineer /Executive Engineer before execution of this work Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | ElEC | Labour | SWR10881 | 142 | EA | 4828
31 | 34 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | ElEC | Labour | SWR12331 | 146.63 | EA | 4985.42
32 | 6 | Loading of 33 KV CTs/ PTs | ElEC | Labour | SWR10200 | 165 | EA | 990
33 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ElEC | Labour | SWR11861 | 3299.7 | EA | 3299.7
34 | 6 | Un loading of 33 KV CTs/ PTs | ElEC | Labour | SWR10518 | 128 | EA | 768
35 | 2 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33kv single phase PT s | ElEC | Labour | SWR10401 | 1079 | SET | 2158
36 | 12 | Loading of 33 KV, 10 KA LAs Station typ | ElEC | Labour | SWR10266 | 41 | EA | 492
37 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ElEC | Labour | SWR11861 | 3299.7 | EA | 3299.7
38 | 12 | Un loading of 33 KV, 10 KA LAs Station type | ElEC | Labour | SWR10584 | 35 | EA | 420
39 | 4 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33 KV LAS station/Line type including earthing | ElEC | Labour | SWR10396 | 880 | SET | 3520
40 | 2 | Loading of 33 KV VCBs along with Panel boards | ElEC | Labour | SWR10198 | 1024 | EA | 2048
41 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ElEC | Labour | SWR11861 | 3299.7 | EA | 3299.7
42 | 2 | Un loading of 33 KV VCBs along with Panel boards | ElEC | Labour | SWR10516 | 1044.48 | EA | 2088.96
43 | 12.584 | Excavate-Pit for 33KV VCB | ElEC | Labour | SWR23224 | 331 | M3 | 4165.304
44 | 14.52 | Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x 1.8 x 0.75 cum for VCB Plinth | ElEC | Labour | SWR20685 | 5160 | M3 | 74923.2
45 | 2 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33 KV VCB with Control Panel | ElEC | Labour | SWR10460 | 12500 | EA | 25000
46 | 2 | Loading and unloading of PTR on constructed plinth-Loading of 8MVA PTR | ElEC | Labour | SWR10613 | 5805.84 | EA | 11611.68
47 | 2 | Transport of Power transformers (0 to 100 KM) from one place to another place in GHMC Area.(excluding of loading & unloading )-8MVA power transformer | ElEC | Labour | SWR10854 | 21945 | EA | 43890
48 | 2 | Loading and unloading of PTR on constructed plinth-Unloading of 8MVA PTR | ElEC | Labour | SWR10627 | 5805.84 | EA | 11611.68
49 | 700 | S/o rail poles 90/105lb (250x2N) | ElEC | Labour | SMR22718 | 47.27 | KG | 33089
50 | 14 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Rail pole 90 lbs | ElEC | Labour | SWR10344 | 3510 | EA | 49140
51 | 2 | Erection of PTR on constructed plinth-Erection of 8 MVA PTR. | ElEC | Labour | SWR21321 | 49480.2 | EA | 98960.4
52 | 0.436 | Extention of 33KV Bay at 132/33KV Sub-station-Zebra condutor | ElEC | Labour | SMR24910 | 299369 | KM | 130524.884
53 | 30 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing | ElEC | Supply | SMR11915 | 2055 | SET | 61650
54 | 30 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of I-Bolts | ElEC | Supply | SMR22473 | 294 | EA | 8820
55 | 45 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 "to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating . Sup T clamp LM6 Al alloy of 12 mm, 800 A | ElEC | Supply | SMR40011 | 299 | EA | 13455
56 | 6 | Bus stringing Hoisting of Insulators and hardware, stretching the conductor and stringing of 33 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bussection of 4.5mt) Hoisting post ins&hrd wr 1panther 33kv | ElEC | Labour | SWR21240 | 781 | EA | 4686
57 | 84 | Stringing of bus with panther conductor including jumpering etc., complete to all the equipment in SS fixing to all clamps and equipment.(3 Conductors) | ElEC | Labour | SWR10404 | 327.68 | M | 27525.12
58 | 30 | Bus stringing Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | ElEC | Labour | SWR10884 | 224 | EA | 6720
59 | 75 | Labour for Fixing of all types of clamps | ElEC | Labour | SWR10917 | 65 | EA | 4875
60 | 25 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | ElEC | Labour | SWR11039 | 928 | EA | 23200
61 | 8.68 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ElEC | Labour | SWR10868 | 6852 | TO | 59475.36
62 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ElEC | Supply | SMR40009 | 2181 | TO | 18931.08
63 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ElEC | Labour | SWR10877 | 851 | TO | 7386.68
64 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ElEC | Supply | SMR40010 | 1293 | TO | 11223.24
65 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ElEC | Labour | SWR10879 | 482 | TO | 4183.76
66 | 8.68 | Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ElEC | Labour | SWR10867 | 1470 | TO | 12759.6
67 | 25 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-R.S. Joists 150 x 150 mm | ElEC | Labour | SWR10348 | 1952.61 | EA | 48815.25
68 | 27.75 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ElEC | Labour | SWR10356 | 6579 | M3 | 182567.25
69 | 17.91 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ElEC | Labour | SWR10862 | 373 | M2 | 6680.43
70 | 25 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | ElEC | Labour | SWR11089 | 48 | EA | 1200
71 | 4.642 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ElEC | Labour | SWR10868 | 6852 | TO | 31806.984
72 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ElEC | Supply | SMR40009 | 2181 | TO | 10124.202
73 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ElEC | Labour | SWR10877 | 851 | TO | 3950.342
74 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ElEC | Supply | SMR40010 | 1293 | TO | 6002.106
75 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ElEC | Labour | SWR10879 | 482 | TO | 2237.444
76 | 4.642 | Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ElEC | Labour | SWR10867 | 1470 | TO | 6823.74
77 | 17 | Erection of AB Switch and aligment complete-Erection of 11KV 800A double throw AB Switches | ElEC | Labour | SWR21277 | 3500 | EA | 59500
78 | 3 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | ElEC | Labour | SWR10393 | 3200 | EA | 9600
79 | 2 | Loading of 11 KV CT - PT Sets | ElEC | Labour | SWR10201 | 190 | EA | 380
80 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ElEC | Labour | SWR11861 | 3299.7 | EA | 3299.7
81 | 2 | Un loading of 11 KV CT - PT Sets | ElEC | Labour | SWR10519 | 101 | EA | 202
82 | 2 | Erection of 11 KV three phase PTs | ElEC | Labour | SWR10402 | 800 | SET | 1600
83 | 24 | Loading of 11 KV, 10 KA LAs Station type | ElEC | Labour | SWR10264 | 32 | EA | 768
84 | 2 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ElEC | Labour | SWR11861 | 3299.7 | EA | 6599.4
85 | 24 | Un loading of 11 KV, 10 KA LAs Station type | ElEC | Labour | SWR10582 | 32 | EA | 768
86 | 2 | Erection of 11 KV LAS station type including earthing | ElEC | Labour | SWR10397 | 559 | SET | 1118
87 | 6 | Erection of 11 KV LAS line type including earthing | ElEC | Labour | SWR10398 | 505 | SET | 3030
88 | 8 | Loading of 11 KV VCBs along with Panel boards | ElEC | Labour | SWR10199 | 1024 | EA | 8192
89 | 4 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ElEC | Labour | SWR11861 | 3299.7 | EA | 13198.8
90 | 8 | Un Loading of 11 KV VCBs along with Panel boards | ElEC | Labour | SWR10517 | 1044.48 | EA | 8355.84
91 | 41.6 | Excavate-Pit for 33KV VCB | ElEC | Labour | SWR23224 | 331 | M3 | 13769.6
92 | 48 | Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x 1.8 x 0.75 cum for VCB Plinth | ElEC | Labour | SWR20685 | 5160 | M3 | 247680
93 | 8 | Erection of 11 KV VCB with Control Panel | ElEC | Labour | SWR10461 | 12000 | EA | 96000
94 | 12 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing | ElEC | Supply | SMR11915 | 2055 | SET | 24660
95 | 12 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of I-Bolts | ElEC | Supply | SMR22473 | 294 | EA | 3528
96 | 45 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 "to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating . Sup T clamp LM6 Al alloy of 12 mm, 800 A | ElEC | Supply | SMR40011 | 299 | EA | 13455
97 | 2 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 11 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 3.5mt) Hoisting post ins&hrd wr 1panther 11kv | ElEC | Labour | SWR21241 | 507 | EA | 1014
98 | 63 | Stringing of bus with panther conductor including jumpering etc., complete to all the equipment in SS fixing to all clamps and equipment.(3 Conductors) | ElEC | Labour | SWR10404 | 327.68 | M | 20643.84
99 | 45 | Bus stringing Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | ElEC | Labour | SWR10884 | 224 | EA | 10080
100 | 57 | Labour for Fixing of all types of clamps | ElEC | Labour | SWR10917 | 65 | EA | 3705
101 | 584 | Laying of earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication 75x 8mm MS Flat / GI Flat. Laying of earth mat,excavation 75x 8mm | ElEC | Labour | SWR10920 | 65 | RMT | 37960
102 | 1010 | Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) Earthing for raisers of SS Flat 50x6 mm. | ElEC | Labour | SWR10919 | 41 | RMT | 41410
103 | 36 | Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | ElEC | Supply | SMR11482 | 3486 | EA | 125496
104 | 36 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | ElEC | Labour | SWR10357 | 1234.2 | EA | 44431.2
105 | 36 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINES-Providing of RCC collar | ElEC | Labour | SWR10359 | 386 | EA | 13896
106 | 2 | Supply of Copper Flexible jumper with 75 X 8 of length 250 mm at neutral of Power tranformer end and 50 X 6 of length 50mm two Nos at double neutral end duly brasing with flexible jumper of capacity of 5kA/3 sec for power transformer neutral. SupCU Flexi jumper for Power T/F Neutral | ElEC | Supply | SMR40033 | 4725 | EA | 9450
107 | 2 | Providing of earthing with various types of earth electrodes-Providing of double earthing for neutral with flexible copper jumpers including arrangement by fixing M.S.Channel 100x50mm. | ElEC | Labour | SWR11892 | 1323 | EA | 2646
108 | 4 | Loading of LT AB Cable 3X16+25 Sqmm | ElEC | Labour | SWR11702 | 200 | DR | 800
109 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ElEC | Labour | SWR11861 | 3299.7 | EA | 3299.7
110 | 4 | Un loading of LT AB Cable 3X16+25 Sqmm | ElEC | Labour | SWR11713 | 204 | DR | 816
111 | 80 | Providing of control cable trench as per DATA-XII | ElEC | Labour | SWR22093 | 3148 | RMT | 251840
112 | 3074 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends . Lay-4C/10C 2.5Sqmm Control Cable | ElEC | Labour | SWR11879 | 27 | M | 82998
113 | 270 | Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per specification (including cost of ferrules, lugs and glands) | ElEC | Labour | SWR12510 | 27 | EA | 7290
114 | 4 | Marshalling Box Supply of FRP PT Marshalling Box | ElEC | supply | SMR40048 | 4463 | EA | 17852
115 | 4 | Marshalling Box Erection of Marshalling boxes | ElEC | Labour | SWR10940 | 374.85 | EA | 1499.4
116 | 1 | Loading of 220 V Batterry with charger | ElEC | Labour | SWR11166 | 1612 | SET | 1612
117 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ElEC | Labour | SWR11861 | 3299.7 | EA | 3299.7
118 | 1 | Un loading of 220 V Batterry with charger | ElEC | Labour | SWR11147 | 1024 | SET | 1024
119 | 1 | Batteries-Erection of 220 V, 200 AH battery in complete shape fit for | ElEC | Labour | SWR12350 | 7666 | EA | 7666
120 | 1 | Supply of DC Annunciation & relay panel for 10 feeder panel including the cost of LED Indiacation lamps, VAA auxilairy relays, Electronic Hooters complete as per specification. | ElEC | supply | SMR40044 | 42500 | EA | 42500
121 | 1 | Supply of AC Supply panel inluding providing of changeover switch, SFU, metering unit, 32 A three phase MCB, 16 A Single phase MCB complete as per specification. Supply of AC Supply panel complete | ElEC | Supply | SMR40045 | 42000 | EA | 42000
122 | 2 | Fixing of AC/DC Panel and giving Connections to the protection equipment and Metering circuits as per the specification and standards. The 3 1/2 core 25 Sqmm power cable required from distribution box to AC/DC panel in the control room is also to be supply | ElEC | Labour | SWR20025 | 7871.85 | SET | 15743.7
123 | 8 | Yard lightning-Supply of stepped tubular poles single way made of steel of length 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9 mm, 2.1 mtrs with outer dia 76.1 mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79 kgf as per IS 2713 | ElEC | Supply | SMR40051 | 13913 | EA | 111304
124 | 8 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE/CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA /OSRAM /SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty S-90W LED fixture set | ElEC | Supply | SMR11594 | 8200 | EA | 65600
125 | 8 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | ElEC | Labour | SWR11039 | 928 | EA | 7424
126 | 8 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE / CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA/OSRAM/SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty-Erection of tubular poles | ElEC | Labour | SWR10955 | 1379 | EA | 11032
127 | 5.27 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ElEC | Labour | SWR10356 | 6579 | M3 | 34671.33
128 | 8 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE/CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA /OSRAM /SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty. Fixing of Metal halide lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5 GI pipe complete Fixing of LED/Metal halide complete. | ElEC | Labour | SWR10956 | 1268 | EA | 10144
129 | 45 | Supply of HBG metal-Supply & spreading of 20mm machine crushed metal (HBG) including cost of conveneyance of all materials, labour charges etc complete for finished item of work and directed by the engineer incharge | ElEC | Supply | SWR10860 | 2113 | M3 | 95085
130 | 2 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M Ex of Hard pit w/o blast 0.75X0.9X1.95M | ElEC | Labour | SWR11040 | 990.68 | EA | 1981.36
131 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ElEC | Supply | SMR40009 | 2181 | TO | 1635.75
132 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ElEC | Labour | SWR10877 | 851 | TO | 638.25
133 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ElEC | Supply | SMR40010 | 1293 | TO | 969.75
134 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ElEC | Labour | SWR10879 | 482 | TO | 361.5
135 | 1 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Box pole 12 Mtr | ElEC | Labour | SWR11267 | 3901.37 | EA | 3901.37
136 | 2.22 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ElEC | Labour | SWR10356 | 6579 | M3 | 14605.38
137 | 1.16 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ElEC | Labour | SWR10862 | 373 | M2 | 432.68
138 | 2 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | ElEC | Labour | SWR11089 | 48 | EA | 96
139 | 1 | Construction of DTR Plinth-RCC Column type DTR Plinth of size 1'X1'X10',topslab 4'x4'x6" & beam size 4'X8'X8" upto 160KVA | ElEC | Labour | SWR21843 | 25967.57 | EA | 25967.57
140 | 1 | Loading of 50,63, 75 & 100 KVA DTR | ElEC | Labour | SWR10195 | 350 | EA | 350
141 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ElEC | Labour | SWR11861 | 3299.7 | EA | 3299.7
142 | 1 | Un loading of 50,63, 75 & 100 KVA DTR | ElEC | Labour | SWR10513 | 280 | EA | 280
143 | 1 | Erection of DTR's including loading and Unloading DTR on the Structure/Plinth etc-Erection of 3 Phase DTRs 63,75 & 100 KVA | ElEC | Labour | SWR20905 | 1650 | EA | 1650
144 | 1 | Erection of AB Switch and aligment complete Erection of 11KV 200A TT type AB Switch including fixing of cross angles and alignment complete | ElEC | Labour | SWR20102 | 1813.49 | EA | 1813.49
145 | 1 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc -- Erection of 11 KV HG Fuse set including earthing | ElEC | labour | SWR10395 | 740.52 | SET | 740.52
146 | 40 | Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.-In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road-11KV 3x185 Sqmm Cable | ElEC | Labour | SWR11920 | 465.46 | M | 18618.4
147 | 20 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-11 KV 3x185 Sqmm Cable | ElEC | Labour | SWR11956 | 126.23 | M | 2524.6
148 | 2 | UG Cables Joints Making of Outdoor/Indoor End Termination OD/Idoor end termination 11kv 3x185 xlpe | ElEC | Labour | SWR10390 | 2370.63 | EA | 4741.26
149 | 1 | Erection of LT distribution box including laying of LT cable from distribution box to LT OH line and DTR to distribution box including earthing of distribution box and crimping of lugs connecting of jumpers etc | ElEC | Labour | SWR10674 | 1594.67 | EA | 1594.67
150 | 85 | LAYING OF 33KV, 11KV UG CABLE Excavation & laying of UG Cable in Single Run Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road-LT 3 1/2 x 185 Sqmm Cable | ElEC | Labour | SWR11923 | 377.63 | M | 32098.55
151 | 15 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-LT 3 1/2 x 185 Sqmm Cable | ElEC | Labour | SWR11959 | 85.43 | M | 1281.45
152 | 2 | Supply & fixing of Oout Door/Indoor end termination LT 3 1/2 x 185 Sqmm Cable | ElEC | Labour | SWR10765 | 968.9 | EA | 1937.8
153 | 1 | Supply and fixing of Substation board of size 3'x2.5' indicating the layout of switchyard Sup &fix of board ind Switchyard layout | ElEC | Supply | SWR20032 | 1654 | EA | 1654
154 | 1 | Supply and fixing of safety instructions/Substation operation instruction board. Sup& fix safety inst/SS Op. inst board | ElEC | Supply | SWR22090 | 2205 | EA | 2205
155 | 750 | Control Panels Supplying & fabrication erection of 6mm Checkerd plates as per the field conditions Supply,fabricati of 6mm Checkerd plates | ElEC | Labour | SWR10873 | 83 | KG | 62250
156 | 1 | T & P Supply of Wall clock standard make | ElEC | Supply | SMR40059 | 578 | EA | 578
157 | 1 | S-10ft Aluminium Ladder | ElEC | Supply | SMR12378 | 1654 | EA | 1654
158 | 1 | Sup Alluminium Ladder for indoor works | ElEC | Supply | SMR40062 | 4410 | EA | 4410
159 | 30 | T & P Painting of Name Plates for any equipmen | ElEC | Labour | SWR10963 | 122 | EA | 3660
160 | 1 | T & P Supply of Taparia Tool kit of Size 20”x10”x15” with tier arrangements Tool box with locking arrangement & key containing (1) Double Ended fix Spanner sets, (Ribbed) 6 x 7, 8 x 9, 10 x 11, 12 x 13, 14 x 15, 16 x 17, 18 x19, 20 x 22, 21 x 23, 24 x 27, 25 x28, 30 x 32, (2) Double Ended Ring Spanners sets, 6 x 7 , 8 x 9, 10 x 11, 12 x 13, 14 x 15. 16 x 17 , 18 x 19, 20 x 22 , 21 x 23, 24 x 27, 25 x28, 30 x 32 mm, (3) Adjustable Spanner 305 mm length least maximum opening 35mm chrome, (4) Pipe Wrench Length 350 mm 14”, (5) Soft faced Hammer with suitable handle 2 lb, (6) Hacksaw frame with metal handle heavy duty for 12" hacksaw blade with High Speed blade, (7) Insulated Screw drivers Transparent Green Handle Set Length 6”, 8” & 12”, (8) Star Screw Driver Transparent Green Handle Length 6”, (9) Insulated Wire Cutter, (10) Insulated Cutting Plier Length 8” with cable stripper insulated with thick C. A. sleeve confirming to IS: 4378 - 1990, (11) Long Nose Plier insulated with thick C.A. sleeve generally confirming to IS:3552-1989, (12) Tester type screw driver (special with neon bulb) generally confirm to IS: 5579- 1985 Grade:II handle yellow/ green colour overall length 130 mm, (13) Insulated Crimping Plier of all Taparia make. SupTaparia Tool kit complete as per Spec | ElEC | Supply | SMR40063 | 4925 | SET | 4925
161 | 1 | T & P Sup Rechargeable LED torch light of Standard make | ElEC | Supply | SMR40064 | 1733 | EA | 1733
162 | 1 | T & P-Steel almarah(61/2 X 3ft) Godrej | ElEC | Supply | SMR40061 | 9818 | EA | 9818
163 | 1 | T & P-Table (3x6ft) Godrej | ElEC | Supply | SMR40057 | 6050 | EA | 6050
164 | 4 | T & P-S type chairs (Godrej) | ElEC | Supply | SMR40058 | 924 | EA | 3696
165 | 1 | T & P Sup Angle racks(18x36.6inches) Godrej | ElEC | Supply | SMR40060 | 1733 | EA | 1733
166 | 1 | T & P Supply of Hack saw (12 inches) | ElEC | Supply | SMR40065 | 289 | EA | 289
167 | 4 | Sup Earth Rods (8ft) Screw & clamp type | ElEC | Supply | SMR40066 | 578 | EA | 2312
168 | 2 | Supply of Hand Gloves | ElEC | Supply | SMR40067 | 289 | SET | 578
169 | 12 | SupRubber mats( 6'x3')size fo indoorSS | ElEC | Labour | SMR40068 | 1386 | EA | 16632
170 | 1 | Biometric Time attendence System & Telecom Sup Stand basic cell phone with charger | ElEC | Supply | SMR40069 | 1386 | EA | 1386
171 | 14 | Supply of Danger boards with clamps | ElEC | Supply | SMR40070 | 116 | EA | 1624
172 | 2 | Fire bucket stand with 3 buckets (8 -10 ltr capacity) | ElEC | Supply | SMR40088 | 1386 | SET | 2772
173 | 2 | Room fire extinguisher (2 ltrs capacity) for control room | ElEC | Supply | SMR40089 | 4620 | EA | 9240
174 | 4 | Sup TrollyMounted Co2 (6.5Kgs) Cylinders(IS-2878) | ElEC | Supply | SMR40087 | 9240 | EA | 36960
175 | 6 | Supply of Safety Helmet of standard make | ElEC | Supply | SMR40071 | 231 | EA | 1386
176 | 8 | Supply of LC Boards | ElEC | Supply | SMR40072 | 116 | EA | 928
177 | 4 | Supply of Gum Boots(Pair) | ElEC | Supply | SMR40073 | 693 | EA | 2772
178 | 1 | Supply of 5000v megger | ElEC | Supply | SMR40074 | 13860 | EA | 13860
179 | 1 | Supply of Earth megger (1000v) | ElEC | Supply | SMR40075 | 8085 | EA | 8085
180 | 1 | Supply of Digital clamp meter. | ElEC | Supply | SMR40076 | 2888 | EA | 2888
181 | 1 | Name board of the 33/11kV Sub-Station(As per Standard Specification) Sup 33/11kv S.S Permanent name board | ElEC | Supply | SMR40086 | 10238 | EA | 10238
182 | 800 | Supply of Hot dip galvanized/zinc coated bolts & nuts including spring washers, pack washers and flat washers etc. | ElEC | Supply | SMR12488 | 90 | KG | 72000
183 | 2 | Fabrication of poles-Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | ElEC | Labour | SWR10642 | 512.55 | EA | 1025.1
184 | 1 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-RS Joists 150x75/175 x 85 mm | ElEC | Labour | SWR10346 | 1934 | EA | 1934
185 | 5760 | Supply of Materials -- Supply of RS Joist girder Poles (150X150mm) | ElEC | Supply | SMR12302 | 59.25 | KG | 341280
186 | 1000 | Supply of Materials -- supply of RS Joist Poles (175X85mm) | ElEC | Supply | SMR12303 | 60.75 | KG | 60750
187 | 5063 | Supply of Materials -- Supply of MS Channel 100X50mm | ElEC | Supply | SMR22745 | 57.45 | KGS | 290869.35
188 | 13 | Supply of Materials -- Supply of 33 kV 800 A Double break AB switch | ElEC | Supply | SMR12315 | 40658.78 | EA | 528564.14
189 | 8680 | Supply of Materials -- Supply of RS Joist girder Poles (150X150mm) | ElEC | Supply | SMR12302 | 59.25 | KG | 514290
190 | 4642 | Supply of Materials -- Supply of MS Channel 100X50mm | ElEC | Supply | SMR22745 | 57.45 | KGS | 266682.9
191 | 17 | Supply of Materials -- Supply of 11 kV 800 A Double break AB switch | ElEC | Supply | SMR12316 | 30847.46 | EA | 524406.82
192 | 3 | Supply of Materials -- Supply of 11 kV 400 A Double break AB switch | ElEC | Supply | SMR12317 | 18150 | EA | 54450
193 | 3045 | Supply of Materials -- Supply of MS Flat 75x8 mm | ElEC | Supply | SMR12321 | 56.42 | KG | 171798.9
194 | 2666 | Supply of Materials -- Supply of MS Flat 50x6 mm | ElEC | Supply | SMR12322 | 56.5 | KG | 150629
195 | 750 | Supply of Materials -- supply of RS Joist Poles (175X85mm) | ElEC | Supply | SMR12303 | 60.75 | KG | 45562.5
196 | 1 | Supply of Materials -- Supply of 11 kV 200 A Tilting type AB switch | ElEC | Supply | SMR12318 | 8991 | EA | 8991
197 | 1 | Supply of Materials -- Supply of 11KV HG fuse set for station transformer | ElEC | Supply | SMR12324 | 1974 | EA | 1974
198 | 1 | Supply of LT Distribution Box (SMC) | ElEC | Supply | SMR25200 | 7797 | EA | 7797
199 | 2 | Supply of 11KV 3x185 Heat Shble O/d End Term Kit | ElEC | Supply | SMR25201 | 1182.97 | EA | 2365.94
200 | 40 | Supply of XLPE Cable 1 C 150 sqmm | ElEC | Supply | SMR25203 | 114.83 | M | 4593.2
201 | 100 | Supply of XLPE Cable 3 1/2 C 185 sqmm | ElEC | Supply | SMR25204 | 547 | M | 54700
202 | 1 | survey line&cabl inc peg mark&tree clear | ElEC | Labour | SWR22092 | 765 | KM | 765
203 | 21 | Load-11/33KV XLPE UG Cable for all sizes | ElEC | Labour | SWR11230 | 1024 | DR | 21504
204 | 11 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ElEC | Labour | SWR11861 | 3299.7 | EA | 36296.7
205 | 21 | Unload-11/33KV XLPE UG Cable for all sizes | ElEC | Labour | SWR11231 | 1024 | DR | 21504
206 | 1000 | #N/A | ElEC | Excavation & laying of UG Cable (Double Run) Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil/CC-33 KV 3x400 Sqmm Cable | SWR11972 | 749 | M | 749000
207 | 1800 | Excavation & laying of UG Cable (Double Run) Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, Along the CC / BT multi layer road requiring compressor-33 KV 3x400 Sqmm Cable | ElEC | Labour | SWR11980 | 1388.84 | M | 2499912
208 | 200 | Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, Across the CC/ BT road crossing multi layer road requiring compressor (excluding the cost of Hume pipe)-33 KV 3x400 Sqmm Cable | ElEC | Labour | SWR11988 | 1587.07 | M | 317414
209 | 3000 | Laying of 2nd cable in excavated trench | ElEC | Labour | SWR10988 | 204.1 | M | 612300
210 | 30 | S&E-Smart RFID marker | ElEC | Labour | SWR25089 | 2745 | EA | 82350
211 | 22 | UG Cables Joints 33 KV 3x400 Sqmm Cable Straight through joint 33kv 3x400 xlpe | ElEC | Labour | SWR10382 | 5700.78 | EA | 125417.16
212 | 1000 | Supply of 6" B class GI pipe | ElEC | Supply | SMR40081 | 1044 | M | 1044000
213 | 300 | Cost of Pipes and slabs-supply of 6" DWC pipe | ElEC | Supply | SMR11610 | 1012 | M | 303600
214 | 400 | Cost of Pipes and slabs-Suppy of Hume pipe 9" size | ElEC | Supply | SMR40001 | 125 | M | 50000
215 | 12 | Making of Outdoor/Indoor End Making 33 KV 3x400 Sqmm Cable Out Door/Indoor end termination TerminationOD/Idoor end termination 33kv 3x400 xlpe | ElEC | Labour | SWR10387 | 2764.76 | EA | 33177.12
216 | 60 | Excavation & laying of UG Cable (Double Run) Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-33 KV 3x400 Sqmm Cable | ElEC | Labour | SWR12004 | 323.85 | M | 19431
217 | 3000 | Hard Rock Cutting-11KV-Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours. | ElEC | Labour | SWR21903 | 30 | M | 90000
218 | 30 | Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters , CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | ElEC | Supply | SMR40085 | 484 | EA | 14520
219 | 3 | Erection of AB Switch and aligment complete Erection of 33 KV AB Switch including alignment and earthing | ElEC | Labour | SWR10392 | 4500 | EA | 13500
220 | 3 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | ElEC | Labour | SWR12331 | 146.63 | EA | 439.89
221 | 3 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Note:-The requirement of 2nd coat is to be justified by the concerned Divisional Engineer /Executive Engineer before execution of this work Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | ElEC | Labour | SWR10881 | 142 | EA | 426
222 | 12 | Fabrication of poles-Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | ElEC | Labour | SWR10642 | 512.55 | EA | 6150.6
223 | 18 | Painting of poles-Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | ElEC | Labour | SWR10640 | 1132 | EA | 20376
224 | 12 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M Ex of Hard pit w/o blast 0.75X0.9X1.95M | ElEC | Labour | SWR11040 | 990.68 | EA | 11888.16
225 | 3 | Assembly and erection of Structure as per specification which includes fixing of top channels and cross bracings, transport of all materials from road side to the location, earthing, back filling with earth ramming etc excluding pit excavation and concreting-33 KV DP Structure with 175x85/150x75mm RS joist | ElEC | Labour | SWR11276 | 5670 | SET | 17010
226 | 6 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-RS Joists 150x75/175 x 85 mm | ElEC | Labour | SWR10346 | 1934 | EA | 11604
227 | 155 | Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) Earthing for raisers of SS Flat 50x6 mm. | ElEC | Labour | SWR10919 | 41 | RMT | 6355
228 | 11.282 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ElEC | Labour | SWR10356 | 6579 | M3 | 74224.278
229 | 0.37 | Mass Concreting for pole-Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | ElEC | Labour | SWR11890 | 3893 | M3 | 1440.41
230 | 0.975 | Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to theRS-Joist poles excluding cost of Mild Steel and transportcharges to substation site, including erection. Fabrication of struc.with welding. | ElEC | Labour | SWR10869 | 3426 | TO | 3340.35
231 | 6 | Supply of earthing pipe with materials-Supply of CI eath pipe with 80mm dia,2.0 M Length | ElEC | Supply | SMR11483 | 2789 | EA | 16734
232 | 6 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | ElEC | Labour | SWR10357 | 1234.2 | EA | 7405.2
233 | 6 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINES-Providing of RCC collar | ElEC | Labour | SWR10359 | 386 | EA | 2316
234 | 3 | Painting of poles-Painting of feeder name on support including cost of paint | ElEC | Labour | SWR12101 | 53 | EA | 159
235 | 1 | survey line&cabl inc peg mark&tree clear | ElEC | Labour | SWR22092 | 765 | KM | 765
236 | 5 | S-M+3 Tower GALV | ElEC | supply | SMR11683 | 140674.3 | EA | 703371.5
237 | 5 | Supply of material for Extension of 3Mtrs for M+3 (Galvanized) S-Mat. for Extn of M+3 Tower by 3M GALV | ElEC | supply | SMR11684 | 28520.64 | EA | 142603.2
238 | 5 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-M-Type Tower (1.2M x 1.2M x 3.3M ) 4.752cum | ElEC | labour | SWR12090 | 3592.95 | EA | 17964.75
239 | 5 | Erect- M+3 Tower GALV | ElEC | labour | SWR11850 | 64576 | EA | 322880
240 | 5 | Erect-Extn of 3M for M+3 Tower GALV | ElEC | labour | SWR11851 | 5168.95 | EA | 25844.75
241 | 45 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M Ex of Hard pit w/o blast 0.75X0.9X1.95M | ElEC | Labour | SWR11040 | 990.68 | EA | 44580.6
242 | 187.5 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) (other than SS)-Earth work excavtion hard rock boulders | ElEC | labour | SWR10856 | 1318.35 | M3 | 247190.625
243 | 120 | Fabrication of materials including 2 coats of Red oxide painting-Back clamps with 75 x 8 mm MS Flat | ElEC | labour | SWR10319 | 31 | EA | 3720
244 | 96 | Fabrication of materials including 2 coats of Red oxide painting-Top insulator fittings with channel and flat | ElEC | labour | SWR10325 | 44 | EA | 4224
245 | 10 | Fabrication of materials including 2 coats of Red oxide painting-Strut clamps with 75 x 8 mm MS Flat | ElEC | labour | SWR11262 | 84 | EA | 840
246 | 90 | Painting of poles-Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | ElEC | Labour | SWR10640 | 1132 | EA | 101880
247 | 90 | Fabrication of poles-Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | ElEC | Labour | SWR10642 | 512.55 | EA | 46129.5
248 | 45 | Erection of OH Lines including AB Cable (33KV, 11KV, LT)-Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Box pole 9/10/11 Mtr | ElEC | Labour | SWR11266 | 2643.83 | EA | 118972.35
249 | 157.5 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ElEC | Labour | SWR10356 | 6579 | M3 | 1036192.5
250 | 10 | Excavation of pits in all soils except hard rock requiring blasting-Stud Poles 0.6 M x 0.9 M x 1.5 M | ElEC | Labour | SWR10106 | 645 | EA | 6450
251 | 10 | Erection of OH Lines including AB Cable (33KV, 11KV, LT) Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Erec of 9.1 Mts PSCC poles for stuts | ElEC | Labour | SWR11083 | 2400 | EA | 24000
252 | 14.1 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ElEC | Labour | SWR10356 | 6579 | M3 | 92763.9
253 | 8.1 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ElEC | Labour | SWR10356 | 6579 | M3 | 53289.9
254 | 3.72 | Mass Concreting for pole-Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | ElEC | Labour | SWR11890 | 3893 | M3 | 14481.96
255 | 6 | LOADING of Conductor drums | ElEC | Labour | SWR10191 | 202 | EA | 1212
256 | 3 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ElEC | Labour | SWR11861 | 3299.7 | EA | 9899.1
257 | 6 | UNLOADING of Conductor drums | ElEC | Labour | SWR10509 | 100 | EA | 600
258 | 6 | Paving out and stringing of conductor by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location-100 Sqmm Single Circuit (3 Conductors) | ElEC | labour | SWR10366 | 13856.7 | KM | 83140.2
259 | 24 | Formation of Cut points-Formation of Cut point for 33 KV Single Circuit line excluding pole erection and stays | ElEC | Labour | SWR10981 | 1791.12 | EA | 42986.88
260 | 120 | Painting of poles-Numbering of poles incl. cost of paint | ElEC | Labour | SWR10378 | 32 | EA | 3840
261 | 90 | Supply of earthing pipe with materials-Supply of GI wire No 8 | ElEC | suply | SMR11486 | 105 | KG | 9450
262 | 90 | Cost of Pipes and slabs-Supply of 2" B class GI pipe | ElEC | Supply | SMR40079 | 307 | M | 27630
263 | 90 | Supply of earthing pipe with materials S-GI Bolts & Nuts,Washers etc., | ElEC | Supply | SMR11488 | 117.5 | KG | 10575
264 | 75 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Spun poles 12.5 Mtrs / 12.9Mtrs PSCC | ElEC | labour | SWR10350 | 4521.66 | EA | 339124.5
265 | 10 | Supply of PSCC Pole 9.1Mtr 280KG | ElEC | supply | SMR25233 | 3109.41 | EA | 31094.1
266 | 3240 | Supply of Materials -- Supply of MS Channel 100X50mm | ElEC | Supply | SMR22745 | 57.45 | KGS | 186138
267 | 312 | S-MS Angle 65X65X6 | ElEC | Supply | SMR25207 | 57.25 | KG | 17862
268 | 1323 | S-PSCC Spun Pole 15Mtr 500Kg (Cement) | ElEC | Supply | SMR12321 | 56.42 | KG | 74643.66
269 | 12 | S-11KV 3x300 Heat Shble I/d End Term Kit | ElEC | supply | SMR22222 | 4554 | EA | 54648
270 | 22 | S-11KV 3x300 Heat Shble str thr JointKit | ElEC | supply | SMR22223 | 24151 | EA | 531322
271 | 3 | End Term KitS-11KV 3x300 Heat Shble O/d | ElEC | Supply | SMR12315 | 40658.78 | EA | 121976.34
272 | 4500 | Supply of Materials -- supply of RS Joist Poles (175X85mm) | ElEC | Supply | SMR12303 | 60.75 | KG | 273375
273 | 370 | Supply of Materials -- Supply of MS Flat 50x6 mm | ElEC | Supply | SMR12322 | 56.5 | KG | 20905
274 | 975 | Supply of Materials -- Supply of MS Channel 100X50mm | ElEC | Supply | SMR22745 | 57.45 | KGS | 56013.75
275 | 75 | S-PSCC Spun Pole 15Mtr 500Kg (Cement) | ElEC | Supply | SMR25239 | 42372.88 | EA | 3177966
276 | 22500 | S-11KV 3x300 Heat Shble I/d End Term Kit | ElEC | Supply | SMR12303 | 60.75 | KG | 1366875
277 | 1 | S-11KV 3x300 Heat Shble str thr JointKit | ElEC | Labour | SWR22092 | 765 | KM | 765
278 | 2 | End Term KitS-11KV 3x300 Heat Shble O/d | ElEC | Labour | SWR11230 | 1024 | DR | 2048
279 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ElEC | Labour | SWR11861 | 3299.7 | EA | 3299.7
280 | 2 | Unload-11/33KV XLPE UG Cable for all sizes | ElEC | Labour | SWR11231 | 1024 | DR | 2048
281 | 300 | Excavation & laying of UG Cable (Double Run)-Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road leveland cable separation with machine cut bricks horizontally for every 3 meters ,providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet,3feet depths and filling with sand 250mm above the cable and 50mm below thecable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of leadand lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts-In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil/CC-11 KV 3x300 Sqmm Cable | ElEC | labour | SWR11973 | 631.06 | M | 189318
282 | 300 | Laying of 2nd cable in excavated trench | ElEC | Labour | SWR10988 | 204.1 | M | 61230
283 | 3 | S&E-Smart RFID marker | ElEC | Labour | SWR25089 | 2745 | EA | 8235
284 | 2 | UG Cables Joints-Making of Straight through joints-11 KV 3x300 Sqmm Cable | ElEC | Labour | SWR10386 | 3725.45 | EA | 7450.9
285 | 100 | Cost of Pipes and slabs-Supply of 4" B class GI pip | ElEC | supply | SMR40080 | 740 | M | 74000
286 | 100 | Cost of Pipes and slabs-supply of 4" DWC pipe | ElEC | supply | SMR11609 | 759 | M | 75900
287 | 100 | Cost of Pipes and slabs-Suppy of Hume pipe 4" size | ElEC | supply | SMR40003 | 80 | M | 8000
288 | 8 | Making of Outdoor/Indoor End Termination-Making 11 KV 3x300 Sqmm Cable Out Door/Indoor end termination | ElEC | labour | SWR10391 | 2370.63 | EA | 18965.04
289 | 40 | Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-11 KV 3x300 Sqmm Cable | ElEC | labour | SWR12005 | 275.4 | M | 11016
290 | 300 | Hard Rock Cutting-11KV-Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours. | ElEC | Labour | SWR21903 | 30 | M | 9000
291 | 3 | Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters , CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | ElEC | Supply | SMR40085 | 484 | EA | 1452
292 | 12 | Fabrication of poles-Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | ElEC | Labour | SWR10642 | 512.55 | EA | 6150.6
293 | 12 | Painting of poles-Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | ElEC | Labour | SWR10640 | 1132 | EA | 13584
294 | 6 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M Ex of Hard pit w/o blast 0.75X0.9X1.95M | ElEC | Labour | SWR11040 | 990.68 | EA | 5944.08
295 | 6 | Erection of OH Lines including AB Cable (33KV, 11KV, LT)-Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Box pole 9/10/11 Mtr | ElEC | Labour | SWR11266 | 2643.83 | EA | 15862.98
296 | 160 | Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) Earthing for raisers of SS Flat 50x6 mm. | ElEC | Labour | SWR10919 | 41 | RMT | 6560
297 | 5.64 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ElEC | Labour | SWR10356 | 6579 | M3 | 37105.56
298 | 0.186 | Mass Concreting for pole-Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | ElEC | Labour | SWR11890 | 3893 | M3 | 724.098
299 | 0.31 | Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to theRS-Joist poles excluding cost of Mild Steel and transportcharges to substation site, including erection. Fabrication of struc.with welding. | ElEC | Labour | SWR10869 | 3426 | TO | 1062.06
300 | 12 | Supply of earthing pipe with materials-Supply of CI eath pipe with 80mm dia,2.0 M Length | ElEC | Supply | SMR11483 | 2789 | EA | 33468
301 | 12 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | ElEC | Labour | SWR10357 | 1234.2 | EA | 14810.4
302 | 12 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINES-Providing of RCC collar | ElEC | Labour | SWR10359 | 386 | EA | 4632
303 | 6 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | ElEC | Labour | SWR10393 | 3200 | EA | 19200
304 | 6 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | ElEC | Labour | SWR12331 | 146.63 | EA | 879.78
305 | 6 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Note:-The requirement of 2nd coat is to be justified by the concerned Divisional Engineer /Executive Engineer before execution of this work Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | ElEC | Labour | SWR10881 | 142 | EA | 852
306 | 6 | Painting of poles-Painting of feeder name on support including cost of paint | ElEC | Labour | SWR12101 | 53 | EA | 318
307 | 90 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M Ex of Hard pit w/o blast 0.75X0.9X1.95M | ElEC | Labour | SWR11040 | 990.68 | EA | 89161.2
308 | 90 | Erection of OH Lines including AB Cable (33KV, 11KV, LT) Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Errection of 11 M long PSCC pole | ElEC | Labour | SWR10978 | 4336.85 | EA | 390316.5
309 | 23.69 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ElEC | Labour | SWR10356 | 6579 | M3 | 155856.51
310 | 2.79 | Mass Concreting for pole-Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | ElEC | Labour | SWR11890 | 3893 | M3 | 10861.47
311 | 3.7 | Stringing of HT AB Cable with GI Metal Parts-HT AB Cable 11 KV 3x185+70 Sqmm | ElEC | labour | SWR10454 | 41876.1 | KM | 154941.57
312 | 84 | End Termination of AB cable (each lead):-Supply of 11KV 3x185+70sq.mm/ 3x70+70sq.mm/3x35+35sq.mm AB cable end Kits | ElEC | supply | SMR11504 | 950 | SET | 79800
313 | 84 | End Termination of AB cable (each lead)-120 Sqmm to 185 Sqmm | ElEC | labour | SWR10667 | 800 | EA | 67200
314 | 20 | Straight through joints of AB cable (each lead)-Supply and ere Angle line Asmbly kits | ElEC | labour | SWR10673 | 2124 | EA | 42480
315 | 90 | Straight through joints of AB cable (each lead)-Supply and ere Straight line Asmbly kits | ElEC | labour | SWR10672 | 1661 | EA | 149490
316 | 90 | Supply and Erection of I Hook and Suspension Hook-Erection of I hook | ElEC | labour | SWR12099 | 55 | EA | 4950
317 | 90 | Supply and Erection of I Hook and Suspension Hook-Erection of I hook | ElEC | supply | SMR12099 | 158 | EA | 14220
318 | 5 | T Branch Kit-Supply and erection of T-Branch kit | ElEC | labour | SWR24971 | 3215 | EA | 16075
319 | 100 | Supply of earthing pipe with materials S-GI Bolts & Nuts,Washers etc., | ElEC | Supply | SMR11488 | 117.5 | KG | 11750
320 | 8 | Formation of Cut point for 11 KV Single Circuit line excluding pole erection and stays Formatn of Horiz Cut point for 11KV line | ElEC | Labour | SWR10653 | 1435.81 | EA | 11486.48
321 | 5 | Earth-11KV 3x185+1x75 AB Cb-GIStrip&Pipe | ElEC | labour | SWR20612 | 500 | EA | 2500
322 | 8 | Loading of 11 KV AB Cable (XLPE) 3 Core upto 500 Mts. Drum (including Accessories ) | ElEC | labour | SWR12413 | 584 | DR | 4672
323 | 8 | Un loading of 11 KV AB Cable (XLPE) 3 Core upto 500 Mts. Drum (including Accessories ) | ElEC | labour | SWR12431 | 438 | DR | 3504
324 | 4 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ElEC | Labour | SWR11861 | 3299.7 | EA | 13198.8
325 | 90 | Supply of PSCC Pole 11Mtr 365KG | ElEC | supply | SMR25236 | 5399 | EA | 485910
326 | 6 | Supply of Materials -- Supply of 11 kV 400 A Double break AB switch | ElEC | Supply | SMR12317 | 18150 | EA | 108900
327 | 3000 | Supply of Materials -- supply of RS Joist Poles (175X85mm) | ElEC | Supply | SMR12303 | 60.75 | KG | 182250
328 | 384 | Supply of Materials -- Supply of MS Flat 50x6 mm | ElEC | Supply | SMR12322 | 56.5 | KG | 21696
329 | 150 | Supply of MS Angle 50x50x6 | ElEC | supply | SMR25206 | 58.15 | KG | 8722.5
330 | 160 | Supply of MS Channel 75x40 mm | ElEC | supply | SMR25205 | 58.45 | KG | 9352
331 | 4 | S-11KV 3x300 Heat Shble I/d End Term Kit | ElEC | supply | SMR25209 | 1459.83 | EA | 5839.32
332 | 2 | S-11KV 3x300 Heat Shble str thr JointKit | ElEC | supply | SMR25210 | 4110.17 | EA | 8220.34
333 | 4 | End Term KitS-11KV 3x300 Heat Shble O/d | ElEC | supply | SMR25208 | 1372.88 | EA | 5491.52
Electrical labour | [7 empty] | 24939480.456
Civil labour - WBS. No. S- 1802-13-07-01-01-001
Sl.No. | Estimate Quantity (only Figures) | Item Detailed Specification Description | Work Type eg. Earth Work, Electrical works. etc (upto 200 Characters) | Item Short Description (upto 100 Characters) | APSS / Morth Cl. Number (upto 200 Characters) | Rate (INR) (Upto 2 Decimals ) | UOM (upto 50 Characters) | Amount
1 | 32 | Leveliing the site by cutting and levelling with the help of JCB including cost,conveyance of all materials,hire chareges etc complete for finished item of work as directed by Engineer-in-charge. | Civil | Labour | SWR34179 | 2165 | Hrs | 69280
2 | 358.34 | Earth Work Mass Excavation (hard rock) to a depth as directed, in soils such as hard rock requiring blasting in prohibited area and all conditions such as dry, wet, slurry etc.and in dense or hard soils, disposal and depositing of excavated soil with intial lead of 10 mt and intial lift of 2m or as directed, including cost and conveyance of all materials, ramping and lifting of materials, and labour charges, hire charges of machinery, tools & plants, bailing of water ( either sub soil water, stoMts water, rain water, surface water or of any kind) if any at any stage of work until all works below ground level is finished to the satisfaction ,and from work such as shoring, timbering, strutting with required supports etc. for the work and removal of form work after completion of work etc all complete as directed by the engineer-incharge. | Civil | Labour | SWR33018 | 1440 | cum | 516009.6
3 | 295.2 | Earth work excavation in all type of ordinary soils red earth, Hard gravelly soils, earth mixed with sand and sandy soils etc., in all conditions such as slushy and dry with initial leads and lifts for foundations. Ordinary Soil | Civil | Labour | SWR33015 | 486 | cum | 143467.2
4 | 102.438 | PCC (1:4:8) using 40 mm metal with concrete Mixture. All work upto Plinth level including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete as directed by Engineer incharge of the work | Civil | Labour | SWR33028 | 4748 | cum | 486375.624
5 | 142.5 | Coursed Rubble stone CRS masonry 2nd sort with hard granite stones in cement mortar CM (1:6) for basement, including cost and conveyance of all materials, labour charges, curing, all leads and lifts, etc, complete for finished item of work. | Civil | Labour | SWR33041 | 4890 | cum | 696825
6 |  | RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge
7 | 1.09 | RCC M20 Grade Footing 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33098 | 9500 | cum | 10355
8 | 1.58 | RCC M20 Grade Column 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33100 | 13249 | cum | 20933.42
9 | 1.15 | RCC M20 Grade plinth beam 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33099 | 12371 | cum | 14226.65
10 | 0.458 | Reinforcement steel Supplying, Cutting, bending, binding, placing in position and tying reinforcement steel in all heights including cost and conveyance of steel and binding wire etc,. With all leads and lifts, labour charges, etc., complete for finished item of work. | Civil | Labour | SWR33144 | 70687 | MT | 32374.646
11 | 107.582 | Brick masonry in CM (1:6) for superstructure using well burnt country made second class bricks of approved quality including cost and conveyance of all materials curing, scaffolding with all leads and lifts in all heights etc., complete for finished item of work | Civil | Labour | SWR33068 | 8262 | cum | 888842.484
12 | 82.526 | PCC (1:2:4) using 20mm size well graded HBG metal for foundations, including cost, conveyance of all materials,labour all leads and lifts,consolidation and all operations, formwork as required, curing,etc. complete for finished item of work | Civil | Labour | SWR33030 | 6117 | cum | 504811.542
13 | 824.75 | Plastering with CM 2 coats, 20 mm thick, base coat in CM (1:6), 16 mm thick and top coat in CM (1:4), 4mm thick with Dubara sponze finishing including cost of all materials, seigniorage charges, excluding conveyance charges of materials and including all operational, incidental and labour charges for mixing mortar, laying rendering smooth and thread lining, curing, rounding off junctions of wall and slab etc., complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33163 | 561 | Sqm | 462684.75
14 | 824.75 | Painting with two coats of Plastic Emulsn paint over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33356 | 210 | Sqm | 173197.5
15 | 271.85 | Painting with two coats of Surya Cem paint over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33329 | 85 | sqm | 23107.25
16 | 650 | Supplying and fixing Structural Steel angles channal etc.Manufacturing, Supplying and fixing of MS grill for (Gate and raillings) of approved design as per drawings, including cost and conveyance of all materials, labour charges etc.,complete for finished item of work as directed by the Engineer- in-charge. | Civil | Labour | SWR33145 | 128 | Kgs | 83200
17 | 3 | Supply and Fixng of MS Name Board including cost & conveyance of all materials,labour charges etc complete for finished item of work. | Civil | Labour | SWR33421 | 4326 | sqm | 12978
18 | 1 | Geophysical Investgation charges for water point by Geologist | Civil | Labour | SWR33608 | 5000 | EA | 5000
19 |  | Drilling of 165mm bore well with machine rig including deployment and hire charges of rig and other machinery and equipment labour charges , measuring the yeild of borewell including cost and conveyance etc complete
20 | 90 | Drill-165mm Bore Well 0 to 90 | Civil | Labour | SWR33609 | 336 | M | 30240
21 | 30 | Drill-165mm Bore Well 90M to 120M | Civil | Labour | SWR34830 | 369 | M | 11070
22 | 30 | Drill-165mm Bore Well 120M to 150M | Civil | Labour | SWR34831 | 394 | M | 11820
23 | 30 | Drill-165mm Bore Well 150M to 180M | Civil | Labour | SWR34832 | 492 | M | 14760
24 | 30 | Drill-165mm Bore Well 180M to 210M | Civil | Labour | SWR34833 | 623 | M | 18690
25 | 30 | Drill-165mm Bore Well 210M to 240M | Civil | Labour | SWR34834 | 754 | M | 22620
26 | 30 | Drill-165mm Bore Well 240M to 270M | Civil | Labour | SWR34835 | 918 | M | 27540
27 | 150 | Drill-165mm Bore Well 270M and above | Civil | Labour | SWR34836 | 1082 | M | 162300
28 | 40 | Supply and fixing of 160mm dia PVC casing of A class 6Kg point pressure including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR33611 | 883 | M | 35320
29 | 1 | Supply and erecting, ISI mark submersible 5.0 HP, three Phase 30 stages pumpset suitable for 106/156mm dia borewell including cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33640 | 48007 | EA | 48007
30 | 370 | Supply and fixing of HDPE pipe 40mm dia of 16Kg/cm2 including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR34410 | 180 | M | 66600
31 | 1 | Supply and erecting D.O.L Starter 415V ,3 phase,50Hz with SS enclouserincluding cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33645 | 7854 | EA | 7854
32 | 450 | Supply of 3 Core 2.5 Sqmm Flat Copper cable of ISI for Submersible Motors of makes Finolex / Polycab / Gold Medal / Million / Payal / Sun Light / Power Flex / Fortune Art | Civil | Labour | SWR33641 | 192 | M | 86400
33 | 6 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-28.60mm OD Pipe - SDR 11 | Civil | Labour | SWR34363 | 410 | M | 2460
34 | 1 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type - 25mm NB Size | Civil | Labour | SWR34346 | 466 | EA | 466
35 | 72.73 | Earth work excavation in all type of ordinary soils red earth, Hard gravelly soils, earth mixed with sand and sandy soils etc., in all conditions such as slushy and dry with initial leads and lifts for foundations. | Civil | Labour | SWR33015 | 486 | Cum | 35346.78
36 | 39.53 | PCC (1:4:8) using 40mm HBG metal for foundations and leveling course, including cost and conveyance of all materials, labour all leads and lifts, consolidation and all operations, formwork as required, curing, etc. complete for finished item w | Civil | Labour | SWR33028 | 4748 | Cum | 187688.44
37 | 27.37 | CRS Coursed Rubble Stone masonry 2nd sort with hard granite stones in cement mortar (1:6) for basement, including cost and conveyance of all materials, labour charges, curing, all leads and lifts, etc, complete for finished item of work. | Civil | Labour | SWR33041 | 4890 | Cum | 133839.3
38 | 133.29 | Supplying and filling the substation site with borrowed gravel, watering, ramming, thoroughly complying with the standard specification. | Civil | Labour | SWR33052 | 339 | Cum | 45185.31
39 |  | 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge
40 | 5.346 | a) RCC M20 Grade Footings 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33098 | 9500 | Cum | 50787
41 | 3.42 | b)RCC M20 Grade Columns 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33100 | 13249 | Cum | 45311.58
42 | 4.03 | c)RCC M20 Grade Plinth Beams 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33099 | 12371 | Cum | 49855.13
43 | 3.55 | D) RCC M20 Grade Roof Beams 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33121 | 12287 | Cum | 43618.85
44 | 0.58 | e) RCC M20 Grade Lintels 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33107 | 13078 | Cum | 7585.24
45 | 2.7 | f) RCC M20 Grade Sunshades 600mm wide and 75mm thick 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33114 | 1376 | Sqm | 3715.2
46 | 19.206 | g) RCC M20 Grade Roof Slab 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33128 | 10875 | Cum | 208865.25
47 | 4.55 | reinforcement steel Supplying, Cutting, bending, binding, placing in position and tying reinforcement steel in all heights including cost and conveyance of steel and binding wire etc,. With all leads and lifts, labour charges, etc., complete for finished item of work. | Civil | Labour | SWR33144 | 70687 | MT | 321625.85
48 | 59.32 | Brick masonry in CM (1:6) for superstructure using well burnt country made second class bricks of approved quality including cost and conveyance of all materials curing, scaffolding with all leads and lifts in all heights etc., complete for fin | Civil | Labour | SWR33068 | 8262 | Cum | 490101.84
49 | 536.48 | Plastering with CM 2 coats, 20 mm thick, base coat in CM (1:6), 16 mm thick and top coat in CM (1:4), 4mm thick with Dubara sponze finishing including cost of all materials, seigniorage charges, excluding conveyance charges of materials and including all operational, incidental and labour charges for mixing mortar, laying rendering smooth and thread lining, curing, rounding off junctions of wall and slab etc., complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33163 | 561 | Sqm | 300965.28
50 | 85.68 | Providing Structural steel tube box type 60x40x4mm thick including cost and conveyance of all materials, labour charges,curing etc. complete for finished item of work and as directed by the engineer-in-charge. | Civil | Labour | SWR33146 | 147 | Kgs | 12594.96
51 | 18 | Providing Roofing with Trapezoidal/Galvalume Sheet including cost and conveyance of all materials, labour charges,curing etc. complete for finished item of work and as directed by the engineer-in-charge. | Civil | Labour | SWR33402 | 600 | Sqm | 10800
52 | 18.9 | Providing Design R.C.M. drop wall of 40mm thickness with cm 1:2 and 6mm dia MS bars at 150mm both ways and chicken mesh in two coats 20mm thick each plastering including cost and conveyance of all materials with leads and lifts, scaffolding and curing, labo | Civil | Labour | SWR33203 | 3070 | Sqm | 58023
53 | 12.24 | Supply and fixing of MS ornamental safety grill of approved design including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33310 | 2990 | sqm | 36597.6
54 | 5.91 | Supply and fixing of doors with the MT Wood frames the door shall be made well seasoned mt wood of cross section 100x75mm. The shutter shall be made isi mark flushed door with decolam sheets pasted on both sides with PVC beading 40mm width all round.Frame shall be painted with two coats of synthetic enamel paint of approved color over one coat of primer over luppum with spary with 3 no 150mm brass hinges 1 no brass door stoper, 1 no 250mm brass aldrops. 2 no 300 mm aluminium tower bolts, 2 no 150mm brass fancy door handlers, 1 no keyless lockset with cp handel. The quoted rate shall include cost and conveyance of the meterials, fixig, labour carges, tools, handles,locking arrangementts and other fixtures & fittings for finished item work as directed by the Engineer - in- charge. | Civil | Labour | SWR33264 | 7314 | Sqm | 43225.74
55 | 20.25 | Raised pointing to the exposed surfaces of CRS masonry in cm 1:3 prop. including cost and conveyance of all materials, labour charges, all leads and lifts curing etc, complete for finished item of work. | Civil | Labour | SWR33184 | 125 | sqm | 2531.25
56 | 8.64 | Supplying and fixing Aluminium sliding windows with grill and fixed glass panels using anodised aluminium extruded sections of mat finish for frames and mullions made from approved aluminium sections 62x32x1.2mm at 0.73kg/Rm providing 5mm plain glass fix | Civil | Labour | SWR33277 | 3623 | sqm | 31302.72
57 | 16.56 | Supply and laying of Ceramic floor over of CM 1:3 20 mm thick including required materials and labour charges etc complete for item of work | Civil | Labour | SWR33224 | 914 | Sqm | 15135.84
58 | 121.92 | Flooring with double machine polished and hand cut Tandur blue stone 20mm thick of approved colour, quality and of minimum of 300x300mm size over a bed of cement mortar 1:3 20mm thick including cost of all materials, with all leads and lifts jointing and | Civil | Labour | SWR33219 | 786 | Sqm | 95829.12
59 | 6.74 | Supply and fixing of 4" high skirting of shabad stone to the walls including cost and conveyance of all materials, labour etc for finished item of work. | Civil | Labour | SWR33236 | 876 | Sqm | 5904.24
60 | 243.69 | Painting with two coats of OBD over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials labour charges etc., complete for finished item of work. | Civil | Labour | SWR33333 | 146 | Sqm | 35578.74
61 | 414.315 | Painting with two coats of Plastic emulsn paint 2 coat of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33356 | 210 | Sqm | 87006.15
62 | 129.92 | Providing impervious coat over RCC roof slab to requried slopes with 20mm thick in CM 1:3 mixed with approved brand of water proffing compound inclding cost and conveyance of all materials, labour charges, curing, rounding off junctions of wall and slab, all leads and lifts, etc . complete for finished item of work as directed by the Engineer - in - charge. | Civil | Labour | SWR33156 | 584 | sqm | 75873.28
63 | 60 | Supply & fixing of 25mm dia 2mm thick surface P.V.C. pipe (ISI MARK) Concealed in wall with all required accessories including masonary work and labour charges etc.complete. | Civil | Labour | SWR33441 | 108 | M | 6480
64 | 1 | Supply & fixing TPNDB Distribution board with IP-42 protection (Metal Door)suitable for 3 phase ELCB/RCCB/FP Isolator as incomer and 10kA SP MCBs as out going including internal connection and labour charges for surface / flush mounting etc Complete. | Civil | Labour | SWR33526 | 11353 | EA | 11353
65 | 10 | Supply & fixing Flush type of 6A 3 pin wall plug socket with 6A switch control on a common switch board with earth continuity including wire leads,earth connection along with all labour charges etc., complete | Civil | Labour | SWR33468 | 166 | EA | 1660
66 | 6 | Supply & fixing Flush type of 16A 3 pin and 6A 3pin plug Flush type socket with indicator lamp and 16Amps fuse unit and 16Amps switch control (5 in one )duly recessed in wall with wooden deep box of 6'' x 8'' x 2 1/2'' size covered with hylam sheet earth connection and all labour charges etc., complete on wall. | Civil | Labour | SWR33470 | 449 | EA | 2694
67 | 24 | Supply and Fixing of modular switch, LP,FP,EFP,Wiring with 2 runs of 14/0.3mm (1.0 sq.mm)Fire Retardant (FR) P.V.C. insulated flexible copper cable (ISI MARK) in existing pipe with 6A Flush type Switch,ceiling rose and 3mm thick hylam sheet covering to switch control box including all labour charges etc., complete for light points, bell , fan and exhaust fan points in Non-Residential Buildings. | Civil | Labour | SWR33457 | 676 | EA | 16224
68 | 12 | Supply & Fixing of 28W T5 fluorescent tube. | Civil | Labour | SWR33558 | 148 | EA | 1776
69 | 1 | Supply of 12" (300mm)ISI, 900 RPM light duty exhaust fan with metallic blades with Mark of makes Crompton / Bajaj / Havells / Orient. | Civil | Labour | SWR33571 | 2192 | EA | 2192
70 | 180 | Supply and run of 2 of 22/0.3mm (1.5 sq.mm) (FR) P.V.C. insulated flexible copper cable in existing pipe for mains including all labour charges complete. | Civil | Labour | SWR33496 | 75 | M | 13500
71 | 180 | Supply and run of 2 of 36/0.3mm (2.5 sq.mm) FR P.V.C. insulated flexible copper cable in existing pipe for mains including all labour charges complete. | Civil | Labour | SWR33497 | 103 | M | 18540
72 | 12 | Supply & fixing of batten holder /slanting holder in lieu of ceiling rose of light point complete with all connection and all labour charges with 40W bulb (for new installation). | Civil | Labour | SWR33484 | 141 | EA | 1692
73 | 4 | Supply & fixing of 1200mm (48'') sweep 230v,A.C 50 Hz.Ceiling fan with 3 Blades and double ball bearings with all standared accessories. | Civil | Labour | SWR33563 | 2277 | EA | 9108
74 | 4 | Supply & fixing of Electronic Regulator for ceiling fans 900/1200/1400mm sweep including cost of material, Electrical charges complete for finished item of work | Civil | Labour | SWR33564 | 589 | EA | 2356
75 | 1 | Providing independent EARTHING by excavating a trench to a depth of 2.1M in all solid,as per size specified in the Data,using 40mm dia 'B' class GI pipe of 2.5 Mtrs length with necessary accessories with hume pipe ring duly providing staggered holes including filling with equal proportion of salt and Charcoal in layers and all labour charges etc., compiete for small quarters. | Civil | Labour | SWR33596 | 5345 | EA | 5345
76 | 35 | Supplying, laying, jointing and testing 101.6 mm SWG SP-1 pipes of ISI make conforming to ISI 651 & 4127 with airtight cement joints in CM 1.5:1 prop. Including excavation of trenches and socket pits in any soil (except rock requiring blasting) up to 1524 mm(5'0") depth and refilling with watering and tamping. | Civil | Labour | SWR34281 | 755 | M | 26425
77 | 3 | Constructing 904.0 mm (3#0#) dia brick masonry inspection chamber as per IS - 4111: Part-1:1986 with cement mortar (1:6) prop using 2nd Class Clay Bricks of 225 mm thick from approved source having a minimum crushing strength of 5 N/sq.mm including plastering with cement mortar 1:3 prop; ½# thick both inside and outside fitted with 20# dia RCC manhole covers and frames including excavating pits up to a depth of 904 mm (3'-0") in all sorts of soils (excluding rock) and laying cement concrete (1:4:8) 150 mm thick using 40 mm HBG Metal and P.C.C. 1:2:4 benching and channel 100 mm thick as per Standard specification and including cost and conveyance of all materials like cement, sand, bricks, water etc., to site, cost of seigniorage charges on all materials and all incidental and operational, labour charges like mixing cement mortar, constructing masonry, lift charges, curing etc., complete for finished item of work as per Standard specification. | Civil | Labour | SWR34296 | 8766 | EA | 26298
78 | 4 | Supply & fixing of 110 mm dia - Door Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34381 | 128 | EA | 512
79 | 4 | Supply & fixing of 110 mm dia - Plain Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34380 | 100 | EA | 400
80 | 12 | Supply & fixing of 110 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand | Civil | Labour | SWR34377 | 462 | M | 5544
81 | 18 | Supply & fixing of 90 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand | Civil | Labour | SWR34378 | 410 | M | 7380
82 | 3 | Supplying & fixing 150 mm x 100 mm SWG gully traps conforming to ISI 651 & 4127 with C.I Grating & Cost. Brick masonry in CM 1:6 prop. Intermediate chamber and fitted with 304.8 mm x 288.6mm (12"x9") C.I Frame and hinged cover | Civil | Labour | SWR34286 | 767 | EA | 2301
83 | 1 | Supplying and Fixing of European Water Closet of 1st Quality | Civil | Labour | SWR34314 | 2228 | EA | 2228
84 | 6 | Supply & fixing 15 mm angle stop cock Indian make 400 grams Seiko/ Senior/ Nice/ Senior/ Nice or equivalent | Civil | Labour | SWR34328 | 721 | EA | 4326
85 | 4 | S&F 15 mm N.P bib tap Indian make 400 grams full turn Seiko/ Senior/ Nice or equivalent | Civil | Labour | SWR34329 | 296 | EA | 1184
86 | 1 | Supplying & Fixing Indian make Flat Back Wash Hand Basin (HSW/Parryware/ Neycer) 1st quality conforming to IS:2556-Part-4:1972 with waste fittings like rubber plug, chain, 32 mm nominal size C.P. Fitting with parallel pipe thread conforming to IS:2963-1979 and fitted with 15 mm nominal bore Chromium Plated Pillar Tap of 1st quality Indian make 400 grams Seiko/ Senior/ Nice/ Esso or equivalent complete with standard CI brackets including wooden block: 550 x 400 mm - Single C.P. Pillar cock | Civil | Labour | SWR34316 | 1717 | EA | 1717
87 | 2 | Supply & fixing 38.1 mm C.P waste coupling Half or Full Thread 1st Quality Indian make Parryware or equivalent | Civil | Labour | SWR34428 | 309 | EA | 618
88 | 2 | Supply & fixing of 4" (101.6 mm ) Nahany Trap ( Without Jali with inlet)UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34387 | 134 | EA | 268
89 | 1000 | Providing & Placing on Terrace (at all floor levels) polyethylene water storage tank with Double layer approved brand & manufacture with cover and suitable locking arrangement & making necessary holes for inlet & outlets and over flow pipes but with NECESSARY fittings & base support for tanks | Civil | Labour | SWR34375 | 10 | L | 10000
90 | 2 | Supply & fixing 31.75 mm dia PVC flexible waste pipe of 914.4 mm length of Ist quality | Civil | Labour | SWR34426 | 33 | EA | 66
91 | 45 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)- 15.90mm OD Pipe - SDR 11 | Civil | Labour | SWR34361 | 239 | M | 10755
92 | 40 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-22.20mm OD Pipe - SDR 11 | Civil | Labour | SWR34362 | 313 | M | 12520
93 | 65 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-28.60mm OD Pipe - SDR 11 | Civil | Labour | SWR34363 | 410 | M | 26650
94 | 4 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type - 25mm NB Size | Civil | Labour | SWR34346 | 466 | EA | 1864
95 | 4 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type -20mm NB Size | Civil | Labour | SWR34345 | 331 | EA | 1324
96 | 1 | Supply & fixing 25.4 mm dia & 609.6 mm long aluminium anodized towel rod with brackets and aluminium screws | Civil | Labour | SWR34430 | 489 | EA | 489
97 | 85.51 | Earth work excavation in all type of Ordinary soils red earth, Hard gravelly soils, earth mixed with sand and sandy soils etc., in all conditions such as slushy and dry with initial leads and lifts for foundations. Ordinary Soil | Civil | Labour | SWR33015 | 486 | cum | 41557.86
98 | 18.91 | PCC (1:4:8) using 40mm HBG metal for foundations and leveling course, including cost and conveyance of all materials, labour all leads and lifts, consolidation and all operations, formwork as required, curing, etc. complete for finished item w | Civil | Labour | SWR33028 | 4748 | cum | 89784.68
99 | 91.8 | Coursed Rubble stone masonry (CRS) 2nd sort with hard granite stones in cement mortar (1:6) for basement, including cost and conveyance of all materials, labour charges, curing, all leads and lifts, etc, complete for finished item of work. | Civil | Labour | SWR33041 | 4890 | cum | 448902
100 | 36 | PCC (1:3:6) using 40mm HBG metal for foundations and leveling course, including cost and conveyance of all materials, labour all leads and lifts, consolidation and all operations, formwork as required, curing, etc. complete for finished item w | Civil | Labour | SWR33029 | 5038 | cum | 181368
101 | 108 | Raised pointing to the exposed surfaces of CRS masonry in cm 1:3 prop. including cost and conveyance of all materials, labour charges, all leads and lifts curing etc, complete for finished item of work. | Civil | Labour | SWR33184 | 125 | sq.mm | 13500
102 | 787.5 | Supplying and filling the substation site with borrowed gravel, watering, ramming, thoroughly complying with the standard specification. | Civil | Labour | SWR33052 | 339 | cum | 266962.5
103 | 88.8 | Plastering with CM 2 coats, 20 mm thick, base coat in CM (1:6), 16 mm thick and top coat in CM (1:4), 4mm thick with Dubara sponze finishing including cost of all materials, seigniorage charges, excluding conveyance charges of materials and including all operational, incidental and labour charges for mixing mortar, laying rendering smooth and thread lining, curing, rounding off junctions of wall and slab etc., complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33163 | 561 | sq.mm | 49816.8
104 | 200.85 | Painting with two coats of Surya Cem paint over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33329 | 85 | sq.mm | 17072.25
105 | 120 | Supply&Fabrication and fixing of Welded wire mesh ( 2" x 2") of 3mm dia. with ISMC (75x40x4.4mm) and Pheriperal frame of ISA(35x35x3mm) incldg cost& conveyance painting with synthetic enamil paint two coats over a coat of red oxide primer etc complete for finished item of work.. | Civil | Labour | SWR33403 | 2310 | sq.mm | 277200
106 | 160 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-22.20mm OD Pipe - SDR 11 | Civil | Labour | SWR34362 | 313 | M | 50080
107 | 30 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type - 25mm NB Size | Civil | Labour | SWR34346 | 466 | EA | 13980
108 | 1 | Providing Consultancy services for arranging contour surveying with total station incuding preparation of boundary and contour levels with 2 Nos. Hard copies and soft copies complete for finished items of work | Civil | Labour | SWR33427 | 5665 | EA | 5665
109 | 576.3905 | Seigniorage Charges - Sand | Civil | Labour | SWR34470 | 40 | cum | 23055.6204
110 | 1837.9351 | Seigniorage Charges - Metal | Civil | Labour | SWR34471 | 97.5 | cum | 179198.6683
111 | 920.79 | Seigniorage Charges - Gravel | Civil | Labour | SWR34472 | 30 | cum | 27623.7
112 | 60 | Supply and fixing of RCC fencing poles of size 0.1mx0.1mx1.8m (security fencing of sub station), including cost and conveyance of all labour, materials,and hire chareges etc complete for finished item of work. | Civil | Labour | Swr33405 | 1444 | EA | 86640
113 | 1200 | Supply and fixing of galvanised barded wire (1 horizantal & 2 cross strands. including cost and conveyance of all labour, materials,and hire chareges etc complete for finished item of work. | Civil | Labour | Swr33408 | 16 | M | 19200
[5 empty] | Total Rs. |  |  | 9152105.4348
[5 empty] | 18% GST Rs. |  |  | 34091585.8907

## 14. Badangpet
Name of the work: Erection of 33/11kV outdoor SS at Badangpet in Balapur( M) with 2x8 MVA PTRS and connected 33kV and 11kV Lines with 6 Nos. 11 kV feeders at Badangpet Dumping Yard in Balapur (M) in ECGH Division/Masterplan/RR Circle
WBS No. S-1803-13-03-01-01-001
Sl No | Estimate Quantity | Description of item | Work Type | Item Short Description | APSS / Month Cl.NumberSSR 11 & 12 | Rate (INR) | UOM | AMOUNT
1 | 16 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | ELECT | Labour | SWR11039 | 928 | EA | 14848
2 | 5.76 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ELECT | Labour | SWR10868 | 6852 | TO | 39467.52
3 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELECT | supply | SMR40009 | 2181 | TO | 12562.56
4 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELECT | labour | SWR10877 | 851 | TO | 4901.76
5 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELECT | supply | SMR40010 | 1293 | TO | 7447.68
6 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELECT | labour | SWR10879 | 482 | TO | 2776.32
7 | 5.76 | Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ELECT | labour | SWR10867 | 1470 | TO | 8467.2
8 | 17.758 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELECT | labour | SWR10356 | 6579 | M3 | 116829.882
9 | 9.24 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ELECT | labour | SWR10862 | 373 | M2 | 3446.52
10 | 16 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | ELECT | labour | SWR11089 | 48 | EA | 768
11 | 4 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-8.0Mtrs PSCC Poles 0.76 M x 0.76M x 1.52M (2.6" x 2.6" x 5.0') 0.88 cum | ELECT | labour | SWR11037 | 793 | EA | 3172
12 | 1 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ELECT | Labour | SWR10868 | 6852 | TO | 6852
13 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELECT | supply | SMR40009 | 2181 | TO | 2181
14 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELECT | labour | SWR10877 | 851 | TO | 851
15 | 1 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELECT | supply | SMR40010 | 1293 | TO | 1293
16 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELECT | labour | SWR10879 | 482 | TO | 482
17 | 1 | Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ELECT | labour | SWR10867 | 1470 | TO | 1470
18 | 4 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Box pole 12 Mtr | ELECT | labour | SWR11267 | 3901.37 | EA | 15605.48
19 | 2.65 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELECT | labour | SWR10356 | 6579 | M3 | 17434.35
20 | 2.31 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ELECT | labour | SWR10862 | 373 | M2 | 861.63
21 | 4 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | ELECT | labour | SWR11089 | 48 | EA | 192
22 | 5.063 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ELECT | Labour | SWR10868 | 6852 | TO | 34691.676
23 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELECT | supply | SMR40009 | 2181 | TO | 11042.403
24 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELECT | labour | SWR10877 | 851 | TO | 4308.613
25 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELECT | supply | SMR40010 | 1293 | TO | 6546.459
26 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELECT | labour | SWR10879 | 482 | TO | 2440.366
27 | 5.063 | Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ELECT | labour | SWR10867 | 1470 | TO | 7442.61
28 | 13 | Erection of AB Switch and aligment complete Erection of 33 KV AB Switch including alignment and earthing | ELECT | labour | SWR10392 | 4500 | EA | 58500
29 | 34 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Note:-The requirement of 2nd coat is to be justified by the concerned Divisional Engineer /Executive Engineer before execution of this work Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | ELECT | labour | SWR10881 | 142 | EA | 4828
30 | 34 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | ELECT | labour | SWR12331 | 146.63 | EA | 4985.42
31 | 6 | Loading of 33 KV CTs/ PTs | ELECT | labour | SWR10200 | 165 | EA | 990
32 | 6 | Un loading of 33 KV CTs/ PTs | ELECT | labour | SWR10518 | 128 | EA | 768
33 | 2 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33kv single phase PT s | ELECT | labour | SWR10401 | 1079 | SET | 2158
34 | 12 | Loading of 33 KV, 10 KA LAs Station typ | ELECT | labour | SWR10266 | 41 | EA | 492
35 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELECT | labour | SWR11861 | 3299.7 | EA | 3299.7
36 | 12 | Un loading of 33 KV, 10 KA LAs Station type | ELECT | labour | SWR10584 | 35 | EA | 420
37 | 4 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33 KV LAS station/Line type including earthing | ELECT | labour | SWR10396 | 880 | SET | 3520
38 | 2 | Loading of 33 KV VCBs along with Panel boards | ELECT | labour | SWR10198 | 1024 | EA | 2048
39 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELECT | labour | SWR11861 | 3299.7 | EA | 3299.7
40 | 2 | Un loading of 33 KV VCBs along with Panel boards | ELECT | labour | SWR10516 | 1044.48 | EA | 2088.96
41 | 12.584 | Excavate-Pit for 33KV VCB | ELECT | labour | SWR23224 | 331 | M3 | 4165.304
42 | 14.52 | Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x 1.8 x 0.75 cum for VCB Plinth | ELECT | labour | SWR20685 | 5160 | M3 | 74923.2
43 | 2 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33 KV VCB with Control Panel | ELECT | labour | SWR10460 | 12500 | EA | 25000
44 | 2 | Loading and unloading of PTR on constructed plinth-Loading of 8MVA PTR | ELECT | labour | SWR10613 | 5805.84 | EA | 11611.68
45 | 2 | Transport of Power transformers (0 to 100 KM) from one place to another place in GHMC Area.(excluding of loading & unloading )-8MVA power transformer | ELECT | labour | SWR10854 | 21945 | EA | 43890
46 | 2 | Loading and unloading of PTR on constructed plinth-Unloading of 8MVA PTR | ELECT | labour | SWR10627 | 5805.84 | EA | 11611.68
47 | 700 | S/o rail poles 90/105lb (250x2N) | ELECT | supply | SMR22718 | 47.27 | KG | 33089
48 | 14 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Rail pole 90 lbs | ELECT | labour | SWR10344 | 3510 | EA | 49140
49 | 2 | Erection of PTR on constructed plinth-Erection of 8 MVA PTR. | ELECT | labour | SWR21321 | 49480.2 | EA | 98960.4
50 | 0.436 | Extention of 33KV Bay at 132/33KV Sub-station-Zebra condutor | ELECT | supply | SMR24910 | 299369 | KM | 130524.884
51 | 30 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing | ELECT | supply | SMR11915 | 2055 | SET | 61650
52 | 30 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of I-Bolts | ELECT | supply | SMR22473 | 294 | EA | 8820
53 | 45 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 "to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating . Sup T clamp LM6 Al alloy of 12 mm, 800 A | ELECT | supply | SMR40011 | 299 | EA | 13455
54 | 6 | Bus stringing Hoisting of Insulators and hardware, stretching the conductor and stringing of 33 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bussection of 4.5mt) Hoisting post ins&hrd wr 1panther 33kv | ELECT | labour | SWR21240 | 781 | EA | 4686
55 | 84 | Stringing of bus with panther conductor including jumpering etc., complete to all the equipment in SS fixing to all clamps and equipment.(3 Conductors) | ELECT | labour | SWR10404 | 327.68 | M | 27525.12
56 | 30 | Bus stringing Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | ELECT | labour | SWR10884 | 224 | EA | 6720
57 | 75 | Labour for Fixing of all types of clamps | ELECT | labour | SWR10917 | 65 | EA | 4875
58 | 25 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | ELECT | Labour | SWR11039 | 928 | EA | 23200
59 | 8.68 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ELECT | Labour | SWR10868 | 6852 | TO | 59475.36
60 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELECT | supply | SMR40009 | 2181 | TO | 18931.08
61 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELECT | labour | SWR10877 | 851 | TO | 7386.68
62 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELECT | supply | SMR40010 | 1293 | TO | 11223.24
63 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELECT | labour | SWR10879 | 482 | TO | 4183.76
64 | 8.68 | Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ELECT | labour | SWR10867 | 1470 | TO | 12759.6
65 | 25 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-R.S. Joists 150 x 150 mm | ELECT | labour | SWR10348 | 1952.61 | EA | 48815.25
66 | 27.75 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELECT | labour | SWR10356 | 6579 | M3 | 182567.25
67 | 17.91 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ELECT | labour | SWR10862 | 373 | M2 | 6680.43
68 | 25 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | ELECT | labour | SWR11089 | 48 | EA | 1200
69 | 4.642 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ELECT | Labour | SWR10868 | 6852 | TO | 31806.984
70 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELECT | supply | SMR40009 | 2181 | TO | 10124.202
71 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELECT | labour | SWR10877 | 851 | TO | 3950.342
72 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELECT | supply | SMR40010 | 1293 | TO | 6002.106
73 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELECT | labour | SWR10879 | 482 | TO | 2237.444
74 | 4.642 | Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ELECT | labour | SWR10867 | 1470 | TO | 6823.74
75 | 17 | Erection of AB Switch and aligment complete-Erection of 11KV 800A double throw AB Switches | ELECT | labour | SWR21277 | 3500 | EA | 59500
76 | 3 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | ELECT | labour | SWR10393 | 3200 | EA | 9600
77 | 2 | Loading of 11 KV CT - PT Sets | ELECT | labour | SWR10201 | 190 | EA | 380
78 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELECT | labour | SWR11861 | 3299.7 | EA | 3299.7
79 | 2 | Un loading of 11 KV CT - PT Sets | ELECT | labour | SWR10519 | 101 | EA | 202
80 | 2 | Erection of 11 KV three phase PTs | ELECT | labour | SWR10402 | 800 | SET | 1600
81 | 24 | Loading of 11 KV, 10 KA LAs Station type | ELECT | labour | SWR10264 | 32 | EA | 768
82 | 2 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELECT | labour | SWR11861 | 3299.7 | EA | 6599.4
83 | 24 | Un loading of 11 KV, 10 KA LAs Station type | ELECT | labour | SWR10582 | 32 | EA | 768
84 | 2 | Erection of 11 KV LAS station type including earthing | ELECT | labour | SWR10397 | 559 | SET | 1118
85 | 6 | Erection of 11 KV LAS line type including earthing | ELECT | labour | SWR10398 | 505 | SET | 3030
86 | 8 | Loading of 11 KV VCBs along with Panel boards | ELECT | labour | SWR10199 | 1024 | EA | 8192
87 | 4 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELECT | labour | SWR11861 | 3299.7 | EA | 13198.8
88 | 8 | Un Loading of 11 KV VCBs along with Panel boards | ELECT | labour | SWR10517 | 1044.48 | EA | 8355.84
89 | 41.6 | Excavate-Pit for 33KV VCB | ELECT | labour | SWR23224 | 331 | M3 | 13769.6
90 | 48 | Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x 1.8 x 0.75 cum for VCB Plinth | ELECT | labour | SWR20685 | 5160 | M3 | 247680
91 | 8 | Erection of 11 KV VCB with Control Panel | ELECT | labour | SWR10461 | 12000 | EA | 96000
92 | 12 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing | ELECT | supply | SMR11915 | 2055 | SET | 24660
93 | 12 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of I-Bolts | ELECT | supply | SMR22473 | 294 | EA | 3528
94 | 45 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 "to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating . Sup T clamp LM6 Al alloy of 12 mm, 800 A | ELECT | supply | SMR40011 | 299 | EA | 13455
95 | 2 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 11 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 3.5mt) Hoisting post ins&hrd wr 1panther 11kv | ELECT | labour | SWR21241 | 507 | EA | 1014
96 | 63 | Stringing of bus with panther conductor including jumpering etc., complete to all the equipment in SS fixing to all clamps and equipment.(3 Conductors) | ELECT | labour | SWR10404 | 327.68 | M | 20643.84
97 | 45 | Bus stringing Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | ELECT | labour | SWR10884 | 224 | EA | 10080
98 | 57 | Labour for Fixing of all types of clamps | ELECT | labour | SWR10917 | 65 | EA | 3705
99 | 584 | Laying of earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication 75x 8mm MS Flat / GI Flat. Laying of earth mat,excavation 75x 8mm | ELECT | labour | SWR10920 | 65 | RMT | 37960
100 | 1010 | Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) Earthing for raisers of SS Flat 50x6 mm. | ELECT | labour | SWR10919 | 41 | RMT | 41410
101 | 36 | Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | ELECT | supply | SMR11482 | 3486 | EA | 125496
102 | 36 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | ELECT | labour | SWR10357 | 1234.2 | EA | 44431.2
103 | 36 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINES-Providing of RCC collar | ELECT | labour | SWR10359 | 386 | EA | 13896
104 | 2 | Supply of Copper Flexible jumper with 75 X 8 of length 250 mm at neutral of Power tranformer end and 50 X 6 of length 50mm two Nos at double neutral end duly brasing with flexible jumper of capacity of 5kA/3 sec for power transformer neutral. SupCU Flexi jumper for Power T/F Neutral | ELECT | supply | SMR40033 | 4725 | EA | 9450
105 | 2 | Providing of earthing with various types of earth electrodes-Providing of double earthing for neutral with flexible copper jumpers including arrangement by fixing M.S.Channel 100x50mm. | ELECT | labour | SWR11892 | 1323 | EA | 2646
106 | 4 | Loading of LT AB Cable 3X16+25 Sqmm | ELECT | labour | SWR11702 | 200 | DR | 800
107 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELECT | labour | SWR11861 | 3299.7 | EA | 3299.7
108 | 4 | Un loading of LT AB Cable 3X16+25 Sqmm | ELECT | labour | SWR11713 | 204 | DR | 816
109 | 80 | Providing of control cable trench as per DATA-XII | ELECT | labour | SWR22093 | 3148 | RMT | 251840
110 | 3074 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends . Lay-4C/10C 2.5Sqmm Control Cable | ELECT | labour | SWR11879 | 27 | M | 82998
111 | 270 | Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per specification (including cost of ferrules, lugs and glands) | ELECT | labour | SWR12510 | 27 | EA | 7290
112 | 4 | Marshalling Box Supply of FRP PT Marshalling Box | ELECT | supply | SMR40048 | 4463 | EA | 17852
113 | 4 | Marshalling Box Erection of Marshalling boxes | ELECT | labour | SWR10940 | 374.85 | EA | 1499.4
114 | 1 | Loading of 220 V Batterry with charger | ELECT | labour | SWR11166 | 1612 | SET | 1612
115 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELECT | labour | SWR11861 | 3299.7 | EA | 3299.7
116 | 1 | Un loading of 220 V Batterry with charger | ELECT | labour | SWR11147 | 1024 | SET | 1024
117 | 1 | Batteries-Erection of 220 V, 200 AH battery in complete shape fit for | ELECT | labour | SWR12350 | 7666 | EA | 7666
118 | 1 | Supply of DC Annunciation & relay panel for 10 feeder panel including the cost of LED Indiacation lamps, VAA auxilairy relays, Electronic Hooters complete as per specification. | ELECT | supply | SMR40044 | 42500 | EA | 42500
119 | 1 | Supply of AC Supply panel inluding providing of changeover switch, SFU, metering unit, 32 A three phase MCB, 16 A Single phase MCB complete as per specification. Supply of AC Supply panel complete | ELECT | supply | SMR40045 | 42000 | EA | 42000
120 | 2 | Fixing of AC/DC Panel and giving Connections to the protection equipment and Metering circuits as per the specification and standards. The 3 1/2 core 25 Sqmm power cable required from distribution box to AC/DC panel in the control room is also to be supply | ELECT | labour | SWR20025 | 7871.85 | SET | 15743.7
121 | 8 | Yard lightning-Supply of stepped tubular poles single way made of steel of length 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9 mm, 2.1 mtrs with outer dia 76.1 mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79 kgf as per IS 2713 | ELECT | Supply | SMR40051 | 13913 | EA | 111304
122 | 8 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE/CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA /OSRAM /SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty S-90W LED fixture set | ELECT | suppply | SMR11594 | 8200 | EA | 65600
123 | 8 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | ELECT | Labour | SWR11039 | 928 | EA | 7424
124 | 8 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE / CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA/OSRAM/SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty-Erection of tubular poles | ELECT | labour | SWR10955 | 1379 | EA | 11032
125 | 5.27 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELECT | labour | SWR10356 | 6579 | M3 | 34671.33
126 | 8 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE/CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA /OSRAM /SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty. Fixing of Metal halide lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5 GI pipe complete Fixing of LED/Metal halide complete. | ELECT | labour | SWR10956 | 1268 | EA | 10144
127 | 45 | Supply of HBG metal-Supply & spreading of 20mm machine crushed metal (HBG) including cost of conveneyance of all materials, labour charges etc complete for finished item of work and directed by the engineer incharge | ELECT | labour | SWR10860 | 2113 | M3 | 95085
128 | 2 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M Ex of Hard pit w/o blast 0.75X0.9X1.95M | ELECT | labour | SWR11040 | 990.68 | EA | 1981.36
129 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELECT | supply | SMR40009 | 2181 | TO | 1635.75
130 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELECT | labour | SWR10877 | 851 | TO | 638.25
131 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELECT | supply | SMR40010 | 1293 | TO | 969.75
132 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELECT | labour | SWR10879 | 482 | TO | 361.5
133 | 1 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Box pole 12 Mtr | ELECT | labour | SWR11267 | 3901.37 | EA | 3901.37
134 | 2.22 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELECT | labour | SWR10356 | 6579 | M3 | 14605.38
135 | 1.16 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ELECT | labour | SWR10862 | 373 | M2 | 432.68
136 | 2 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints | ELECT | labour | SWR11089 | 48 | EA | 96
137 | 1 | Construction of DTR Plinth-RCC Column type DTR Plinth of size 1'X1'X10',topslab 4'x4'x6" & beam size 4'X8'X8" upto 160KVA | ELECT | labour | SWR21843 | 25967.57 | EA | 25967.57
138 | 1 | Loading of 50,63, 75 & 100 KVA DTR | ELECT | labour | SWR10195 | 350 | EA | 350
139 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELECT | labour | SWR11861 | 3299.7 | EA | 3299.7
140 | 1 | Un loading of 50,63, 75 & 100 KVA DTR | ELECT | labour | SWR10513 | 280 | EA | 280
141 | 1 | Erection of DTR's including loading and Unloading DTR on the Structure/Plinth etc-Erection of 3 Phase DTRs 63,75 & 100 KVA | ELECT | labour | SWR20905 | 1650 | EA | 1650
142 | 1 | Erection of AB Switch and aligment complete Erection of 11KV 200A TT type AB Switch including fixing of cross angles and alignment complete | ELECT | labour | SWR20102 | 1813.49 | EA | 1813.49
143 | 1 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erect. of 11kv HG Fuseset incl earthing | ELECT | labour | SWR10395 | 740.52 | SET | 740.52
144 | 40 | Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.-In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road-11KV 3x185 Sqmm Cable | ELECT | labour | SWR11920 | 465.46 | M | 18618.4
145 | 20 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-11 KV 3x185 Sqmm Cable | ELECT | labour | SWR11956 | 126.23 | M | 2524.6
146 | 2 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-11 KV 3x185 Sqmm Cable | ELECT | labour | SWR10390 | 2370.63 | EA | 4741.26
147 | 1 | UG Cables Joints Making of Outdoor/Indoor End Termination OD/Idoor end termination 11kv 3x185 xlpe | ELECT | labour | SWR10674 | 1594.67 | EA | 1594.67
148 | 85 | Erection of LT distribution box including laying of LT cable from distribution box to LT OH line and DTR to distribution box including earthing of distribution box and crimping of lugs connecting of jumpers etc | ELECT | labour | SWR11923 | 377.63 | M | 32098.55
149 | 15 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-LT 3 1/2 x 185 Sqmm Cable | ELECT | labour | SWR11959 | 85.43 | M | 1281.45
150 | 2 | Making of Outdoor/Indoor End Termination-Supply of 31/2x185Sqmm UG O/D end termination kits | ELECT | supply | SMR40140 | 550 | EA | 1100
151 | 2 | Supply & fixing of Oout Door/Indoor end termination LT 3 1/2 x 185 Sqmm Cable | ELECT | labour | SWR10765 | 968.9 | EA | 1937.8
152 | 1 | Supply and fixing of Substation board of size 3'x2.5' indicating the layout of switchyard Sup &fix of board ind Switchyard layout | ELECT | labour | SWR20032 | 1654 | EA | 1654
153 | 1 | Supply and fixing of safety instructions/Substation operation instruction board. Sup& fix safety inst/SS Op. inst board | ELECT | labour | SWR22090 | 2205 | EA | 2205
154 | 750 | Control Panels Supplying & fabrication erection of 6mm Checkerd plates as per the field conditions Supply,fabricati of 6mm Checkerd plates | ELECT | labour | SWR10873 | 83 | KG | 62250
155 | 1 | T & P Supply of Wall clock standard make | ELECT | supply | SMR40059 | 578 | EA | 578
156 | 1 | S-10ft Aluminium Ladder | ELECT | supply | SMR12378 | 1654 | EA | 1654
157 | 1 | Sup Alluminium Ladder for indoor works | ELECT | supply | SMR40062 | 4410 | EA | 4410
158 | 30 | T & P Painting of Name Plates for any equipmen | ELECT | labour | SWR10963 | 122 | EA | 3660
159 | 1 | T & P Supply of Taparia Tool kit of Size 20”x10”x15” with tier arrangements Tool box with locking arrangement & key containing (1) Double Ended fix Spanner sets, (Ribbed) 6 x 7, 8 x 9, 10 x 11, 12 x 13, 14 x 15, 16 x 17, 18 x19, 20 x 22, 21 x 23, 24 x 27, 25 x28, 30 x 32, (2) Double Ended Ring Spanners sets, 6 x 7 , 8 x 9, 10 x 11, 12 x 13, 14 x 15. 16 x 17 , 18 x 19, 20 x 22 , 21 x 23, 24 x 27, 25 x28, 30 x 32 mm, (3) Adjustable Spanner 305 mm length least maximum opening 35mm chrome, (4) Pipe Wrench Length 350 mm 14”, (5) Soft faced Hammer with suitable handle 2 lb, (6) Hacksaw frame with metal handle heavy duty for 12" hacksaw blade with High Speed blade, (7) Insulated Screw drivers Transparent Green Handle Set Length 6”, 8” & 12”, (8) Star Screw Driver Transparent Green Handle Length 6”, (9) Insulated Wire Cutter, (10) Insulated Cutting Plier Length 8” with cable stripper insulated with thick C. A. sleeve confirming to IS: 4378 - 1990, (11) Long Nose Plier insulated with thick C.A. sleeve generally confirming to IS:3552-1989, (12) Tester type screw driver (special with neon bulb) generally confirm to IS: 5579- 1985 Grade:II handle yellow/ green colour overall length 130 mm, (13) Insulated Crimping Plier of all Taparia make. SupTaparia Tool kit complete as per Spec | ELECT | supply | SMR40063 | 4925 | SET | 4925
160 | 1 | T & P Sup Rechargeable LED torch light of Standard make | ELECT | supply | SMR40064 | 1733 | EA | 1733
161 | 1 | T & P-Steel almarah(61/2 X 3ft) Godrej | ELECT | supply | SMR40061 | 9818 | EA | 9818
162 | 1 | T & P-Table (3x6ft) Godrej | ELECT | supply | SMR40057 | 6050 | EA | 6050
163 | 4 | T & P-S type chairs (Godrej) | ELECT | supply | SMR40058 | 924 | EA | 3696
164 | 1 | T & P Sup Angle racks(18x36.6inches) Godrej | ELECT | supply | SMR40060 | 1733 | EA | 1733
165 | 1 | T & P Supply of Hack saw (12 inches) | ELECT | supply | SMR40065 | 289 | EA | 289
166 | 4 | Sup Earth Rods (8ft) Screw & clamp type | ELECT | supply | SMR40066 | 578 | EA | 2312
167 | 2 | Supply of Hand Gloves | ELECT | supply | SMR40067 | 289 | SET | 578
168 | 12 | SupRubber mats( 6'x3')size fo indoorSS | ELECT | supply | SMR40068 | 1386 | EA | 16632
169 | 1 | Biometric Time attendence System & Telecom Sup Stand basic cell phone with charger | ELECT | supply | SMR40069 | 1386 | EA | 1386
170 | 14 | Supply of Danger boards with clamps | ELECT | supply | SMR40070 | 116 | EA | 1624
171 | 2 | Fire bucket stand with 3 buckets (8 -10 ltr capacity) | ELECT | supply | SMR40088 | 1386 | SET | 2772
172 | 2 | Room fire extinguisher (2 ltrs capacity) for control room | ELECT | supply | SMR40089 | 4620 | EA | 9240
173 | 4 | Sup TrollyMounted Co2 (6.5Kgs) Cylinders(IS-2878) | ELECT | supply | SMR40087 | 9240 | EA | 36960
174 | 6 | Supply of Safety Helmet of standard make | ELECT | supply | SMR40071 | 231 | EA | 1386
175 | 8 | Supply of LC Boards | ELECT | supply | SMR40072 | 116 | EA | 928
176 | 4 | Supply of Gum Boots(Pair) | ELECT | supply | SMR40073 | 693 | EA | 2772
177 | 1 | Supply of 5000v megger | ELECT | supply | SMR40074 | 13860 | EA | 13860
178 | 1 | Supply of Earth megger (1000v) | ELECT | supply | SMR40075 | 8085 | EA | 8085
179 | 1 | Supply of Digital clamp meter. | ELECT | supply | SMR40076 | 2888 | EA | 2888
180 | 1 | Name board of the 33/11kV Sub-Station(As per Standard Specification) Sup 33/11kv S.S Permanent name board | ELECT | supply | SMR40086 | 10238 | EA | 10238
181 | 800 | Supply of Hot dip galvanized/zinc coated bolts & nuts including spring washers, pack washers and flat washers etc. | ELECT | supply | SMR12488 | 90 | KG | 72000
182 | 2 | Fabrication of poles-Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | ELECT | labour | SWR10642 | 512.55 | EA | 1025.1
183 | 1 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-RS Joists 150x75/175 x 85 mm | ELECT | labour | SWR10346 | 1934 | EA | 1934
184 | 5760 | Supply of Materials -- Supply of RS Joist girder Poles (150X150mm) | ELECT | Supply | SMR12302 | 59.25 | KG | 341280
185 | 1000 | Supply of Materials -- supply of RS Joist Poles (175X85mm) | ELECT | Supply | SMR12303 | 60.75 | KG | 60750
186 | 5063 | Supply of Materials -- Supply of MS Channel 100X50mm | ELECT | Supply | SMR22745 | 57.45 | KGS | 290869.35
187 | 13 | Supply of Materials -- Supply of 33 kV 800 A Double break AB switch | ELECT | Supply | SMR12315 | 40658.78 | EA | 528564.14
188 | 8680 | Supply of Materials -- Supply of RS Joist girder Poles (150X150mm) | ELECT | Supply | SMR12302 | 59.25 | KG | 514290
189 | 4642 | Supply of Materials -- Supply of MS Channel 100X50mm | ELECT | Supply | SMR22745 | 57.45 | KGS | 266682.9
190 | 17 | Supply of Materials -- Supply of 11 kV 800 A Double break AB switch | ELECT | Supply | SMR12316 | 30847.46 | EA | 524406.82
191 | 3 | Supply of Materials -- Supply of 11 kV 400 A Double break AB switch | ELECT | Supply | SMR12317 | 18150 | EA | 54450
192 | 3045 | Supply of Materials -- Supply of MS Flat 75x8 mm | ELECT | Supply | SMR12321 | 56.42 | KG | 171798.9
193 | 2666 | Supply of Materials -- Supply of MS Flat 50x6 mm | ELECT | Supply | SMR12322 | 56.5 | KG | 150629
194 | 750 | Supply of Materials -- supply of RS Joist Poles (175X85mm) | ELECT | Supply | SMR12303 | 60.75 | KG | 45562.5
195 | 1 | Supply of Materials -- Supply of 11 kV 200 A Tilting type AB switch | ELECT | Supply | SMR12318 | 8991 | EA | 8991
196 | 1 | Supply of Materials -- Supply of 11KV HG fuse set for station transformer | ELECT | Supply | SMR12324 | 1974 | EA | 1974
197 | 1 | Supply of LT Distribution Box (SMC) | ELECT | Supply | SMR25200 | 7797 | EA | 7797
198 | 2 | Supply of 11KV 3x185 Heat Shble O/d End Term Kit | ELECT | Supply | SMR25201 | 1182.97 | EA | 2365.94
199 | 40 | Supply of XLPE Cable 1 C 150 sqmm | ELECT | Supply | SMR25203 | 114.83 | M | 4593.2
200 | 100 | Supply of XLPE Cable 3 1/2 C 185 sqmm | ELECT | Supply | SMR25204 | 547 | M | 54700
201 | 16 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation - R.S. Joists 150 x 150 mm of loading unloading) | ELECT | labour | SWR10348 | 1952.61 | EA | 31241.76
202 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-- Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Above 10 Km and upto 20 Km with Lorry for each trip | ELECT | labour | SWR11861 | 3299.7 | EA | 3299.7
203 | 27 | Load-11/33KV XLPE UG Cable for all sizes | ELECT | labour | SWR11230 | 1024 | DR | 27648
204 | 27 | Unload-11/33KV XLPE UG Cable for all sizes | ELECT | labour | SWR11231 | 1024 | DR | 27648
205 | 2500 | Excavation & laying of UG Cable (Double Run) Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, Along the CC / BT multi layer road requiring compressor-33 KV 3x400 Sqmm Cable | ELECT | labour | SWR11980 | 1388.84 | M | 3472100
206 | 200 | Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, Across the CC/ BT road crossing multi layer road requiring compressor (excluding the cost of Hume pipe)-33 KV 3x400 Sqmm Cable | ELECT | labour | SWR11988 | 1587.07 | M | 317414
207 | 1200 | Excavation & laying of UG Cable (Double Run) Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil/CC-33 KV 3x400 Sqmm Cable | ELECT | labour | SWR11972 | 749 | M | 898800
208 | 3900 | Laying of 2nd cable in excavated trench | ELECT | labour | SWR10988 | 204.1 | M | 795990
209 | 100 | Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-33 KV 3x400 Sqmm Cable | ELECT | labour | SWR12004 | 323.85 | M | 32385
210 | 16 | Making of Outdoor/Indoor End Making 33 KV 3x400 Sqmm Cable Out Door/Indoor end termination TerminationOD/Idoor end termination 33kv 3x400 xlpe | ELECT | labour | SWR10387 | 2764.76 | EA | 44236.16
211 | 30 | UG Cables Joints 33 KV 3x400 Sqmm Cable Straight through joint 33kv 3x400 xlpe | ELECT | labour | SWR10382 | 5700.78 | EA | 171023.4
212 | 100 | Cost of Pipes and slabs-Supply of 250 mm Hume pipe of class NP3 with compresive strength of 35N/mm2 for 28 days curing,barewall thickness of 30mm,1.25kG linear/meter and withstanding capability of 22.50KN/linear meter as per IS 458-1993. | ELECT | supply | SMR40077 | 363 | M | 36300
213 | 400 | Supply of 6" B class GI pipe | ELECT | supply | SMR40081 | 1044 | M | 417600
214 | 50 | Cost of Pipes and slabs-supply of 6" DWC pipe | ELECT | supply | SMR11610 | 1012 | M | 50600
215 | 3900 | Hard Rock Cutting-11KV-Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours. | ELECT | labour | SWR21903 | 30 | M | 117000
216 | 2 | Erection of AB Switch and aligment complete Erection of 33 KV AB Switch including alignment and earthing | ELECT | labour | SWR10392 | 4500 | EA | 9000
217 | 5.25 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. -- Including the cost of cement | ELECT | labour | SWR10356 | 6579 | M3 | 34539.75
218 | 0.155 | Mass Concreting for pole-Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | ELECT | labour | SWR11890 | 3893 | M3 | 603.415
219 | 10 | Fabrication of poles-Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | ELECT | labour | SWR10642 | 512.55 | EA | 5125.5
220 | 5 | Erection of pole in position, aligning and setting to work, fixing of cross arms andtop clamps, earthing of supports, back filling with earth and stones properlyramming including transport of materials from road side to location excluding pitexcavation-Box pole 9/10/11 Mtr | ELECT | labour | SWR11266 | 2643.83 | EA | 13219.15
221 | 10 | Painting of poles-Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | ELECT | labour | SWR10640 | 1132 | EA | 11320
222 | 100 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Spun poles 12.5 Mtrs / 12.9Mtrs PSCC | ELECT | labour | SWR10350 | 4521.66 | EA | 452166
223 | 70 | Excavation of pits in all soils except hard rock requiring blasting - 12Mtrs/Spun Pole 0.92 M x 0.92M x 2.3M(3.0" x 3.0" x 7.6") 1.94 cum | ELECT | labour | SWR10109 | 842.78 | EA | 58994.6
224 | 30 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-12Mtrs/Spun Pole 0.92 M x 0.92M x 2.3M (3.0" x 3.0" x 7.6") | ELECT | labour | SWR11041 | 1466.25 | EA | 43987.5
225 | 200 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELECT | labour | SWR10356 | 6579 | M3 | 1315800
226 | 18 | Supply of M+3 Tower GALV | ELECT | supply | SMR11683 | 140674.3 | EA | 2532137.4
227 | 18 | Erection of M+3 Tower GALV | ELECT | labour | SWR11850 | 64576 | EA | 1162368
228 | 18 | Supply of material for Extension of 3Mtrs for M+3 (Galvanized) S-Mat. for Extn of M+3 Tower by 3M GALV | ELECT | supply | SMR11684 | 28520.64 | EA | 513371.52
229 | 18 | Erection of Extn of 3M for M+3 Tower GALV | ELECT | labour | SWR11851 | 5168.95 | EA | 93041.1
230 | 9 | Excavation of pits in all soils except hard rock requiring blasting - M-Type Tower (1.2M x 1.2M x 3.3M ) 4.752cum | ELECT | labour | SWR12085 | 1997.93 | EA | 17981.37
231 | 9 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-M-Type Tower (1.2M x 1.2M x 3.3M ) 4.752cum | ELECT | labour | SWR12090 | 3592.95 | EA | 32336.55
232 | 80 | S&E-Smart RFID marker | ELECT | labour | SWR25089 | 2745 | EA | 219600
233 | 1 | Submission of auto CAD Drawing as per pole schedule (Detailed survey and sketch) - Up to 10 km | ELECT | labour | SWR12104 | 6000 | LS | 6000
234 | 6 | Paving out and stringing of conductor by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location-100 Sqmm Single Circuit (3 Conductors) | ELECT | labour | SWR10366 | 13856.7 | KM | 83140.2
235 | 24 | Formation of Cut points - Formation of Cut point for 33 KV Double circuit line excluding pole erection and stays | ELECT | Labour | SWR10466 | 3198.72 | EA | 76769.28
236 | 6 | LOADING of Conductor drums | ELECT | labour | SWR10191 | 202 | EA | 1212
237 | 6 | UNLOADING of Conductor drums | ELECT | labour | SWR10509 | 100 | EA | 600
238 | 300 | Loading of 33 KV Pin insulators | ELECT | labour | SWR10211 | 3 | CRT | 900
239 | 300 | Un loading of 33 KV Pin insulators | ELECT | labour | SWR10529 | 3 | CRT | 900
240 | 180 | Loading of 33 & 11 KV Disc insulators | ELECT | labour | SWR12416 | 2 | CRT | 360
241 | 180 | Un loading of 33 & 11 KV Disc insulators | ELECT | labour | SWR10631 | 2 | CRT | 360
242 | 10 | Loading of 33 KV Metal parts | ELECT | labour | SWR10618 | 65 | BAG | 650
243 | 10 | Un loading of 33 KV Metal parts | ELECT | labour | SWR10632 | 65 | BAG | 650
244 | 50 | Supply of earthing pipe with materials-Supply of GI wire No 8 | ELECT | supply | SMR11486 | 105 | KG | 5250
245 | 2 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | ELECT | labour | SWR12331 | 146.63 | EA | 293.26
246 | 300 | Supply of earthing pipe with materials S-GI Bolts & Nuts,Washers etc., | ELECT | supply | SMR11488 | 117.5 | KG | 35250
247 | 6 | Supply of earthing pipe with materials -Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | ELECT | supply | SMR11482 | 3486 | EA | 20916
248 | 12 | Earthing of Sub-Station - Supply of GI pipe 40 mm dia, 2 mtrs, 3mm thickness with bolts and nuts. | ELECT | supply | SMR40091 | 733 | EA | 8796
249 | 5000 | Cut-Tree Branch(LT/11/33)&Trnsprt Debris | ELECT | labour | SWR23200 | 4 | EA | 20000
250 | 18 | Providing of RCC collar to earth pit-Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINES-Providing of RCC collar | ELECT | labour | SWR10359 | 386 | EA | 6948
251 | 18 | Providing of Earthing-Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | ELECT | labour | SWR10357 | 1234.2 | EA | 22215.6
252 | 80 | Cost of Pipes and slabs-Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters , CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | ELECT | supply | SMR40085 | 484 | EA | 38720
253 | 2 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | ELECT | labour | SWR10881 | 142 | EA | 284
254 | 80 | S&E-Smart RFID marker | ELECT | labour | SWR25089 | 2745 | EA | 219600
255 | 1 | Fabrication & erection of Channels -Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to theRS-Joist poles excluding cost of Mild Steel and transportcharges to substation site, including erection. Fabrication of struc.with welding. | ELECT | labour | SWR10869 | 3426 | TO | 3426
256 | 367 | Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. - M.S./ G.I. Flat 75x8mm / 75 x 12 mm | ELECT | labour | SWR10918 | 50 | RMT | 18350
257 | 125 | Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) Earthing for raisers of SS Flat 50x6 mm. | ELECT | labour | SWR10919 | 41 | RMT | 5125
258 | 5 | Excavation of pits in all soils except hard rock requiring blasting-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") 1.05 cum | ELECT | labour | SWR10107 | 700 | EA | 3500
259 | 14 | Excavation of pits in all soils except hard rock requiring blasting - 12Mtrs/Spun Pole 0.92 M x 0.92M x 2.3M (3.0" x 3.0" x 7.6") 1.94 cum | ELECT | labour | SWR10109 | 842.78 | EA | 11798.92
260 | 14.8 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELECT | labour | SWR10356 | 6579 | M3 | 97369.2
261 | 0.372 | Mass Concreting for pole-Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | ELECT | labour | SWR11890 | 3893 | M3 | 1448.196
262 | 1000 | Supply of Materials -- Supply of MS Channel 100X50mm | ELECT | supply | SMR22745 | 57.45 | KGS | 57450
263 | 200 | Supply of MS Angle 65x65x6 | ELECT | supply | SMR25207 | 57.25 | KG | 11450
264 | 300 | Supply of Materials - Supply of MS Flat 75x8 mm | ELECT | supply | SMR12321 | 56.42 | KG | 16926
265 | 16 | UG Cables Joints : Making of Outdoor/Indoor End Termination -- Supply 33KV 3x400Sqmm Outdoor | ELECT | supply | SMR22222 | 4554 | EA | 72864
266 | 30 | UG Cables Joints : Making of Straight through joints -- Supply of 33KV 3x400SQmm Straight Through Joint Kit | ELECT | supply | SMR22223 | 24151 | EA | 724530
267 | 2 | Supply of Materials -- Supply of 33 kV 800 A Double break AB switch | ELECT | Supply | SMR12315 | 40658.78 | EA | 81317.56
268 | 2500 | Supply of Materials -- supply of RS Joist Poles (175X85mm) | ELECT | Supply | SMR12303 | 60.75 | KG | 151875
269 | 300 | Supply of Materials -- Supply of MS Flat 50x6 mm | ELECT | Supply | SMR12322 | 56.5 | KG | 16950
270 | 100 | Supply of PSCC Spun Pole 15Mtr 500Kg (Cement) | ELECT | Supply | SMR25239 | 42372.88 | EA | 4237288
271 | 120 | Supply of 33KV V-Cross Arm without Clamps | ELECT | Supply | SMR25229 | 1678 | EA | 201360
272 | 7000 | Supply of Materials -- supply of RS Joist Poles (175X85mm) | ELECT | Supply | SMR12303 | 60.75 | KG | 425250
273 | 17 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELECT | labour | SWR11861 | 3299.7 | EA | 56094.9
274 | 14 | Painting of poles-Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | ELECT | labour | SWR10640 | 1132 | EA | 15848
275 | 14 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Box pole 12 Mtr | ELECT | labour | SWR11267 | 3901.37 | EA | 54619.18
276 | 5 | Load-11/33KV XLPE UG Cable for all sizes | ELECT | labour | SWR11230 | 1024 | DR | 5120
277 | 5 | Unload-11/33KV XLPE UG Cable for all sizes | ELECT | labour | SWR11231 | 1024 | DR | 5120
278 | 3 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELECT | labour | SWR11861 | 3299.7 | EA | 9899.1
279 | 12 | Making of Outdoor/Indoor End Termination-Making 11 KV 3x300 Sqmm Cable Out Door/Indoor end termination | ELECT | labour | SWR10391 | 2370.63 | EA | 28447.56
280 | 8 | UG Cables Joints Making of Straight through joints-11 KV 3x300 Sqmm Cable | ELECT | labour | SWR10386 | 3725.45 | EA | 29803.6
281 | 150 | Cost of Pipes and slabs - Supply of 4" B class GI pipe | ELECT | supply | SMR40080 | 740 | M | 111000
282 | 1920 | Hard Rock Cutting-11KV-Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours. | ELECT | labour | SWR21903 | 30 | M | 57600
283 | 6 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | ELECT | labour | SWR10393 | 3200 | EA | 19200
284 | 1 | Excavation of pits in all soils except hard rock requiring blasting-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") 1.05 cum | ELECT | labour | SWR10107 | 700 | EA | 700
285 | 0.031 | Mass Concreting for pole-Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | ELECT | labour | SWR11890 | 3893 | M3 | 120.683
286 | 1 | Fabrication of poles-Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | ELECT | labour | SWR10642 | 512.55 | EA | 512.55
287 | 1 | Erection of pole in position, aligning and setting to work, fixing of cross arms andtop clamps, earthing of supports, back filling with earth and stones properlyramming including transport of materials from road side to location excluding pitexcavation-Box pole 9/10/11 Mtr | ELECT | labour | SWR11266 | 2643.83 | EA | 2643.83
288 | 2 | Painting of poles-Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | ELECT | labour | SWR10640 | 1132 | EA | 2264
289 | 50 | Supply of earthing pipe with materials-Supply of GI Flat 25X3 mm | ELECT | supply | SMR11485 | 105 | KG | 5250
290 | 6 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | ELECT | labour | SWR12331 | 146.63 | EA | 879.78
291 | 6 | Supply of earthing pipe with materials -Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | ELECT | supply | SMR11482 | 3486 | EA | 20916
292 | 1.8 | Stringing of HT AB Cable with GI Metal Parts- HT AB Cable 11 KV 3x185+70 Sqmm | ELECT | labour | SWR10454 | 41876.1 | KM | 75376.98
293 | 30 | End Termination of AB cable (each lead):- Supply of 11KV 3x185+70sq.mm/ 3x70+70sq.mm/3x35+35sq.mm AB cable end Kits | ELECT | supply | SMR11504 | 950 | SET | 28500
294 | 100 | Supply of earthing pipe with materials S-GI Bolts & Nuts,Washers etc., | ELECT | supply | SMR11488 | 117.5 | KG | 11750
295 | 50 | Drilling of holes upto 20 mm dia using power drills -MS Channel, Angles and flat | ELECT | labour | SWR10307 | 4 | EA | 200
296 | 30 | Cutting charges for MS Sections - MS Channel 100 x 50 mm | ELECT | labour | SWR10294 | 10 | EA | 300
297 | 40 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavationErrection of 11 M long PSCC pole | ELECT | labour | SWR10978 | 4336.85 | EA | 173474
298 | 6 | Providing of Earthing-Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | ELECT | labour | SWR10357 | 1234.2 | EA | 7405.2
299 | 6 | Providing of RCC collar to earth pit-Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINES-Providing of RCC collar | ELECT | labour | SWR10359 | 386 | EA | 2316
300 | 1 | LOADING of Conductor drums | ELECT | labour | SWR10191 | 202 | EA | 202
301 | 1 | UNLOADING of Conductor drums | ELECT | labour | SWR10509 | 100 | EA | 100
302 | 9.434 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELECT | labour | SWR10356 | 6579 | M3 | 62066.286
303 | 60 | Loading of 33 & 11 KV Disc insulators | ELECT | labour | SWR12416 | 2 | CRT | 120
304 | 60 | 0 | ELECT | labour | SWR10631 | 2 | CRT | 120
305 | 3 | Loading of 11 KV Metal parts | ELECT | labour | SWR12402 | 48 | BAG | 144
306 | 3 | Un loading of 11 KV Metal parts | ELECT | labour | SWR12421 | 48 | BAG | 144
307 | 80 | Excavation & laying of UG Cable (Triple Run )- Laying of XLPE UG cable Triple or more Run including excavation of trench of size 1000 mm wide to 750mm wide as per the site conditions and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the nstructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second,third or more cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs- Across the CC/ BT road crossing multi layer road requiring compressor (excluding the cost of Hume pipe) - 11 KV 3x300 Sqmm Cable | ELECT | labour | SWR12025 | 1805.4 | M | 144432
308 | 120 | Excavation & laying of UG Cable (Triple Run ) Laying of XLPE UG cable Triple or more Run including excavation of trench of size 1000mm wide to 750mm wide as per the site conditions and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second,third or more cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. - In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil/CC - 11 KV 3x300 Sqmm Cable | ELECT | labour | SWR12014 | 780.3 | M | 93636
309 | 320 | Excavation & laying of UG Cable in Single Run-Laying of XLPE UG cable including excavation of trench of size 450mm wide and850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providingof DWC/GI pipes whereever required depth is not acquired as per the instructions ofEngineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths andfilling with sand 250mm above the cable and 50mm below the cable, laying of cable,placing 40mm shabad protective slabs, back filling the trench with earth, levellingand and removing the debris from the site inluding the cost of lead and lift etc.depthof the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road-11 KV 3x300 Sqmm Cable | ELECT | labour | SWR11919 | 465.46 | M | 148947.2
310 | 1000 | Excavation & laying of UG Cable in Single Run - Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. - Along the CC / BT multi layer road requiring compressor - 11 KV 3x300 Sqmm Cable | ELECT | labour | SWR11928 | 1073.94 | M | 1073940
311 | 400 | Excavation & laying of UG Cable in Single Run - Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. - Across the CC/ BT road crossing multi layer road requiring compressor wih hume pipe (cxcluding the cost of Hume Pipe) - 11 KV 3x300 Sqmm Cable | ELECT | labour | SWR11937 | 1199.4 | M | 479760
312 | 400 | Laying of 2nd cable in excavated trench | ELECT | labour | SWR10988 | 204.1 | M | 81640
313 | 80 | Excavation & laying of UG Cable in Single Run - Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. - Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) - 11 KV 3x300 Sqmm Cable | ELECT | labour | SWR11955 | 144.08 | M | 11526.4
314 | 30 | End Termination of AB cable (each lead):- 120 Sqmm to 185 Sqmm | ELECT | labour | SWR10667 | 800 | EA | 24000
315 | 15 | Straight through joints of AB cable (each lead)- Supply and ere Angle line Asmbly kits | ELECT | labour | SWR10673 | 2124 | EA | 31860
316 | 32 | Straight through joints of AB cable (each lead) - Supply and ere Straight line Asmbly kits | ELECT | labour | SWR10672 | 1661 | EA | 53152
317 | 15 | T Branch Kit - Erection of Assemble Kit for 'T' Branche | ELECT | labour | SWR10671 | 1800 | EA | 27000
318 | 40 | Supply and Erection of I Hook and Suspension Hook - Erection of I hook | ELECT | labour | SWR12099 | 55 | EA | 2200
319 | 40 | Supply and Erection of I Hook and Suspension Hook- Supply of I hook | ELECT | supply | SMR12099 | 158 | EA | 6320
320 | 6 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | ELECT | labour | SWR10881 | 142 | EA | 852
321 | 20 | S&E-Smart RFID marker | ELECT | labour | SWR25089 | 2745 | EA | 54900
322 | 20 | Cost of Pipes and slabs-Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters , CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | ELECT | supply | SMR40085 | 484 | EA | 9680
323 | 62.5 | Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) Earthing for raisers of SS Flat 50x6 mm. | ELECT | labour | SWR10919 | 41 | RMT | 2562.5
324 | 30 | End Termination of AB cable (each lead): - Supply of 11KV 3x185+70sq.mm/ 3x70+70sq.mm/3x35+35sq.mm AB cable end Kits | ELECT | supply | SMR11504 | 950 | SET | 28500
325 | 40 | Excavation of pits in all soils except hard rock requiring blasting - 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M (1.31cum) | ELECT | labour | SWR10108 | 629.85 | EA | 25194
326 | 40 | Supply of PSCC Pole 11Mtr 365KG | ELECT | supply | SMR25236 | 5399 | EA | 215960
327 | 40 | Supply of 33KV V X- Arm with MS Channel 75x40 | ELECT | supply | SMR25219 | 561 | EA | 22440
328 | 40 | Supply of 11KV Top Cleat for 9.1M(Vertical) | ELECT | supply | SMR25226 | 256 | EA | 10240
329 | 80 | Supply of LT 11KV MS Black Clamps | ELECT | supply | SMR25217 | 72 | SET | 5760
330 | 500 | Supply of Materials -- supply of RS Joist Poles (175X85mm) | ELECT | supply | SMR12303 | 60.75 | KG | 30375
331 | 150 | Supply of Materials -- Supply of MS Flat 50x6 mm | ELECT | supply | SMR12322 | 56.5 | KG | 8475
332 | 300 | Supply of MS Channel 75x40 mm | ELECT | supply | SMR25205 | 58.45 | KG | 17535
333 | 6 | Supply of Materials -- Supply of 11 kV 800 A Double break AB switch | ELECT | supply | SMR12316 | 30847.46 | EA | 185084.76
334 | 12 | Supply of 11KV 3x300 Heat Shble o/d end term Kit | ELECT | supply | SMR25203 | 1372.88 | EA | 16474.56
335 | 8 | Supply of 11KV 3x300 Heat Shble stright through joint Kit | ELECT | supply | SMR25210 | 4110.17 | EA | 32881.36
Electrical Labour | [7 empty] | 29829887.175
Civil labour - WBS. No. S-1803-13-07-01-01-001
Sl.No. | Estimate Quantity (only Figures) | Item Detailed Specification Description | Work Type eg. Earth Work, Electrical works. etc (upto 200 Characters) | Item Short Description (upto 100 Characters) | APSS / Morth Cl. Number (upto 200 Characters) | Rate (INR) (Upto 2 Decimals ) | UOM (upto 50 Characters) | Amount
1 | 32 | Leveliing the site by cutting and levelling with the help of JCB including cost,conveyance of all materials,hire chareges etc complete for finished item of work as directed by Engineer-in-charge. | Civil | Labour | SWR34179 | 2165 | Hrs | 69280
2 | 358.34 | Earth Work Mass Excavation (hard rock) to a depth as directed, in soils such as hard rock requiring blasting in prohibited area and all conditions such as dry, wet, slurry etc.and in dense or hard soils, disposal and depositing of excavated soil with intial lead of 10 mt and intial lift of 2m or as directed, including cost and conveyance of all materials, ramping and lifting of materials, and labour charges, hire charges of machinery, tools & plants, bailing of water ( either sub soil water, stoMts water, rain water, surface water or of any kind) if any at any stage of work until all works below ground level is finished to the satisfaction ,and from work such as shoring, timbering, strutting with required supports etc. for the work and removal of form work after completion of work etc all complete as directed by the engineer-incharge. | Civil | Labour | SWR33018 | 1440 | cum | 516009.6
3 | 294.6 | Earth work excavation in all type of ordinary soils red earth, Hard gravelly soils, earth mixed with sand and sandy soils etc., in all conditions such as slushy and dry with initial leads and lifts for foundations. Ordinary Soil | Civil | Labour | SWR33015 | 486 | cum | 143175.6
4 | 102.14 | PCC (1:4:8) using 40 mm metal with concrete Mixture. All work upto Plinth level including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete as directed by Engineer incharge of the work | Civil | Labour | SWR33028 | 4780 | cum | 488229.2
5 | 142.5 | Coursed Rubble stone CRS masonry 2nd sort with hard granite stones in cement mortar CM (1:6) for basement, including cost and conveyance of all materials, labour charges, curing, all leads and lifts, etc, complete for finished item of work. | Civil | Labour | SWR33041 | 4932 | cum | 702810
6 |  | RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge
7 | 1.09 | RCC M20 Grade Footing 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33098 | 9531 | cum | 10388.79
8 | 1.58 | RCC M20 Grade Column 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33100 | 13280 | cum | 20982.4
9 | 1.15 | RCC M20 Grade plinth beam 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33099 | 12402 | cum | 14262.3
10 | 0.46 | Reinforcement steel Supplying, Cutting, bending, binding, placing in position and tying reinforcement steel in all heights including cost and conveyance of steel and binding wire etc,. With all leads and lifts, labour charges, etc., complete for finished item of work. | Civil | Labour | SWR33144 | 70687 | MT | 32516.02
11 | 107.58 | Brick masonry in CM (1:6) for superstructure using well burnt country made second class bricks of approved quality including cost and conveyance of all materials curing, scaffolding with all leads and lifts in all heights etc., complete for finished item of work | Civil | Labour | SWR33068 | 8288 | cum | 891623.04
12 | 82.23 | PCC (1:2:4) using 20mm size well graded HBG metal for foundations, including cost, conveyance of all materials,labour all leads and lifts,consolidation and all operations, formwork as required, curing,etc. complete for finished item of work | Civil | Labour | SWR33030 | 6149 | cum | 505632.27
13 | 824.75 | Plastering with CM 2 coats, 20 mm thick, base coat in CM (1:6), 16 mm thick and top coat in CM (1:4), 4mm thick with Dubara sponze finishing including cost of all materials, seigniorage charges, excluding conveyance charges of materials and including all operational, incidental and labour charges for mixing mortar, laying rendering smooth and thread lining, curing, rounding off junctions of wall and slab etc., complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33163 | 564 | Sqm | 465159
14 | 824.75 | Painting with two coats of Plastic Emulsn paint over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33356 | 210 | Sqm | 173197.5
15 | 271.85 | Painting with two coats of Surya Cem paint over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33329 | 85 | sqm | 23107.25
16 | 650 | Supplying and fixing Structural Steel angles channal etc.Manufacturing, Supplying and fixing of MS grill for (Gate and raillings) of approved design as per drawings, including cost and conveyance of all materials, labour charges etc.,complete for finished item of work as directed by the Engineer- in-charge. | Civil | Labour | SWR33145 | 128 | Kgs | 83200
17 | 3 | Supply and Fixng of MS Name Board including cost & conveyance of all materials,labour charges etc complete for finished item of work. | Civil | Labour | SWR33421 | 4326 | sqm | 12978
18 | 1 | Geophysical Investgation charges for water point by Geologist | Civil | Labour | SWR33608 | 5000 | EA | 5000
19 |  | Drilling of 165mm bore well with machine rig including deployment and hire charges of rig and other machinery and equipment labour charges , measuring the yeild of borewell including cost and conveyance etc complete
20 | 90 | Drill-165mm Bore Well 0 to 90 | Civil | Labour | SWR33609 | 336 | M | 30240
21 | 30 | Drill-165mm Bore Well 90M to 120M | Civil | Labour | SWR34830 | 369 | M | 11070
22 | 30 | Drill-165mm Bore Well 120M to 150M | Civil | Labour | SWR34831 | 394 | M | 11820
23 | 30 | Drill-165mm Bore Well 150M to 180M | Civil | Labour | SWR34832 | 492 | M | 14760
24 | 30 | Drill-165mm Bore Well 180M to 210M | Civil | Labour | SWR34833 | 623 | M | 18690
25 | 30 | Drill-165mm Bore Well 210M to 240M | Civil | Labour | SWR34834 | 754 | M | 22620
26 | 30 | Drill-165mm Bore Well 240M to 270M | Civil | Labour | SWR34835 | 918 | M | 27540
27 | 150 | Drill-165mm Bore Well 270M and above | Civil | Labour | SWR34836 | 1082 | M | 162300
28 | 40 | Supply and fixing of 160mm dia PVC casing of A class 6Kg point pressure including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR33611 | 883 | M | 35320
29 | 1 | Supply and erecting, ISI mark submersible 5.0 HP, three Phase 30 stages pumpset suitable for 106/156mm dia borewell including cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33640 | 48007 | EA | 48007
30 | 370 | Supply and fixing of HDPE pipe 40mm dia of 16Kg/cm2 including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR34410 | 180 | M | 66600
31 | 1 | Supply and erecting D.O.L Starter 415V ,3 phase,50Hz with SS enclouserincluding cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33645 | 7854 | EA | 7854
32 | 450 | Supply of 3 Core 2.5 Sqmm Flat Copper cable of ISI for Submersible Motors of makes Finolex / Polycab / Gold Medal / Million / Payal / Sun Light / Power Flex / Fortune Art | Civil | Labour | SWR33641 | 192 | M | 86400
33 | 6 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-28.60mm OD Pipe - SDR 11 | Civil | Labour | SWR34363 | 410 | M | 2460
34 | 1 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type - 25mm NB Size | Civil | Labour | SWR34346 | 466 | EA | 466
35 | 72.73 | Earth work excavation in all type of ordinary soils red earth, Hard gravelly soils, earth mixed with sand and sandy soils etc., in all conditions such as slushy and dry with initial leads and lifts for foundations. | Civil | Labour | SWR33015 | 486 | Cum | 35346.78
36 | 39.53 | PCC (1:4:8) using 40mm HBG metal for foundations and leveling course, including cost and conveyance of all materials, labour all leads and lifts, consolidation and all operations, formwork as required, curing, etc. complete for finished item w | Civil | Labour | SWR33028 | 4780 | Cum | 188953.4
37 | 27.37 | CRS Coursed Rubble Stone masonry 2nd sort with hard granite stones in cement mortar (1:6) for basement, including cost and conveyance of all materials, labour charges, curing, all leads and lifts, etc, complete for finished item of work. | Civil | Labour | SWR33041 | 4932 | Cum | 134988.84
38 | 133.29 | Supplying and filling the substation site with borrowed gravel, watering, ramming, thoroughly complying with the standard specification. | Civil | Labour | SWR33052 | 309 | Cum | 41186.61
39 |  | 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge
40 | 5.35 | a) RCC M20 Grade Footings 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33098 | 9531 | Cum | 50990.85
41 | 3.42 | b)RCC M20 Grade Columns 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33100 | 13280 | Cum | 45417.6
42 | 4.03 | c)RCC M20 Grade Plinth Beams 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33099 | 12402 | Cum | 49980.06
43 | 3.55 | D) RCC M20 Grade Roof Beams 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33121 | 12318 | Cum | 43728.9
44 | 0.58 | e) RCC M20 Grade Lintels 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33107 | 13110 | Cum | 7603.8
45 | 2.7 | f) RCC M20 Grade Sunshades 600mm wide and 75mm thick 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33114 | 1379 | Sqm | 3723.3
46 | 19.21 | g) RCC M20 Grade Roof Slab 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33128 | 10906 | Cum | 209504.26
47 | 4.55 | reinforcement steel Supplying, Cutting, bending, binding, placing in position and tying reinforcement steel in all heights including cost and conveyance of steel and binding wire etc,. With all leads and lifts, labour charges, etc., complete for finished item of work. | Civil | Labour | SWR33144 | 70687 | MT | 321625.85
48 | 59.32 | Brick masonry in CM (1:6) for superstructure using well burnt country made second class bricks of approved quality including cost and conveyance of all materials curing, scaffolding with all leads and lifts in all heights etc., complete for fin | Civil | Labour | SWR33068 | 8288 | Cum | 491644.16
49 | 536.48 | Plastering with CM 2 coats, 20 mm thick, base coat in CM (1:6), 16 mm thick and top coat in CM (1:4), 4mm thick with Dubara sponze finishing including cost of all materials, seigniorage charges, excluding conveyance charges of materials and including all operational, incidental and labour charges for mixing mortar, laying rendering smooth and thread lining, curing, rounding off junctions of wall and slab etc., complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33163 | 564 | Sqm | 302574.72
50 | 85.68 | Providing Structural steel tube box type 60x40x4mm thick including cost and conveyance of all materials, labour charges,curing etc. complete for finished item of work and as directed by the engineer-in-charge. | Civil | Labour | SWR33146 | 147 | Kgs | 12594.96
51 | 18 | Providing Roofing with Trapezoidal/Galvalume Sheet including cost and conveyance of all materials, labour charges,curing etc. complete for finished item of work and as directed by the engineer-in-charge. | Civil | Labour | SWR33402 | 600 | Sqm | 10800
52 | 18.9 | Providing Design R.C.M. drop wall of 40mm thickness with cm 1:2 and 6mm dia MS bars at 150mm both ways and chicken mesh in two coats 20mm thick each plastering including cost and conveyance of all materials with leads and lifts, scaffolding and curing, labo | Civil | Labour | SWR33203 | 3116 | Sqm | 58892.4
53 | 12.24 | Supply and fixing of MS ornamental safety grill of approved design including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33310 | 2990 | sqm | 36597.6
54 | 5.91 | Supply and fixing of doors with the MT Wood frames the door shall be made well seasoned mt wood of cross section 100x75mm. The shutter shall be made isi mark flushed door with decolam sheets pasted on both sides with PVC beading 40mm width all round.Frame shall be painted with two coats of synthetic enamel paint of approved color over one coat of primer over luppum with spary with 3 no 150mm brass hinges 1 no brass door stoper, 1 no 250mm brass aldrops. 2 no 300 mm aluminium tower bolts, 2 no 150mm brass fancy door handlers, 1 no keyless lockset with cp handel. The quoted rate shall include cost and conveyance of the meterials, fixig, labour carges, tools, handles,locking arrangementts and other fixtures & fittings for finished item work as directed by the Engineer - in- charge. | Civil | Labour | SWR33264 | 7314 | Sqm | 43225.74
55 | 20.25 | Raised pointing to the exposed surfaces of CRS masonry in cm 1:3 prop. including cost and conveyance of all materials, labour charges, all leads and lifts curing etc, complete for finished item of work. | Civil | Labour | SWR33184 | 125 | sqm | 2531.25
56 | 8.64 | Supplying and fixing Aluminium sliding windows with grill and fixed glass panels using anodised aluminium extruded sections of mat finish for frames and mullions made from approved aluminium sections 62x32x1.2mm at 0.73kg/Rm providing 5mm plain glass fix | Civil | Labour | SWR33277 | 3623 | sqm | 31302.72
57 | 16.56 | Supply and laying of Ceramic floor over of CM 1:3 20 mm thick including required materials and labour charges etc complete for item of work | Civil | Labour | SWR33224 | 914 | Sqm | 15135.84
58 | 121.92 | Flooring with double machine polished and hand cut Tandur blue stone 20mm thick of approved colour, quality and of minimum of 300x300mm size over a bed of cement mortar 1:3 20mm thick including cost of all materials, with all leads and lifts jointing and | Civil | Labour | SWR33219 | 788 | Sqm | 96072.96
59 | 6.74 | Supply and fixing of 4" high skirting of shabad stone to the walls including cost and conveyance of all materials, labour etc for finished item of work. | Civil | Labour | SWR33236 | 877 | Sqm | 5910.98
60 | 243.69 | Painting with two coats of OBD over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials labour charges etc., complete for finished item of work. | Civil | Labour | SWR33333 | 146 | Sqm | 35578.74
61 | 414.32 | Painting with two coats of Plastic emulsn paint 2 coat of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33356 | 210 | Sqm | 87007.2
62 | 129.92 | Providing impervious coat over RCC roof slab to requried slopes with 20mm thick in CM 1:3 mixed with approved brand of water proffing compound inclding cost and conveyance of all materials, labour charges, curing, rounding off junctions of wall and slab, all leads and lifts, etc . complete for finished item of work as directed by the Engineer - in - charge. | Civil | Labour | SWR33156 | 587 | Sqm | 76263.04
63 | 60 | Supply & fixing of 25mm dia 2mm thick surface P.V.C. pipe (ISI MARK) Concealed in wall with all required accessories including masonary work and labour charges etc.complete. | Civil | Labour | SWR33441 | 108 | M | 6480
64 | 1 | Supply & fixing TPNDB Distribution board with IP-42 protection (Metal Door)suitable for 3 phase ELCB/RCCB/FP Isolator as incomer and 10kA SP MCBs as out going including internal connection and labour charges for surface / flush mounting etc Complete. | Civil | Labour | SWR33526 | 11353 | EA | 11353
65 | 10 | Supply & fixing Flush type of 6A 3 pin wall plug socket with 6A switch control on a common switch board with earth continuity including wire leads,earth connection along with all labour charges etc., complete | Civil | Labour | SWR33468 | 166 | EA | 1660
66 | 6 | Supply & fixing Flush type of 16A 3 pin and 6A 3pin plug Flush type socket with indicator lamp and 16Amps fuse unit and 16Amps switch control (5 in one )duly recessed in wall with wooden deep box of 6'' x 8'' x 2 1/2'' size covered with hylam sheet earth connection and all labour charges etc., complete on wall. | Civil | Labour | SWR33470 | 449 | EA | 2694
67 | 24 | Supply and Fixing of modular switch, LP,FP,EFP,Wiring with 2 runs of 14/0.3mm (1.0 sq.mm)Fire Retardant (FR) P.V.C. insulated flexible copper cable (ISI MARK) in existing pipe with 6A Flush type Switch,ceiling rose and 3mm thick hylam sheet covering to switch control box including all labour charges etc., complete for light points, bell , fan and exhaust fan points in Non-Residential Buildings. | Civil | Labour | SWR33457 | 676 | EA | 16224
68 | 12 | Supply & Fixing of 28W T5 fluorescent tube. | Civil | Labour | SWR33558 | 148 | EA | 1776
69 | 1 | Supply of 12" (300mm)ISI, 900 RPM light duty exhaust fan with metallic blades with Mark of makes Crompton / Bajaj / Havells / Orient. | Civil | Labour | SWR33571 | 2192 | EA | 2192
70 | 180 | Supply and run of 2 of 22/0.3mm (1.5 sq.mm) (FR) P.V.C. insulated flexible copper cable in existing pipe for mains including all labour charges complete. | Civil | Labour | SWR33496 | 75 | M | 13500
71 | 180 | Supply and run of 2 of 36/0.3mm (2.5 sq.mm) FR P.V.C. insulated flexible copper cable in existing pipe for mains including all labour charges complete. | Civil | Labour | SWR33497 | 103 | M | 18540
72 | 12 | Supply & fixing of batten holder /slanting holder in lieu of ceiling rose of light point complete with all connection and all labour charges with 40W bulb (for new installation). | Civil | Labour | SWR33484 | 141 | EA | 1692
73 | 4 | Supply & fixing of 1200mm (48'') sweep 230v,A.C 50 Hz.Ceiling fan with 3 Blades and double ball bearings with all standared accessories. | Civil | Labour | SWR33563 | 2277 | EA | 9108
74 | 4 | Supply & fixing of Electronic Regulator for ceiling fans 900/1200/1400mm sweep including cost of material, Electrical charges complete for finished item of work | Civil | Labour | SWR33564 | 589 | EA | 2356
75 | 1 | Providing independent EARTHING by excavating a trench to a depth of 2.1M in all solid,as per size specified in the Data,using 40mm dia 'B' class GI pipe of 2.5 Mtrs length with necessary accessories with hume pipe ring duly providing staggered holes including filling with equal proportion of salt and Charcoal in layers and all labour charges etc., compiete for small quarters. | Civil | Labour | SWR33596 | 5345 | EA | 5345
76 | 35 | Supplying, laying, jointing and testing 101.6 mm SWG SP-1 pipes of ISI make conforming to ISI 651 & 4127 with airtight cement joints in CM 1.5:1 prop. Including excavation of trenches and socket pits in any soil (except rock requiring blasting) up to 1524 mm(5'0") depth and refilling with watering and tamping. | Civil | Labour | SWR34281 | 755 | M | 26425
77 | 3 | Constructing 904.0 mm (3#0#) dia brick masonry inspection chamber as per IS - 4111: Part-1:1986 with cement mortar (1:6) prop using 2nd Class Clay Bricks of 225 mm thick from approved source having a minimum crushing strength of 5 N/sq.mm including plastering with cement mortar 1:3 prop; ½# thick both inside and outside fitted with 20# dia RCC manhole covers and frames including excavating pits up to a depth of 904 mm (3'-0") in all sorts of soils (excluding rock) and laying cement concrete (1:4:8) 150 mm thick using 40 mm HBG Metal and P.C.C. 1:2:4 benching and channel 100 mm thick as per Standard specification and including cost and conveyance of all materials like cement, sand, bricks, water etc., to site, cost of seigniorage charges on all materials and all incidental and operational, labour charges like mixing cement mortar, constructing masonry, lift charges, curing etc., complete for finished item of work as per Standard specification. | Civil | Labour | SWR34296 | 8766 | EA | 26298
78 | 4 | Supply & fixing of 110 mm dia - Door Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34381 | 128 | EA | 512
79 | 4 | Supply & fixing of 110 mm dia - Plain Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34380 | 100 | EA | 400
80 | 12 | Supply & fixing of 110 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand | Civil | Labour | SWR34377 | 462 | M | 5544
81 | 18 | Supply & fixing of 90 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand | Civil | Labour | SWR34378 | 410 | M | 7380
82 | 3 | Supplying & fixing 150 mm x 100 mm SWG gully traps conforming to ISI 651 & 4127 with C.I Grating & Cost. Brick masonry in CM 1:6 prop. Intermediate chamber and fitted with 304.8 mm x 288.6mm (12"x9") C.I Frame and hinged cover | Civil | Labour | SWR34286 | 767 | EA | 2301
83 | 1 | Supplying and Fixing of European Water Closet of 1st Quality | Civil | Labour | SWR34314 | 2228 | EA | 2228
84 | 6 | Supply & fixing 15 mm angle stop cock Indian make 400 grams Seiko/ Senior/ Nice/ Senior/ Nice or equivalent | Civil | Labour | SWR34328 | 721 | EA | 4326
85 | 4 | S&F 15 mm N.P bib tap Indian make 400 grams full turn Seiko/ Senior/ Nice or equivalent | Civil | Labour | SWR34329 | 296 | EA | 1184
86 | 1 | Supplying & Fixing Indian make Flat Back Wash Hand Basin (HSW/Parryware/ Neycer) 1st quality conforming to IS:2556-Part-4:1972 with waste fittings like rubber plug, chain, 32 mm nominal size C.P. Fitting with parallel pipe thread conforming to IS:2963-1979 and fitted with 15 mm nominal bore Chromium Plated Pillar Tap of 1st quality Indian make 400 grams Seiko/ Senior/ Nice/ Esso or equivalent complete with standard CI brackets including wooden block: 550 x 400 mm - Single C.P. Pillar cock | Civil | Labour | SWR34316 | 1717 | EA | 1717
87 | 2 | Supply & fixing 38.1 mm C.P waste coupling Half or Full Thread 1st Quality Indian make Parryware or equivalent | Civil | Labour | SWR34428 | 309 | EA | 618
88 | 2 | Supply & fixing of 4" (101.6 mm ) Nahany Trap ( Without Jali with inlet)UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34387 | 134 | EA | 268
89 | 1000 | Providing & Placing on Terrace (at all floor levels) polyethylene water storage tank with Double layer approved brand & manufacture with cover and suitable locking arrangement & making necessary holes for inlet & outlets and over flow pipes but with NECESSARY fittings & base support for tanks | Civil | Labour | SWR34375 | 10 | L | 10000
90 | 2 | Supply & fixing 31.75 mm dia PVC flexible waste pipe of 914.4 mm length of Ist quality | Civil | Labour | SWR34426 | 33 | EA | 66
91 | 45 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)- 15.90mm OD Pipe - SDR 11 | Civil | Labour | SWR34361 | 239 | M | 10755
92 | 40 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-22.20mm OD Pipe - SDR 11 | Civil | Labour | SWR34362 | 313 | M | 12520
93 | 65 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-28.60mm OD Pipe - SDR 11 | Civil | Labour | SWR34363 | 410 | M | 26650
94 | 4 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type - 25mm NB Size | Civil | Labour | SWR34346 | 466 | EA | 1864
95 | 4 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type -20mm NB Size | Civil | Labour | SWR34345 | 331 | EA | 1324
96 | 1 | Supply & fixing 25.4 mm dia & 609.6 mm long aluminium anodized towel rod with brackets and aluminium screws | Civil | Labour | SWR34430 | 489 | EA | 489
97 | 85.51 | Earth work excavation in all type of Ordinary soils red earth, Hard gravelly soils, earth mixed with sand and sandy soils etc., in all conditions such as slushy and dry with initial leads and lifts for foundations. Ordinary Soil | Civil | Labour | SWR33015 | 486 | cum | 41557.86
98 | 18.91 | PCC (1:4:8) using 40mm HBG metal for foundations and leveling course, including cost and conveyance of all materials, labour all leads and lifts, consolidation and all operations, formwork as required, curing, etc. complete for finished item w | Civil | Labour | SWR33028 | 4780 | cum | 90389.8
99 | 91.8 | Coursed Rubble stone masonry (CRS) 2nd sort with hard granite stones in cement mortar (1:6) for basement, including cost and conveyance of all materials, labour charges, curing, all leads and lifts, etc, complete for finished item of work. | Civil | Labour | SWR33041 | 4932 | cum | 452757.6
100 | 36 | PCC (1:3:6) using 40mm HBG metal for foundations and leveling course, including cost and conveyance of all materials, labour all leads and lifts, consolidation and all operations, formwork as required, curing, etc. complete for finished item w | Civil | Labour | SWR33029 | 5070 | cum | 182520
101 | 108 | Raised pointing to the exposed surfaces of CRS masonry in cm 1:3 prop. including cost and conveyance of all materials, labour charges, all leads and lifts curing etc, complete for finished item of work. | Civil | Labour | SWR33184 | 125 | sq.mm | 13500
102 | 787.5 | Supplying and filling the substation site with borrowed gravel, watering, ramming, thoroughly complying with the standard specification. | Civil | Labour | SWR33052 | 309 | cum | 243337.5
103 | 88.8 | Plastering with CM 2 coats, 20 mm thick, base coat in CM (1:6), 16 mm thick and top coat in CM (1:4), 4mm thick with Dubara sponze finishing including cost of all materials, seigniorage charges, excluding conveyance charges of materials and including all operational, incidental and labour charges for mixing mortar, laying rendering smooth and thread lining, curing, rounding off junctions of wall and slab etc., complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33163 | 564 | sq.mm | 50083.2
104 | 200.85 | Painting with two coats of Surya Cem paint over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33329 | 85 | sq.mm | 17072.25
105 | 120 | Supply&Fabrication and fixing of Welded wire mesh ( 2" x 2") of 3mm dia. with ISMC (75x40x4.4mm) and Pheriperal frame of ISA(35x35x3mm) incldg cost& conveyance painting with synthetic enamil paint two coats over a coat of red oxide primer etc complete for finished item of work.. | Civil | Labour | SWR33403 | 2310 | sq.mm | 277200
106 | 160 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-22.20mm OD Pipe - SDR 11 | Civil | Labour | SWR34362 | 313 | M | 50080
107 | 30 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type - 25mm NB Size | Civil | Labour | SWR34346 | 466 | EA | 13980
108 | 1 | Providing Consultancy services for arranging contour surveying with total station incuding preparation of boundary and contour levels with 2 Nos. Hard copies and soft copies complete for finished items of work | Civil | Labour | SWR33427 | 5665 | EA | 5665
109 | 576.11 | Seigniorage Charges - Sand | Civil | Labour | SWR34470 | 40 | cum | 23044.4
110 | 1837.38 | Seigniorage Charges - Metal | Civil | Labour | SWR34471 | 97.5 | cum | 179144.55
111 | 920.79 | Seigniorage Charges - Gravel | Civil | Labour | SWR34472 | 30 | cum | 27623.7
112 | 60 | Supply and fixing of RCC fencing poles of size 0.1mx0.1mx1.8m (security fencing of sub station), including cost and conveyance of all labour, materials,and hire chareges etc complete for finished item of work. | Civil | Labour | Swr33405 | 1444 | EA | 86640
113 | 1200 | Supply and fixing of galvanised barded wire (1 horizantal & 2 cross strands. including cost and conveyance of all labour, materials,and hire chareges etc complete for finished item of work. | Civil | Labour | Swr33408 | 16 | M | 19200
Civil labour | [7 empty] | 9152465.39
Electrical and Civil labour |  |  |  |  | 18% GST Rs. |  |  | 38982352.565

## 15. Bandlaguda
Name of the Work :- Erection of 33/11 kV Outdoor SS Bandlaguda (Fatheguda) in Saroornagar Circlewith connected 33KV and with 6 No.s new 11KV feeders at FATHALGUDA in LB Nagar (M) of LB Nagar Sub-Division of Saroornagar Division in Saroornagar Circle
WBS Element :- S-1804-13-03-01-01-001
Sl No | Estimate Quantity | Description of item | Work Type | Item Short Description | APSS / Month Cl.NumberSSR 11 & 12 | Rate (INR) | UOM | AMOUNT
1 | 16 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | ELECT | Labour | SWR11039 | 928 | EA | 14848
2 | 5.76 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ELECT | Labour | SWR10868 | 6852 | TO | 39467.52
3 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELECT | Supply | SMR40009 | 2181 | TO | 12562.56
4 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELECT | Labour | SWR10877 | 851 | TO | 4901.76
5 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELECT | Supply | SMR40010 | 1293 | TO | 7447.68
6 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELECT | Labour | SWR10879 | 482 | TO | 2776.32
7 | 5.76 | Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ELECT | Labour | SWR10867 | 1470 | TO | 8467.2
8 | 16 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-R.S. Joists 150 x 150 mm | ELECT | Labour | SWR10348 | 1952.61 | EA | 31241.76
9 | 17.758 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELECT | Labour | SWR10356 | 6579 | M3 | 116829.88
10 | 9.24 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ELECT | Labour | SWR10862 | 373 | M2 | 3446.52
11 | 16 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | ELECT | Labour | SWR11089 | 48 | EA | 768
12 | 4 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-8.0Mtrs PSCC Poles 0.76 M x 0.76M x 1.52M (2.6" x 2.6" x 5.0') 0.88 cum | ELECT | Labour | SWR11037 | 793 | EA | 3172
13 | 1 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ELECT | Labour | SWR10868 | 6852 | TO | 6852
14 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELECT | Supply | SMR40009 | 2181 | TO | 2181
15 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELECT | Labour | SWR10877 | 851 | TO | 851
16 | 1 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELECT | Supply | SMR40010 | 1293 | TO | 1293
17 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELECT | Labour | SWR10879 | 482 | TO | 482
18 | 1 | Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ELECT | Labour | SWR10867 | 1470 | TO | 1470
19 | 4 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Box pole 12 Mtr | ELECT | Labour | SWR11267 | 3901.37 | EA | 15605.48
20 | 2.65 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELECT | Labour | SWR10356 | 6579 | M3 | 17434.35
21 | 2.31 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ELECT | Labour | SWR10862 | 373 | M2 | 861.63
22 | 4 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | ELECT | Labour | SWR11089 | 48 | EA | 192
23 | 5.063 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ELECT | Labour | SWR10868 | 6852 | TO | 34691.68
24 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELECT | Supply | SMR40009 | 2181 | TO | 11042.4
25 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELECT | Labour | SWR10877 | 851 | TO | 4308.61
26 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELECT | Supply | SMR40010 | 1293 | TO | 6546.46
27 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELECT | Labour | SWR10879 | 482 | TO | 2440.37
28 | 5.063 | Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ELECT | Labour | SWR10867 | 1470 | TO | 7442.61
29 | 13 | Erection of AB Switch and aligment complete Erection of 33 KV AB Switch including alignment and earthing | ELECT | Labour | SWR10392 | 4500 | EA | 58500
30 | 34 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Note:-The requirement of 2nd coat is to be justified by the concerned Divisional Engineer /Executive Engineer before execution of this work Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | ELECT | Labour | SWR10881 | 142 | EA | 4828
31 | 34 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | ELECT | Labour | SWR12331 | 146.63 | EA | 4985.42
32 | 6 | Loading of 33 KV CTs/ PTs | ELECT | Labour | SWR10200 | 165 | EA | 990
33 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELECT | Labour | SWR11861 | 3299.7 | EA | 3299.7
34 | 6 | Un loading of 33 KV CTs/ PTs | ELECT | Labour | SWR10518 | 128 | EA | 768
35 | 2 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33kv single phase PT s | ELECT | Labour | SWR10401 | 1079 | SET | 2158
36 | 12 | Loading of 33 KV, 10 KA LAs Station typ | ELECT | Labour | SWR10266 | 41 | EA | 492
37 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELECT | Labour | SWR11861 | 3299.7 | EA | 3299.7
38 | 12 | Un loading of 33 KV, 10 KA LAs Station type | ELECT | Labour | SWR10584 | 35 | EA | 420
39 | 4 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33 KV LAS station/Line type including earthing | ELECT | Labour | SWR10396 | 880 | SET | 3520
40 | 2 | Loading of 33 KV VCBs along with Panel boards | ELECT | Labour | SWR10198 | 1024 | EA | 2048
41 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELECT | Labour | SWR11861 | 3299.7 | EA | 3299.7
42 | 2 | Un loading of 33 KV VCBs along with Panel boards | ELECT | Labour | SWR10516 | 1044.48 | EA | 2088.96
43 | 12.584 | Excavate-Pit for 33KV VCB | ELECT | Labour | SWR23224 | 331 | M3 | 4165.3
44 | 14.52 | Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x 1.8 x 0.75 cum for VCB Plinth | ELECT | Labour | SWR20685 | 5160 | M3 | 74923.2
45 | 2 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33 KV VCB with Control Panel | ELECT | Labour | SWR10460 | 12500 | EA | 25000
46 | 2 | Loading and unloading of PTR on constructed plinth-Loading of 8MVA PTR | ELECT | Labour | SWR10613 | 5805.84 | EA | 11611.68
47 | 2 | Transport of Power transformers (0 to 100 KM) from one place to another place in GHMC Area.(excluding of loading & unloading )-8MVA power transformer | ELECT | Labour | SWR10854 | 21945 | EA | 43890
48 | 2 | Loading and unloading of PTR on constructed plinth-Unloading of 8MVA PTR | ELECT | Labour | SWR10627 | 5805.84 | EA | 11611.68
49 | 700 | S/o rail poles 90/105lb (250x2N) | ELECT | Labour | SMR22718 | 47.27 | KG | 33089
50 | 14 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Rail pole 90 lbs | ELECT | Labour | SWR10344 | 3510 | EA | 49140
51 | 2 | Erection of PTR on constructed plinth-Erection of 8 MVA PTR. | ELECT | Labour | SWR21321 | 49480.2 | EA | 98960.4
52 | 0.436 | Extention of 33KV Bay at 132/33KV Sub-station-Zebra condutor | ELECT | Labour | SMR24910 | 299369 | KM | 130524.88
53 | 30 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing | ELECT | Supply | SMR11915 | 2055 | SET | 61650
54 | 30 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of I-Bolts | ELECT | Supply | SMR22473 | 294 | EA | 8820
55 | 45 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 "to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating . Sup T clamp LM6 Al alloy of 12 mm, 800 A | ELECT | Supply | SMR40011 | 299 | EA | 13455
56 | 6 | Bus stringing Hoisting of Insulators and hardware, stretching the conductor and stringing of 33 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bussection of 4.5mt) Hoisting post ins&hrd wr 1panther 33kv | ELECT | Labour | SWR21240 | 781 | EA | 4686
57 | 84 | Stringing of bus with panther conductor including jumpering etc., complete to all the equipment in SS fixing to all clamps and equipment.(3 Conductors) | ELECT | Labour | SWR10404 | 327.68 | M | 27525.12
58 | 30 | Bus stringing Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | ELECT | Labour | SWR10884 | 224 | EA | 6720
59 | 75 | Labour for Fixing of all types of clamps | ELECT | Labour | SWR10917 | 65 | EA | 4875
60 | 25 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | ELECT | Labour | SWR11039 | 928 | EA | 23200
61 | 8.68 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ELECT | Labour | SWR10868 | 6852 | TO | 59475.36
62 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELECT | Supply | SMR40009 | 2181 | TO | 18931.08
63 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELECT | Labour | SWR10877 | 851 | TO | 7386.68
64 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELECT | Supply | SMR40010 | 1293 | TO | 11223.24
65 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELECT | Labour | SWR10879 | 482 | TO | 4183.76
66 | 8.68 | Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ELECT | Labour | SWR10867 | 1470 | TO | 12759.6
67 | 25 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-R.S. Joists 150 x 150 mm | ELECT | Labour | SWR10348 | 1952.61 | EA | 48815.25
68 | 27.75 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELECT | Labour | SWR10356 | 6579 | M3 | 182567.25
69 | 17.91 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ELECT | Labour | SWR10862 | 373 | M2 | 6680.43
70 | 25 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | ELECT | Labour | SWR11089 | 48 | EA | 1200
71 | 4.642 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ELECT | Labour | SWR10868 | 6852 | TO | 31806.98
72 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELECT | Supply | SMR40009 | 2181 | TO | 10124.2
73 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELECT | Labour | SWR10877 | 851 | TO | 3950.34
74 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELECT | Supply | SMR40010 | 1293 | TO | 6002.11
75 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELECT | Labour | SWR10879 | 482 | TO | 2237.44
76 | 4.642 | Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ELECT | Labour | SWR10867 | 1470 | TO | 6823.74
77 | 17 | Erection of AB Switch and aligment complete-Erection of 11KV 800A double throw AB Switches | ELECT | Labour | SWR21277 | 3500 | EA | 59500
78 | 3 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | ELECT | Labour | SWR10393 | 3200 | EA | 9600
79 | 2 | Loading of 11 KV CT - PT Sets | ELECT | Labour | SWR10201 | 190 | EA | 380
80 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELECT | Labour | SWR11861 | 3299.7 | EA | 3299.7
81 | 2 | Un loading of 11 KV CT - PT Sets | ELECT | Labour | SWR10519 | 101 | EA | 202
82 | 2 | Erection of 11 KV three phase PTs | ELECT | Labour | SWR10402 | 800 | SET | 1600
83 | 24 | Loading of 11 KV, 10 KA LAs Station type | ELECT | Labour | SWR10264 | 32 | EA | 768
84 | 2 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELECT | Labour | SWR11861 | 3299.7 | EA | 6599.4
85 | 24 | Un loading of 11 KV, 10 KA LAs Station type | ELECT | Labour | SWR10582 | 32 | EA | 768
86 | 2 | Erection of 11 KV LAS station type including earthing | ELECT | Labour | SWR10397 | 559 | SET | 1118
87 | 6 | Erection of 11 KV LAS line type including earthing | ELECT | Labour | SWR10398 | 505 | SET | 3030
88 | 8 | Loading of 11 KV VCBs along with Panel boards | ELECT | Labour | SWR10199 | 1024 | EA | 8192
89 | 4 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELECT | Labour | SWR11861 | 3299.7 | EA | 13198.8
90 | 8 | Un Loading of 11 KV VCBs along with Panel boards | ELECT | Labour | SWR10517 | 1044.48 | EA | 8355.84
91 | 41.6 | Excavate-Pit for 33KV VCB | ELECT | Labour | SWR23224 | 331 | M3 | 13769.6
92 | 48 | Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x 1.8 x 0.75 cum for VCB Plinth | ELECT | Labour | SWR20685 | 5160 | M3 | 247680
93 | 8 | Erection of 11 KV VCB with Control Panel | ELECT | Labour | SWR10461 | 12000 | EA | 96000
94 | 12 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing | ELECT | Supply | SMR11915 | 2055 | SET | 24660
95 | 12 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of I-Bolts | ELECT | Supply | SMR22473 | 294 | EA | 3528
96 | 45 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 "to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating . Sup T clamp LM6 Al alloy of 12 mm, 800 A | ELECT | Supply | SMR40011 | 299 | EA | 13455
97 | 2 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 11 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 3.5mt) Hoisting post ins&hrd wr 1panther 11kv | ELECT | Labour | SWR21241 | 507 | EA | 1014
98 | 63 | Stringing of bus with panther conductor including jumpering etc., complete to all the equipment in SS fixing to all clamps and equipment.(3 Conductors) | ELECT | Labour | SWR10404 | 327.68 | M | 20643.84
99 | 45 | Bus stringing Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | ELECT | Labour | SWR10884 | 224 | EA | 10080
100 | 57 | Labour for Fixing of all types of clamps | ELECT | Labour | SWR10917 | 65 | EA | 3705
101 | 584 | Laying of earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication 75x 8mm MS Flat / GI Flat. Laying of earth mat,excavation 75x 8mm | ELECT | Labour | SWR10920 | 65 | RMT | 37960
102 | 1010 | Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) Earthing for raisers of SS Flat 50x6 mm. | ELECT | Labour | SWR10919 | 41 | RMT | 41410
103 | 36 | Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | ELECT | Supply | SMR11482 | 3486 | EA | 125496
104 | 36 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | ELECT | Labour | SWR10357 | 1234.2 | EA | 44431.2
105 | 36 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINES-Providing of RCC collar | ELECT | Labour | SWR10359 | 386 | EA | 13896
106 | 2 | Supply of Copper Flexible jumper with 75 X 8 of length 250 mm at neutral of Power tranformer end and 50 X 6 of length 50mm two Nos at double neutral end duly brasing with flexible jumper of capacity of 5kA/3 sec for power transformer neutral. SupCU Flexi jumper for Power T/F Neutral | ELECT | Supply | SMR40033 | 4725 | EA | 9450
107 | 2 | Providing of earthing with various types of earth electrodes-Providing of double earthing for neutral with flexible copper jumpers including arrangement by fixing M.S.Channel 100x50mm. | ELECT | Labour | SWR11892 | 1323 | EA | 2646
108 | 4 | Loading of LT AB Cable 3X16+25 Sqmm | ELECT | Labour | SWR11702 | 200 | DR | 800
109 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELECT | Labour | SWR11861 | 3299.7 | EA | 3299.7
110 | 4 | Un loading of LT AB Cable 3X16+25 Sqmm | ELECT | Labour | SWR11713 | 204 | DR | 816
111 | 80 | Providing of control cable trench as per DATA-XII | ELECT | Labour | SWR22093 | 3148 | RMT | 251840
112 | 3074 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends . Lay-4C/10C 2.5Sqmm Control Cable | ELECT | Labour | SWR11879 | 27 | M | 82998
113 | 270 | Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per specification (including cost of ferrules, lugs and glands) | ELECT | Labour | SWR12510 | 27 | EA | 7290
114 | 4 | Marshalling Box Supply of FRP PT Marshalling Box | ELECT | supply | SMR40048 | 4463 | EA | 17852
115 | 4 | Marshalling Box Erection of Marshalling boxes | ELECT | Labour | SWR10940 | 374.85 | EA | 1499.4
116 | 1 | Loading of 220 V Batterry with charger | ELECT | Labour | SWR11166 | 1612 | SET | 1612
117 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELECT | Labour | SWR11861 | 3299.7 | EA | 3299.7
118 | 1 | Un loading of 220 V Batterry with charger | ELECT | Labour | SWR11147 | 1024 | SET | 1024
119 | 1 | Batteries-Erection of 220 V, 200 AH battery in complete shape fit for | ELECT | Labour | SWR12350 | 7666 | EA | 7666
120 | 1 | Supply of DC Annunciation & relay panel for 10 feeder panel including the cost of LED Indiacation lamps, VAA auxilairy relays, Electronic Hooters complete as per specification. | ELECT | supply | SMR40044 | 42500 | EA | 42500
121 | 1 | Supply of AC Supply panel inluding providing of changeover switch, SFU, metering unit, 32 A three phase MCB, 16 A Single phase MCB complete as per specification. Supply of AC Supply panel complete | ELECT | Supply | SMR40045 | 42000 | EA | 42000
122 | 2 | Fixing of AC/DC Panel and giving Connections to the protection equipment and Metering circuits as per the specification and standards. The 3 1/2 core 25 Sqmm power cable required from distribution box to AC/DC panel in the control room is also to be supply | ELECT | Labour | SWR20025 | 7871.85 | SET | 15743.7
123 | 8 | Yard lightning-Supply of stepped tubular poles single way made of steel of length 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9 mm, 2.1 mtrs with outer dia 76.1 mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79 kgf as per IS 2713 | ELECT | Supply | SMR40051 | 13913 | EA | 111304
124 | 8 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE/CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA /OSRAM /SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty S-90W LED fixture set | ELECT | Supply | SMR11594 | 8200 | EA | 65600
125 | 8 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | ELECT | Labour | SWR11039 | 928 | EA | 7424
126 | 8 | Erection of tubular poles | ELECT | Labour | SWR10955 | 1379 | EA | 11032
127 | 5.27 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELECT | Labour | SWR10356 | 6579 | M3 | 34671.33
128 | 8 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE/CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA /OSRAM /SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty. Fixing of Metal halide lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5 GI pipe complete Fixing of LED/Metal halide complete. | ELECT | Labour | SWR10956 | 1268 | EA | 10144
129 | 45 | Supply of HBG metal-Supply & spreading of 20mm machine crushed metal (HBG) including cost of conveneyance of all materials, labour charges etc complete for finished item of work and directed by the engineer incharge | ELECT | Supply | SWR10860 | 2113 | M3 | 95085
130 | 2 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M Ex of Hard pit w/o blast 0.75X0.9X1.95M | ELECT | Labour | SWR11040 | 990.68 | EA | 1981.36
131 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ELECT | Supply | SMR40009 | 2181 | TO | 1635.75
132 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ELECT | Labour | SWR10877 | 851 | TO | 638.25
133 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ELECT | Supply | SMR40010 | 1293 | TO | 969.75
134 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ELECT | Labour | SWR10879 | 482 | TO | 361.5
135 | 1 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Box pole 12 Mtr | ELECT | Labour | SWR11267 | 3901.37 | EA | 3901.37
136 | 2.22 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELECT | Labour | SWR10356 | 6579 | M3 | 14605.38
137 | 1.16 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ELECT | Labour | SWR10862 | 373 | M2 | 432.68
138 | 2 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints | ELECT | Labour | SWR11089 | 48 | EA | 96
139 | 1 | Construction of DTR Plinth-RCC Column type DTR Plinth of size 1'X1'X10',topslab 4'x4'x6" & beam size 4'X8'X8" upto 160KVA | ELECT | Labour | SWR21843 | 25967.57 | EA | 25967.57
140 | 1 | Loading of 50,63, 75 & 100 KVA DTR | ELECT | Labour | SWR10195 | 350 | EA | 350
141 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELECT | Labour | SWR11861 | 3299.7 | EA | 3299.7
142 | 1 | Un loading of 50,63, 75 & 100 KVA DTR | ELECT | Labour | SWR10513 | 280 | EA | 280
143 | 1 | Erection of DTR's including loading and Unloading DTR on the Structure/Plinth etc-Erection of 3 Phase DTRs 63,75 & 100 KVA | ELECT | Labour | SWR20905 | 1650 | EA | 1650
144 | 1 | Erection of AB Switch and aligment complete Erection of 11KV 200A TT type AB Switch including fixing of cross angles and alignment complete | ELECT | Labour | SWR20102 | 1813.49 | EA | 1813.49
145 | 40 | Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.-In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road-11KV 3x185 Sqmm Cable | ELECT | Labour | SWR11920 | 465.46 | M | 18618.4
146 | 20 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-11 KV 3x185 Sqmm Cable | ELECT | Labour | SWR11956 | 126.23 | M | 2524.6
147 | 2 | UG Cables Joints Making of Outdoor/Indoor End Termination OD/Idoor end termination 11kv 3x185 xlpe | ELECT | Labour | SWR10390 | 2370.63 | EA | 4741.26
148 | 1 | Erection of LT distribution box including laying of LT cable from distribution box to LT OH line and DTR to distribution box including earthing of distribution box and crimping of lugs connecting of jumpers etc | ELECT | Labour | SWR10674 | 1594.67 | EA | 1594.67
149 | 85 | LAYING OF 33KV, 11KV UG CABLE Excavation & laying of UG Cable in Single Run Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road-LT 3 1/2 x 185 Sqmm Cable | ELECT | Labour | SWR11923 | 377.63 | M | 32098.55
150 | 15 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-LT 3 1/2 x 185 Sqmm Cable | ELECT | Labour | SWR11959 | 85.43 | M | 1281.45
151 | 2 | Making of Outdoor/Indoor End Termination-Supply of 31/2x185Sqmm UG O/D end termination kits | ELECT | Supply | SMR40140 | 550 | EA | 1100
152 | 2 | Supply & fixing of Oout Door/Indoor end termination LT 3 1/2 x 185 Sqmm Cable | ELECT | Labour | SWR10765 | 968.9 | EA | 1937.8
153 | 1 | Supply and fixing of Substation board of size 3'x2.5' indicating the layout of switchyard Sup &fix of board ind Switchyard layout | ELECT | Supply | SWR20032 | 1654 | EA | 1654
154 | 1 | Supply and fixing of safety instructions/Substation operation instruction board. Sup& fix safety inst/SS Op. inst board | ELECT | Supply | SWR22090 | 2205 | EA | 2205
155 | 750 | Control Panels Supplying & fabrication erection of 6mm Checkerd plates as per the field conditions Supply,fabricati of 6mm Checkerd plates | ELECT | Labour | SWR10873 | 83 | KG | 62250
156 | 1 | T & P Supply of Wall clock standard make | ELECT | Supply | SMR40059 | 578 | EA | 578
157 | 1 | S-10ft Aluminium Ladder | ELECT | Supply | SMR12378 | 1654 | EA | 1654
158 | 1 | Sup Alluminium Ladder for indoor works | ELECT | Supply | SMR40062 | 4410 | EA | 4410
159 | 30 | T & P Painting of Name Plates for any equipmen | ELECT | Labour | SWR10963 | 122 | EA | 3660
160 | 1 | T & P Supply of Taparia Tool kit of Size 20”x10”x15” with tier arrangements Tool box with locking arrangement & key containing (1) Double Ended fix Spanner sets, (Ribbed) 6 x 7, 8 x 9, 10 x 11, 12 x 13, 14 x 15, 16 x 17, 18 x19, 20 x 22, 21 x 23, 24 x 27, 25 x28, 30 x 32, (2) Double Ended Ring Spanners sets, 6 x 7 , 8 x 9, 10 x 11, 12 x 13, 14 x 15. 16 x 17 , 18 x 19, 20 x 22 , 21 x 23, 24 x 27, 25 x28, 30 x 32 mm, (3) Adjustable Spanner 305 mm length least maximum opening 35mm chrome, (4) Pipe Wrench Length 350 mm 14”, (5) Soft faced Hammer with suitable handle 2 lb, (6) Hacksaw frame with metal handle heavy duty for 12" hacksaw blade with High Speed blade, (7) Insulated Screw drivers Transparent Green Handle Set Length 6”, 8” & 12”, (8) Star Screw Driver Transparent Green Handle Length 6”, (9) Insulated Wire Cutter, (10) Insulated Cutting Plier Length 8” with cable stripper insulated with thick C. A. sleeve confirming to IS: 4378 - 1990, (11) Long Nose Plier insulated with thick C.A. sleeve generally confirming to IS:3552-1989, (12) Tester type screw driver (special with neon bulb) generally confirm to IS: 5579- 1985 Grade:II handle yellow/ green colour overall length 130 mm, (13) Insulated Crimping Plier of all Taparia make. SupTaparia Tool kit complete as per Spec | ELECT | Supply | SMR40063 | 4925 | SET | 4925
161 | 1 | T & P Sup Rechargeable LED torch light of Standard make | ELECT | Supply | SMR40064 | 1733 | EA | 1733
162 | 1 | T & P-Steel almarah(61/2 X 3ft) Godrej | ELECT | Supply | SMR40061 | 9818 | EA | 9818
163 | 1 | T & P-Table (3x6ft) Godrej | ELECT | Supply | SMR40057 | 6050 | EA | 6050
164 | 4 | T & P-S type chairs (Godrej) | ELECT | Supply | SMR40058 | 924 | EA | 3696
165 | 1 | T & P Sup Angle racks(18x36.6inches) Godrej | ELECT | Supply | SMR40060 | 1733 | EA | 1733
166 | 1 | T & P Supply of Hack saw (12 inches) | ELECT | Supply | SMR40065 | 289 | EA | 289
167 | 4 | Sup Earth Rods (8ft) Screw & clamp type | ELECT | Supply | SMR40066 | 578 | EA | 2312
168 | 2 | Supply of Hand Gloves | ELECT | Supply | SMR40067 | 289 | SET | 578
169 | 12 | SupRubber mats( 6'x3')size fo indoorSS | ELECT | Labour | SMR40068 | 1386 | EA | 16632
170 | 1 | Biometric Time attendence System & Telecom Sup Stand basic cell phone with charger | ELECT | Supply | SMR40069 | 1386 | EA | 1386
171 | 14 | Supply of Danger boards with clamps | ELECT | Supply | SMR40070 | 116 | EA | 1624
172 | 2 | Fire bucket stand with 3 buckets (8 -10 ltr capacity) | ELECT | Supply | SMR40088 | 1386 | SET | 2772
173 | 2 | Room fire extinguisher (2 ltrs capacity) for control room | ELECT | Supply | SMR40089 | 4620 | EA | 9240
174 | 4 | Sup TrollyMounted Co2 (6.5Kgs) Cylinders(IS-2878) | ELECT | Supply | SMR40087 | 9240 | EA | 36960
175 | 6 | Supply of Safety Helmet of standard make | ELECT | Supply | SMR40071 | 231 | EA | 1386
176 | 8 | Supply of LC Boards | ELECT | Supply | SMR40072 | 116 | EA | 928
177 | 4 | Supply of Gum Boots(Pair) | ELECT | Supply | SMR40073 | 693 | EA | 2772
178 | 1 | Supply of 5000v megger | ELECT | Supply | SMR40074 | 13860 | EA | 13860
179 | 1 | Supply of Earth megger (1000v) | ELECT | Supply | SMR40075 | 8085 | EA | 8085
180 | 1 | Supply of Digital clamp meter. | ELECT | Supply | SMR40076 | 2888 | EA | 2888
181 | 1 | Name board of the 33/11kV Sub-Station(As per Standard Specification) Sup 33/11kv S.S Permanent name board | ELECT | Supply | SMR40086 | 10238 | EA | 10238
182 | 800 | Supply of Hot dip galvanized/zinc coated bolts & nuts including spring washers, pack washers and flat washers etc. | ELECT | Supply | SMR12488 | 90 | KG | 72000
183 | 2 | Fabrication of poles-Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | ELECT | Labour | SWR10642 | 512.55 | EA | 1025.1
184 | 1 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-RS Joists 150x75/175 x 85 mm | ELECT | Labour | SWR10346 | 1934 | EA | 1934
185 | 5760 | Supply of Materials -- Supply of RS Joist girder Poles (150X150mm) | ELECT | Supply | SMR12302 | 59.25 | KG | 341280
186 | 1000 | Supply of Materials -- supply of RS Joist Poles (175X85mm) | ELECT | Supply | SMR12303 | 60.75 | KG | 60750
187 | 5063 | Supply of Materials -- Supply of MS Channel 100X50mm | ELECT | Supply | SMR22745 | 57.45 | KGS | 290869.35
188 | 13 | Supply of Materials -- Supply of 33 kV 800 A Double break AB switch | ELECT | Supply | SMR12315 | 40658.78 | EA | 528564.14
189 | 8680 | Supply of Materials -- Supply of RS Joist girder Poles (150X150mm) | ELECT | Supply | SMR12302 | 59.25 | KG | 514290
190 | 4642 | Supply of Materials -- Supply of MS Channel 100X50mm | ELECT | Supply | SMR22745 | 57.45 | KGS | 266682.9
191 | 17 | Supply of Materials -- Supply of 11 kV 800 A Double break AB switch | ELECT | Supply | SMR12316 | 30847.46 | EA | 524406.82
192 | 3 | Supply of Materials -- Supply of 11 kV 400 A Double break AB switch | ELECT | Supply | SMR12317 | 18150 | EA | 54450
193 | 3045 | Supply of Materials -- Supply of MS Flat 75x8 mm | ELECT | Supply | SMR12321 | 56.42 | KG | 171798.9
194 | 2666 | Supply of Materials -- Supply of MS Flat 50x6 mm | ELECT | Supply | SMR12322 | 56.5 | KG | 150629
195 | 750 | Supply of Materials -- supply of RS Joist Poles (175X85mm) | ELECT | Supply | SMR12303 | 60.75 | KG | 45562.5
196 | 1 | Supply of Materials -- Supply of 11 kV 200 A Tilting type AB switch | ELECT | Supply | SMR12318 | 8991 | EA | 8991
197 | 1 | Supply of Materials -- Supply of 11KV HG fuse set for station transformer | ELECT | Supply | SMR12324 | 1974 | EA | 1974
198 | 1 | Supply of LT Distribution Box (SMC) | ELECT | Supply | SMR25200 | 7797 | EA | 7797
199 | 2 | Supply of 11KV 3x185 Heat Shble O/d End Term Kit | ELECT | Supply | SMR25201 | 1182.97 | EA | 2365.94
200 | 40 | Supply of XLPE Cable 1 C 150 sqmm | ELECT | Supply | SMR25203 | 114.83 | M | 4593.2
201 | 100 | Supply of XLPE Cable 3 1/2 C 185 sqmm | ELECT | Supply | SMR25204 | 547 | M | 54700
202 | 1 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc -- Erection of 11 KV HG Fuse set including earthing | ELECT | labour | SWR10395 | 740.52 | SET | 740.52
203 | 2 | survey line&cabl inc peg mark&tree clear | ELECT | Labour | SWR22092 | 765 | KM | 1530
204 | 14 | Load-11/33KV XLPE UG Cable for all sizes | ELECT | Labour | SWR11230 | 1024 | DR | 14336
205 | 7 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELECT | Labour | SWR11861 | 3299.7 | EA | 23097.9
206 | 14 | Unload-11/33KV XLPE UG Cable for all sizes | ELECT | Labour | SWR11231 | 1024 | DR | 14336
207 | 1800 | Excavation & laying of UG Cable (Double Run) Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, Along the CC / BT multi layer road requiring compressor-33 KV 3x400 Sqmm Cable | ELECT | Labour | SWR11980 | 1388.84 | M | 2499912
208 | 200 | Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, Across the CC/ BT road crossing multi layer road requiring compressor (excluding the cost of Hume pipe)-33 KV 3x400 Sqmm Cable | ELECT | Labour | SWR11988 | 1587.07 | M | 317414
209 | 2000 | Laying of 2nd cable in excavated trench | ELECT | Labour | SWR10988 | 204.1 | M | 408200
210 | 20 | S&E-Smart RFID marker | ELECT | Labour | SWR25089 | 2745 | EA | 54900
211 | 14 | UG Cables Joints 33 KV 3x400 Sqmm Cable Straight through joint 33kv 3x400 xlpe | ELECT | Labour | SWR10382 | 5700.78 | EA | 79810.92
212 | 1000 | Supply of 6" B class GI pipe | ELECT | Supply | SMR40081 | 1044 | M | 1044000
213 | 300 | Cost of Pipes and slabs-supply of 6" DWC pipe | ELECT | Supply | SMR11610 | 1012 | M | 303600
214 | 400 | Cost of Pipes and slabs-Suppy of Hume pipe 9" size | ELECT | Supply | SMR40001 | 125 | M | 50000
215 | 12 | Making of Outdoor/Indoor End Making 33 KV 3x400 Sqmm Cable Out Door/Indoor end termination TerminationOD/Idoor end termination 33kv 3x400 xlpe | ELECT | Labour | SWR10387 | 2764.76 | EA | 33177.12
216 | 60 | Excavation & laying of UG Cable (Double Run) Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-33 KV 3x400 Sqmm Cable | ELECT | Labour | SWR12004 | 323.85 | M | 19431
217 | 2000 | Hard Rock Cutting-11KV-Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours. | ELECT | Labour | SWR21903 | 30 | M | 60000
218 | 14 | Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters , CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | ELECT | Supply | SMR40085 | 484 | EA | 6776
219 | 3 | Erection of AB Switch and aligment complete Erection of 33 KV AB Switch including alignment and earthing | ELECT | Labour | SWR10392 | 4500 | EA | 13500
220 | 3 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | ELECT | Labour | SWR12331 | 146.63 | EA | 439.89
221 | 3 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Note:-The requirement of 2nd coat is to be justified by the concerned Divisional Engineer /Executive Engineer before execution of this work Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | ELECT | Labour | SWR10881 | 142 | EA | 426
222 | 12 | Fabrication of poles-Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | ELECT | Labour | SWR10642 | 512.55 | EA | 6150.6
223 | 18 | Painting of poles-Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | ELECT | Labour | SWR10640 | 1132 | EA | 20376
224 | 12 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M Ex of Hard pit w/o blast 0.75X0.9X1.95M | ELECT | Labour | SWR11040 | 990.68 | EA | 11888.16
225 | 3 | Assembly and erection of Structure as per specification which includes fixing of top channels and cross bracings, transport of all materials from road side to the location, earthing, back filling with earth ramming etc excluding pit excavation and concreting-33 KV DP Structure with 175x85/150x75mm RS joist | ELECT | Labour | SWR11276 | 5670 | SET | 17010
226 | 6 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-RS Joists 150x75/175 x 85 mm | ELECT | Labour | SWR10346 | 1934 | EA | 11604
227 | 155 | Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) Earthing for raisers of SS Flat 50x6 mm. | ELECT | Labour | SWR10919 | 41 | RMT | 6355
228 | 11.282 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELECT | Labour | SWR10356 | 6579 | M3 | 74224.28
229 | 0.37 | Mass Concreting for pole-Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | ELECT | Labour | SWR11890 | 3893 | M3 | 1440.41
230 | 0.975 | Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to theRS-Joist poles excluding cost of Mild Steel and transportcharges to substation site, including erection. Fabrication of struc.with welding. | ELECT | Labour | SWR10869 | 3426 | TO | 3340.35
231 | 6 | Supply of earthing pipe with materials-Supply of CI eath pipe with 80mm dia,2.0 M Length | ELECT | Supply | SMR11483 | 2789 | EA | 16734
232 | 6 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | ELECT | Labour | SWR10357 | 1234.2 | EA | 7405.2
233 | 6 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINES-Providing of RCC collar | ELECT | Labour | SWR10359 | 386 | EA | 2316
234 | 3 | Painting of poles-Painting of feeder name on support including cost of paint | ELECT | Labour | SWR12101 | 53 | EA | 159
235 | 30 | Supply of earthing pipe with materials S-GI Bolts & Nuts,Washers etc., | ELECT | Supply | SMR11488 | 117.5 | KG | 3525
236 | 12 | UG Cables Joints : Making of Outdoor/Indoor End Termination -- Supply 33KV 3x400Sqmm Outdoor | ELECT | supply | SMR22222 | 4554 | EA | 54648
237 | 14 | UG Cables Joints : Making of Straight through joints -- Supply of 33KV 3x400SQmm Straight Through Joint Kit | ELECT | supply | SMR22223 | 24151 | EA | 338114
238 | 3 | Supply of Materials -- Supply of 33 kV 800 A Double break AB switch | ELECT | Supply | SMR12315 | 40658.78 | EA | 121976.34
239 | 4500 | Supply of Materials -- supply of RS Joist Poles (175X85mm) | ELECT | Supply | SMR12303 | 60.75 | KG | 273375
240 | 370 | Supply of Materials -- Supply of MS Flat 50x6 mm | ELECT | Supply | SMR12322 | 56.5 | KG | 20905
241 | 975 | Supply of Materials -- Supply of MS Channel 100X50mm | ELECT | Supply | SMR22745 | 57.45 | KGS | 56013.75
242 | 12 | Fabrication of poles: Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | ELECT | labour | SWR10642 | 512.55 | EA | 6150.6
243 | 80 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M Ex of Hard pit w/o blast 0.75X0.9X1.95M | ELECT | Labour | SWR11040 | 990.68 | EA | 79254.4
244 | 80 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | ELECT | Labour | SWR11039 | 928 | EA | 74240
245 | 24 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-Stud Poles 0.6 M x 0.9 M x 1.5 M (0.81 cubmic meter) | ELECT | Labour | SWR11038 | 612 | EA | 14688
246 | 80 | Erection of OH Lines including AB Cable (33KV, 11KV, LT) Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Errection of 11 M long PSCC pole | ELECT | Labour | SWR10978 | 4336.85 | EA | 346948
247 | 80 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-9.1 M long PSCC pole | ELECT | Labour | SWR10343 | 2400 | EA | 192000
248 | 24 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-8.0 m long PSCC poles for Strut | ELECT | Labour | SWR21590 | 1500 | EA | 36000
249 | 57.41 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELECT | Labour | SWR10356 | 6579 | M3 | 377700.39
250 | 3 | LOADING of Conductor drums | ELECT | Labour | SWR10191 | 202 | EA | 606
251 | 2 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ELECT | Labour | SWR11861 | 3299.7 | EA | 6599.4
252 | 3 | UNLOADING of Conductor drums | ELECT | Labour | SWR10509 | 100 | EA | 300
253 | 5.5 | Paving out and stringing of conductor by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location-55 Sqmm Single Circuit (3 Conductors) | ELECT | Labour | SWR10365 | 9454.81 | KM | 52001.46
254 | 24 | Formation of Cut point for 11 KV Single Circuit line excluding pole erection and stays Formatn of Horiz Cut point for 11KV line | ELECT | Labour | SWR10653 | 1435.81 | EA | 34459.44
255 | 160 | Painting of poles-Numbering of poles incl. cost of paint | ELECT | Labour | SWR10378 | 32 | EA | 5120
256 | 6 | Painting of poles-Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | ELECT | Labour | SWR10640 | 1132 | EA | 6792
257 | 6 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M Ex of Hard pit w/o blast 0.75X0.9X1.95M | ELECT | Labour | SWR11040 | 990.68 | EA | 5944.08
258 | 6 | Erection of OH Lines including AB Cable (33KV, 11KV, LT)-Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Box pole 9/10/11 Mtr | ELECT | Labour | SWR11266 | 2643.83 | EA | 15862.98
259 | 160 | Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) Earthing for raisers of SS Flat 50x6 mm. | ELECT | Labour | SWR10919 | 41 | RMT | 6560
260 | 5.64 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ELECT | Labour | SWR10356 | 6579 | M3 | 37105.56
261 | 0.186 | Mass Concreting for pole-Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | ELECT | Labour | SWR11890 | 3893 | M3 | 724.1
262 | 0.23 | Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to theRS-Joist poles excluding cost of Mild Steel and transportcharges to substation site, including erection. Fabrication of struc.with welding. | ELECT | Labour | SWR10869 | 3426 | TO | 787.98
263 | 12 | Supply of earthing pipe with materials-Supply of CI eath pipe with 80mm dia,2.0 M Length | ELECT | Supply | SMR11483 | 2789 | EA | 33468
264 | 12 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | ELECT | Labour | SWR10357 | 1234.2 | EA | 14810.4
265 | 12 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINES-Providing of RCC collar | ELECT | Labour | SWR10359 | 386 | EA | 4632
266 | 6 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | ELECT | Labour | SWR10393 | 3200 | EA | 19200
267 | 6 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | ELECT | Labour | SWR12331 | 146.63 | EA | 879.78
268 | 6 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Note:-The requirement of 2nd coat is to be justified by the concerned Divisional Engineer /Executive Engineer before execution of this work Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | ELECT | Labour | SWR10881 | 142 | EA | 852
269 | 6 | Painting of poles-Painting of feeder name on support including cost of paint | ELECT | Labour | SWR12101 | 53 | EA | 318
270 | 40 | Supply of earthing pipe with materials S-GI Bolts & Nuts,Washers etc., | ELECT | Supply | SMR11488 | 117.5 | KG | 4700
271 | 80 | Supply of PSCC Pole 11Mtr 365KG | ELECT | supply | SMR25236 | 5399 | EA | 431920
272 | 80 | Supply of PSCC Pole 9.1Mtr 280KG | ELECT | supply | SMR25233 | 3109.41 | EA | 248752.8
273 | 24 | Supply of PSCC Pole 8Mtr 140KG | ELECT | supply | SMR25232 | 1580 | EA | 37920
274 | 456 | Supply of 33KV V X- Arm with MS Channel 75x40 | ELECT | supply | SMR25219 | 561 | EA | 255816
275 | 456 | Supply of 11KV Top Cleat for 9.1M(Vertical) | ELECT | supply | SMR25226 | 256 | EA | 116736
276 | 48 | Supply of 11KV Horizontal Cross Arm | ELECT | supply | SMR25223 | 528 | EA | 25344
277 | 504 |  | ELECT | supply | SMR25217 | 72 | SET | 36288
278 | 6 | Supply of Materials --- Supply of 11 kV 400 A Double break AB switch | ELECT | supply | SMR12317 | 18150 | EA | 108900
279 | 3000 | Supply of Materials -- supply of RS Joist Poles (175X85mm) | ELECT | supply | SMR12303 | 60.75 | KG | 182250
280 | 384 | Supply of Materials -- Supply of MS Flat 50x6 mm | ELECT | supply | SMR12322 | 56.5 | KG | 21696
281 | 150 | Supply of MS Angle 50x50x6 | ELECT | supply | SMR25206 | 58.15 | KG | 8722.5
282 | 80 | Supply of MS Channel 75x40 mm | ELECT | supply | SMR25205 | 58.45 | KG | 4676
283 | 12 | Fabrication of poles: Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | ELECT | labour | SWR10642 | 512.55 | EA | 6150.6
Electrical labour | [7 empty] | 15440196.49
Civil labour - WBS. No. S-1804-13-07-01-01-001
s.no | Estimate Quantity (only Figures) | Item Detailed Specification Description | Work Type eg. Earth Work, Electrical works. etc (upto 200 Characters) | Item Short Description (upto 100 Characters) | APSS / Morth Cl. Number (upto 200 Characters) | Rate (INR) (Upto 2 Decimals ) | UOM (upto 50 Characters) | Amount
1 | 32 | Leveliing the site by cutting and levelling with the help of JCB including cost,conveyance of all materials,hire chareges etc complete for finished item of work as directed by Engineer-in-charge. | Civil | Labour | SWR34179 | 2165 | Hrs | 69280
2 | 358.34 | Earth Work Mass Excavation (hard rock) to a depth as directed, in soils such as hard rock requiring blasting in prohibited area and all conditions such as dry, wet, slurry etc.and in dense or hard soils, disposal and depositing of excavated soil with intial lead of 10 mt and intial lift of 2m or as directed, including cost and conveyance of all materials, ramping and lifting of materials, and labour charges, hire charges of machinery, tools & plants, bailing of water ( either sub soil water, stoMts water, rain water, surface water or of any kind) if any at any stage of work until all works below ground level is finished to the satisfaction ,and from work such as shoring, timbering, strutting with required supports etc. for the work and removal of form work after completion of work etc all complete as directed by the engineer-incharge. | Civil | Labour | SWR33018 | 1440 | cum | 516009.6
3 | 294.6 | Earth work excavation in all type of ordinary soils red earth, Hard gravelly soils, earth mixed with sand and sandy soils etc., in all conditions such as slushy and dry with initial leads and lifts for foundations. Ordinary Soil | Civil | Labour | SWR33015 | 486 | cum | 143175.6
4 | 102.138 | PCC (1:4:8) using 40 mm metal with concrete Mixture. All work upto Plinth level including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete as directed by Engineer incharge of the work | Civil | Labour | SWR33028 | 4780 | cum | 488219.64
5 | 142.5 | Coursed Rubble stone CRS masonry 2nd sort with hard granite stones in cement mortar CM (1:6) for basement, including cost and conveyance of all materials, labour charges, curing, all leads and lifts, etc, complete for finished item of work. | Civil | Labour | SWR33041 | 4932 | cum | 702810
6 |  | RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge
7 | 1.09 | RCC M20 Grade Footing 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33098 | 9531 | cum | 10388.79
8 | 1.58 | RCC M20 Grade Column 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33100 | 13280 | cum | 20982.4
9 | 1.15 | RCC M20 Grade plinth beam 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33099 | 12402 | cum | 14262.3
10 | 0.458 | Reinforcement steel Supplying, Cutting, bending, binding, placing in position and tying reinforcement steel in all heights including cost and conveyance of steel and binding wire etc,. With all leads and lifts, labour charges, etc., complete for finished item of work. | Civil | Labour | SWR33144 | 70687 | MT | 32374.646
11 | 107.582 | Brick masonry in CM (1:6) for superstructure using well burnt country made second class bricks of approved quality including cost and conveyance of all materials curing, scaffolding with all leads and lifts in all heights etc., complete for finished item of work | Civil | Labour | SWR33068 | 8288 | cum | 891639.616
12 | 82.226 | PCC (1:2:4) using 20mm size well graded HBG metal for foundations, including cost, conveyance of all materials,labour all leads and lifts,consolidation and all operations, formwork as required, curing,etc. complete for finished item of work | Civil | Labour | SWR33030 | 6149 | cum | 505607.674
13 | 824.75 | Plastering with CM 2 coats, 20 mm thick, base coat in CM (1:6), 16 mm thick and top coat in CM (1:4), 4mm thick with Dubara sponze finishing including cost of all materials, seigniorage charges, excluding conveyance charges of materials and including all operational, incidental and labour charges for mixing mortar, laying rendering smooth and thread lining, curing, rounding off junctions of wall and slab etc., complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33163 | 564 | Sqm | 465159
14 | 824.75 | Painting with two coats of Plastic Emulsn paint over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33356 | 210 | Sqm | 173197.5
15 | 271.85 | Painting with two coats of Surya Cem paint over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33329 | 85 | sqm | 23107.25
16 | 650 | Supplying and fixing Structural Steel angles channal etc.Manufacturing, Supplying and fixing of MS grill for (Gate and raillings) of approved design as per drawings, including cost and conveyance of all materials, labour charges etc.,complete for finished item of work as directed by the Engineer- in-charge. | Civil | Labour | SWR33145 | 128 | Kgs | 83200
17 | 3 | Supply and Fixng of MS Name Board including cost & conveyance of all materials,labour charges etc complete for finished item of work. | Civil | Labour | SWR33421 | 4326 | sqm | 12978
18 | 1 | Geophysical Investgation charges for water point by Geologist | Civil | Labour | SWR33608 | 5000 | EA | 5000
19 |  | Drilling of 165mm bore well with machine rig including deployment and hire charges of rig and other machinery and equipment labour charges , measuring the yeild of borewell including cost and conveyance etc complete
20 | 90 | Drill-165mm Bore Well 0 to 90 | Civil | Labour | SWR33609 | 336 | M | 30240
21 | 30 | Drill-165mm Bore Well 90M to 120M | Civil | Labour | SWR34830 | 369 | M | 11070
22 | 30 | Drill-165mm Bore Well 120M to 150M | Civil | Labour | SWR34831 | 394 | M | 11820
23 | 30 | Drill-165mm Bore Well 150M to 180M | Civil | Labour | SWR34832 | 492 | M | 14760
24 | 30 | Drill-165mm Bore Well 180M to 210M | Civil | Labour | SWR34833 | 623 | M | 18690
25 | 30 | Drill-165mm Bore Well 210M to 240M | Civil | Labour | SWR34834 | 754 | M | 22620
26 | 30 | Drill-165mm Bore Well 240M to 270M | Civil | Labour | SWR34835 | 918 | M | 27540
27 | 150 | Drill-165mm Bore Well 270M and above | Civil | Labour | SWR34836 | 1082 | M | 162300
28 | 40 | Supply and fixing of 160mm dia PVC casing of A class 6Kg point pressure including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR33611 | 883 | M | 35320
29 | 1 | Supply and erecting, ISI mark submersible 5.0 HP, three Phase 30 stages pumpset suitable for 106/156mm dia borewell including cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33640 | 48007 | EA | 48007
30 | 370 | Supply and fixing of HDPE pipe 40mm dia of 16Kg/cm2 including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR34410 | 180 | M | 66600
31 | 1 | Supply and erecting D.O.L Starter 415V ,3 phase,50Hz with SS enclouserincluding cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33645 | 7854 | EA | 7854
32 | 450 | Supply of 3 Core 2.5 Sqmm Flat Copper cable of ISI for Submersible Motors of makes Finolex / Polycab / Gold Medal / Million / Payal / Sun Light / Power Flex / Fortune Art | Civil | Labour | SWR33641 | 192 | M | 86400
33 | 6 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-28.60mm OD Pipe - SDR 11 | Civil | Labour | SWR34363 | 410 | M | 2460
34 | 1 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type - 25mm NB Size | Civil | Labour | SWR34346 | 466 | EA | 466
35 | 72.73 | Earth work excavation in all type of ordinary soils red earth, Hard gravelly soils, earth mixed with sand and sandy soils etc., in all conditions such as slushy and dry with initial leads and lifts for foundations. | Civil | Labour | SWR33015 | 486 | Cum | 35346.78
36 | 39.53 | PCC (1:4:8) using 40mm HBG metal for foundations and leveling course, including cost and conveyance of all materials, labour all leads and lifts, consolidation and all operations, formwork as required, curing, etc. complete for finished item w | Civil | Labour | SWR33028 | 4780 | Cum | 188953.4
37 | 27.37 | CRS Coursed Rubble Stone masonry 2nd sort with hard granite stones in cement mortar (1:6) for basement, including cost and conveyance of all materials, labour charges, curing, all leads and lifts, etc, complete for finished item of work. | Civil | Labour | SWR33041 | 4932 | Cum | 134988.84
38 | 133.29 | Supplying and filling the substation site with borrowed gravel, watering, ramming, thoroughly complying with the standard specification. | Civil | Labour | SWR33052 | 309 | Cum | 41186.61
39 |  | 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge
40 | 5.346 | a) RCC M20 Grade Footings 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33098 | 9531 | Cum | 50952.726
41 | 3.42 | b)RCC M20 Grade Columns 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33100 | 13280 | Cum | 45417.6
42 | 4.03 | c)RCC M20 Grade Plinth Beams 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33099 | 12402 | Cum | 49980.06
43 | 3.55 | D) RCC M20 Grade Roof Beams 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33121 | 12318 | Cum | 43728.9
44 | 0.58 | e) RCC M20 Grade Lintels 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33107 | 13110 | Cum | 7603.8
45 | 2.7 | f) RCC M20 Grade Sunshades 600mm wide and 75mm thick 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33114 | 1379 | Sqm | 3723.3
46 | 19.206 | g) RCC M20 Grade Roof Slab 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33128 | 10906 | Cum | 209460.636
47 | 4.55 | reinforcement steel Supplying, Cutting, bending, binding, placing in position and tying reinforcement steel in all heights including cost and conveyance of steel and binding wire etc,. With all leads and lifts, labour charges, etc., complete for finished item of work. | Civil | Labour | SWR33144 | 70687 | MT | 321625.85
48 | 59.32 | Brick masonry in CM (1:6) for superstructure using well burnt country made second class bricks of approved quality including cost and conveyance of all materials curing, scaffolding with all leads and lifts in all heights etc., complete for fin | Civil | Labour | SWR33068 | 8288 | Cum | 491644.16
49 | 536.48 | Plastering with CM 2 coats, 20 mm thick, base coat in CM (1:6), 16 mm thick and top coat in CM (1:4), 4mm thick with Dubara sponze finishing including cost of all materials, seigniorage charges, excluding conveyance charges of materials and including all operational, incidental and labour charges for mixing mortar, laying rendering smooth and thread lining, curing, rounding off junctions of wall and slab etc., complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33163 | 564 | Sqm | 302574.72
50 | 85.68 | Providing Structural steel tube box type 60x40x4mm thick including cost and conveyance of all materials, labour charges,curing etc. complete for finished item of work and as directed by the engineer-in-charge. | Civil | Labour | SWR33146 | 147 | Kgs | 12594.96
51 | 18 | Providing Roofing with Trapezoidal/Galvalume Sheet including cost and conveyance of all materials, labour charges,curing etc. complete for finished item of work and as directed by the engineer-in-charge. | Civil | Labour | SWR33402 | 600 | Sqm | 10800
52 | 18.9 | Providing Design R.C.M. drop wall of 40mm thickness with cm 1:2 and 6mm dia MS bars at 150mm both ways and chicken mesh in two coats 20mm thick each plastering including cost and conveyance of all materials with leads and lifts, scaffolding and curing, labo | Civil | Labour | SWR33203 | 3116 | Sqm | 58892.4
53 | 12.24 | Supply and fixing of MS ornamental safety grill of approved design including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33310 | 2990 | sqm | 36597.6
54 | 5.91 | Supply and fixing of doors with the MT Wood frames the door shall be made well seasoned mt wood of cross section 100x75mm. The shutter shall be made isi mark flushed door with decolam sheets pasted on both sides with PVC beading 40mm width all round.Frame shall be painted with two coats of synthetic enamel paint of approved color over one coat of primer over luppum with spary with 3 no 150mm brass hinges 1 no brass door stoper, 1 no 250mm brass aldrops. 2 no 300 mm aluminium tower bolts, 2 no 150mm brass fancy door handlers, 1 no keyless lockset with cp handel. The quoted rate shall include cost and conveyance of the meterials, fixig, labour carges, tools, handles,locking arrangementts and other fixtures & fittings for finished item work as directed by the Engineer - in- charge. | Civil | Labour | SWR33264 | 7314 | Sqm | 43225.74
55 | 20.25 | Raised pointing to the exposed surfaces of CRS masonry in cm 1:3 prop. including cost and conveyance of all materials, labour charges, all leads and lifts curing etc, complete for finished item of work. | Civil | Labour | SWR33184 | 125 | sqm | 2531.25
56 | 8.64 | Supplying and fixing Aluminium sliding windows with grill and fixed glass panels using anodised aluminium extruded sections of mat finish for frames and mullions made from approved aluminium sections 62x32x1.2mm at 0.73kg/Rm providing 5mm plain glass fix | Civil | Labour | SWR33277 | 3623 | sqm | 31302.72
57 | 16.56 | Supply and laying of Ceramic floor over of CM 1:3 20 mm thick including required materials and labour charges etc complete for item of work | Civil | Labour | SWR33224 | 914 | Sqm | 15135.84
58 | 121.92 | Flooring with double machine polished and hand cut Tandur blue stone 20mm thick of approved colour, quality and of minimum of 300x300mm size over a bed of cement mortar 1:3 20mm thick including cost of all materials, with all leads and lifts jointing and | Civil | Labour | SWR33219 | 788 | Sqm | 96072.96
59 | 6.74 | Supply and fixing of 4" high skirting of shabad stone to the walls including cost and conveyance of all materials, labour etc for finished item of work. | Civil | Labour | SWR33236 | 877 | Sqm | 5910.98
60 | 243.69 | Painting with two coats of OBD over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials labour charges etc., complete for finished item of work. | Civil | Labour | SWR33333 | 146 | Sqm | 35578.74
61 | 414.315 | Painting with two coats of Plastic emulsn paint 2 coat of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33356 | 210 | Sqm | 87006.15
62 | 129.92 | Providing impervious coat over RCC roof slab to requried slopes with 20mm thick in CM 1:3 mixed with approved brand of water proffing compound inclding cost and conveyance of all materials, labour charges, curing, rounding off junctions of wall and slab, all leads and lifts, etc . complete for finished item of work as directed by the Engineer - in - charge. | Civil | Labour | SWR33156 | 587 | sqm | 76263.04
63 | 60 | Supply & fixing of 25mm dia 2mm thick surface P.V.C. pipe (ISI MARK) Concealed in wall with all required accessories including masonary work and labour charges etc.complete. | Civil | Labour | SWR33441 | 108 | M | 6480
64 | 1 | Supply & fixing TPNDB Distribution board with IP-42 protection (Metal Door)suitable for 3 phase ELCB/RCCB/FP Isolator as incomer and 10kA SP MCBs as out going including internal connection and labour charges for surface / flush mounting etc Complete. | Civil | Labour | SWR33526 | 11353 | EA | 11353
65 | 10 | Supply & fixing Flush type of 6A 3 pin wall plug socket with 6A switch control on a common switch board with earth continuity including wire leads,earth connection along with all labour charges etc., complete | Civil | Labour | SWR33468 | 166 | EA | 1660
66 | 6 | Supply & fixing Flush type of 16A 3 pin and 6A 3pin plug Flush type socket with indicator lamp and 16Amps fuse unit and 16Amps switch control (5 in one )duly recessed in wall with wooden deep box of 6'' x 8'' x 2 1/2'' size covered with hylam sheet earth connection and all labour charges etc., complete on wall. | Civil | Labour | SWR33470 | 449 | EA | 2694
67 | 24 | Supply and Fixing of modular switch, LP,FP,EFP,Wiring with 2 runs of 14/0.3mm (1.0 sq.mm)Fire Retardant (FR) P.V.C. insulated flexible copper cable (ISI MARK) in existing pipe with 6A Flush type Switch,ceiling rose and 3mm thick hylam sheet covering to switch control box including all labour charges etc., complete for light points, bell , fan and exhaust fan points in Non-Residential Buildings. | Civil | Labour | SWR33457 | 676 | EA | 16224
68 | 12 | Supply & Fixing of 28W T5 fluorescent tube. | Civil | Labour | SWR33558 | 148 | EA | 1776
69 | 1 | Supply of 12" (300mm)ISI, 900 RPM light duty exhaust fan with metallic blades with Mark of makes Crompton / Bajaj / Havells / Orient. | Civil | Labour | SWR33571 | 2192 | EA | 2192
70 | 180 | Supply and run of 2 of 22/0.3mm (1.5 sq.mm) (FR) P.V.C. insulated flexible copper cable in existing pipe for mains including all labour charges complete. | Civil | Labour | SWR33496 | 75 | M | 13500
71 | 180 | Supply and run of 2 of 36/0.3mm (2.5 sq.mm) FR P.V.C. insulated flexible copper cable in existing pipe for mains including all labour charges complete. | Civil | Labour | SWR33497 | 103 | M | 18540
72 | 12 | Supply & fixing of batten holder /slanting holder in lieu of ceiling rose of light point complete with all connection and all labour charges with 40W bulb (for new installation). | Civil | Labour | SWR33484 | 141 | EA | 1692
73 | 4 | Supply & fixing of 1200mm (48'') sweep 230v,A.C 50 Hz.Ceiling fan with 3 Blades and double ball bearings with all standared accessories. | Civil | Labour | SWR33563 | 2277 | EA | 9108
74 | 4 | Supply & fixing of Electronic Regulator for ceiling fans 900/1200/1400mm sweep including cost of material, Electrical charges complete for finished item of work | Civil | Labour | SWR33564 | 589 | EA | 2356
75 | 1 | Providing independent EARTHING by excavating a trench to a depth of 2.1M in all solid,as per size specified in the Data,using 40mm dia 'B' class GI pipe of 2.5 Mtrs length with necessary accessories with hume pipe ring duly providing staggered holes including filling with equal proportion of salt and Charcoal in layers and all labour charges etc., compiete for small quarters. | Civil | Labour | SWR33596 | 5345 | EA | 5345
76 | 35 | Supplying, laying, jointing and testing 101.6 mm SWG SP-1 pipes of ISI make conforming to ISI 651 & 4127 with airtight cement joints in CM 1.5:1 prop. Including excavation of trenches and socket pits in any soil (except rock requiring blasting) up to 1524 mm(5'0") depth and refilling with watering and tamping. | Civil | Labour | SWR34281 | 755 | M | 26425
77 | 3 | Constructing 904.0 mm (3#0#) dia brick masonry inspection chamber as per IS - 4111: Part-1:1986 with cement mortar (1:6) prop using 2nd Class Clay Bricks of 225 mm thick from approved source having a minimum crushing strength of 5 N/sq.mm including plastering with cement mortar 1:3 prop; ½# thick both inside and outside fitted with 20# dia RCC manhole covers and frames including excavating pits up to a depth of 904 mm (3'-0") in all sorts of soils (excluding rock) and laying cement concrete (1:4:8) 150 mm thick using 40 mm HBG Metal and P.C.C. 1:2:4 benching and channel 100 mm thick as per Standard specification and including cost and conveyance of all materials like cement, sand, bricks, water etc., to site, cost of seigniorage charges on all materials and all incidental and operational, labour charges like mixing cement mortar, constructing masonry, lift charges, curing etc., complete for finished item of work as per Standard specification. | Civil | Labour | SWR34296 | 8766 | EA | 26298
78 | 4 | Supply & fixing of 110 mm dia - Door Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34381 | 128 | EA | 512
79 | 4 | Supply & fixing of 110 mm dia - Plain Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34380 | 100 | EA | 400
80 | 12 | Supply & fixing of 110 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand | Civil | Labour | SWR34377 | 462 | M | 5544
81 | 18 | Supply & fixing of 90 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand | Civil | Labour | SWR34378 | 410 | M | 7380
82 | 3 | Supplying & fixing 150 mm x 100 mm SWG gully traps conforming to ISI 651 & 4127 with C.I Grating & Cost. Brick masonry in CM 1:6 prop. Intermediate chamber and fitted with 304.8 mm x 288.6mm (12"x9") C.I Frame and hinged cover | Civil | Labour | SWR34286 | 767 | EA | 2301
83 | 1 | Supplying and Fixing of European Water Closet of 1st Quality | Civil | Labour | SWR34314 | 2228 | EA | 2228
84 | 6 | Supply & fixing 15 mm angle stop cock Indian make 400 grams Seiko/ Senior/ Nice/ Senior/ Nice or equivalent | Civil | Labour | SWR34328 | 721 | EA | 4326
85 | 4 | S&F 15 mm N.P bib tap Indian make 400 grams full turn Seiko/ Senior/ Nice or equivalent | Civil | Labour | SWR34329 | 296 | EA | 1184
86 | 1 | Supplying & Fixing Indian make Flat Back Wash Hand Basin (HSW/Parryware/ Neycer) 1st quality conforming to IS:2556-Part-4:1972 with waste fittings like rubber plug, chain, 32 mm nominal size C.P. Fitting with parallel pipe thread conforming to IS:2963-1979 and fitted with 15 mm nominal bore Chromium Plated Pillar Tap of 1st quality Indian make 400 grams Seiko/ Senior/ Nice/ Esso or equivalent complete with standard CI brackets including wooden block: 550 x 400 mm - Single C.P. Pillar cock | Civil | Labour | SWR34316 | 1717 | EA | 1717
87 | 2 | Supply & fixing 38.1 mm C.P waste coupling Half or Full Thread 1st Quality Indian make Parryware or equivalent | Civil | Labour | SWR34428 | 309 | EA | 618
88 | 2 | Supply & fixing of 4" (101.6 mm ) Nahany Trap ( Without Jali with inlet)UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34387 | 134 | EA | 268
89 | 1000 | Providing & Placing on Terrace (at all floor levels) polyethylene water storage tank with Double layer approved brand & manufacture with cover and suitable locking arrangement & making necessary holes for inlet & outlets and over flow pipes but with NECESSARY fittings & base support for tanks | Civil | Labour | SWR34375 | 10 | L | 10000
90 | 2 | Supply & fixing 31.75 mm dia PVC flexible waste pipe of 914.4 mm length of Ist quality | Civil | Labour | SWR34426 | 33 | EA | 66
91 | 45 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)- 15.90mm OD Pipe - SDR 11 | Civil | Labour | SWR34361 | 239 | M | 10755
92 | 40 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-22.20mm OD Pipe - SDR 11 | Civil | Labour | SWR34362 | 313 | M | 12520
93 | 65 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-28.60mm OD Pipe - SDR 11 | Civil | Labour | SWR34363 | 410 | M | 26650
94 | 4 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type - 25mm NB Size | Civil | Labour | SWR34346 | 466 | EA | 1864
95 | 4 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type -20mm NB Size | Civil | Labour | SWR34345 | 331 | EA | 1324
96 | 1 | Supply & fixing 25.4 mm dia & 609.6 mm long aluminium anodized towel rod with brackets and aluminium screws | Civil | Labour | SWR34430 | 489 | EA | 489
97 | 85.51 | Earth work excavation in all type of Ordinary soils red earth, Hard gravelly soils, earth mixed with sand and sandy soils etc., in all conditions such as slushy and dry with initial leads and lifts for foundations. Ordinary Soil | Civil | Labour | SWR33015 | 486 | cum | 41557.86
98 | 18.91 | PCC (1:4:8) using 40mm HBG metal for foundations and leveling course, including cost and conveyance of all materials, labour all leads and lifts, consolidation and all operations, formwork as required, curing, etc. complete for finished item w | Civil | Labour | SWR33028 | 4780 | cum | 90389.8
99 | 91.8 | Coursed Rubble stone masonry (CRS) 2nd sort with hard granite stones in cement mortar (1:6) for basement, including cost and conveyance of all materials, labour charges, curing, all leads and lifts, etc, complete for finished item of work. | Civil | Labour | SWR33041 | 4932 | cum | 452757.6
100 | 36 | PCC (1:3:6) using 40mm HBG metal for foundations and leveling course, including cost and conveyance of all materials, labour all leads and lifts, consolidation and all operations, formwork as required, curing, etc. complete for finished item w | Civil | Labour | SWR33029 | 5070 | cum | 182520
101 | 108 | Raised pointing to the exposed surfaces of CRS masonry in cm 1:3 prop. including cost and conveyance of all materials, labour charges, all leads and lifts curing etc, complete for finished item of work. | Civil | Labour | SWR33184 | 125 | sq.mm | 13500
102 | 787.5 | Supplying and filling the substation site with borrowed gravel, watering, ramming, thoroughly complying with the standard specification. | Civil | Labour | SWR33052 | 309 | cum | 243337.5
103 | 88.8 | Plastering with CM 2 coats, 20 mm thick, base coat in CM (1:6), 16 mm thick and top coat in CM (1:4), 4mm thick with Dubara sponze finishing including cost of all materials, seigniorage charges, excluding conveyance charges of materials and including all operational, incidental and labour charges for mixing mortar, laying rendering smooth and thread lining, curing, rounding off junctions of wall and slab etc., complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33163 | 564 | sq.mm | 50083.2
104 | 200.85 | Painting with two coats of Surya Cem paint over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33329 | 85 | sq.mm | 17072.25
105 | 120 | Supply&Fabrication and fixing of Welded wire mesh ( 2" x 2") of 3mm dia. with ISMC (75x40x4.4mm) and Pheriperal frame of ISA(35x35x3mm) incldg cost& conveyance painting with synthetic enamil paint two coats over a coat of red oxide primer etc complete for finished item of work.. | Civil | Labour | SWR33403 | 2310 | sq.mm | 277200
106 | 160 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-22.20mm OD Pipe - SDR 11 | Civil | Labour | SWR34362 | 313 | M | 50080
107 | 30 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type - 25mm NB Size | Civil | Labour | SWR34346 | 466 | EA | 13980
108 | 1 | Providing Consultancy services for arranging contour surveying with total station incuding preparation of boundary and contour levels with 2 Nos. Hard copies and soft copies complete for finished items of work | Civil | Labour | SWR33427 | 5665 | EA | 5665
109 | 576.1145 | Seigniorage Charges - Sand | Civil | Labour | SWR34470 | 40 | cum | 23044.5804
110 | 1837.3831 | Seigniorage Charges - Metal | Civil | Labour | SWR34471 | 97.5 | cum | 179144.8483
111 | 920.79 | Seigniorage Charges - Gravel | Civil | Labour | SWR34472 | 30 | cum | 27623.7
112 | 60 | Supply and fixing of RCC fencing poles of size 0.1mx0.1mx1.8m (security fencing of sub station), including cost and conveyance of all labour, materials,and hire chareges etc complete for finished item of work. | Civil | Labour | Swr33405 | 1444 | EA | 86640
113 | 1200 | Supply and fixing of galvanised barded wire (1 horizantal & 2 cross strands. including cost and conveyance of all labour, materials,and hire chareges etc complete for finished item of work. | Civil | Labour | Swr33408 | 16 | M | 19200
Civil labour | [7 empty] | 9152224.1167
Electrical and Civil labour |  |  |  |  | 18% GST Rs. |  |  | 24592420.6068

## 16. Kuntloor
Name of the Work :- Erection of 33/11 kV Outdoor SS Kuntloor (Mother Dairy) inSaroornagar Circle withwith connected 33kV and 6 No.s new 11kV feeders at Kuntloor (Mother Dairy) in Abdullapurmet (M) in ECGH Division/ Masterpaln /RR Circle.
WBS Element :- S-1805-13-03-01-01-001
Sl No | Estimate Quantity | Description of item | Work Type | Item Short Description | APSS / Month Cl.NumberSSR 11 & 12 | Rate (INR) | UOM | AMOUNT
1 | 16 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | ElEC | labour | SWR11039 | 928 | EA | 14848
2 | 5.76 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ElEC | labour | SWR10868 | 6852 | TO | 39467.52
3 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ElEC | Supply | SMR40009 | 2181 | TO | 12562.56
4 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ElEC | labour | SWR10877 | 851 | TO | 4901.76
5 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ElEC | supply | SMR40010 | 1293 | TO | 7447.68
6 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ElEC | labour | SWR10879 | 482 | TO | 2776.32
7 | 5.76 | Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ElEC | labour | SWR10867 | 1470 | TO | 8467.2
8 | 16 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-R.S. Joists 150 x 150 mm | ElEC | labour | SWR10348 | 1952.61 | EA | 31241.76
9 | 17.758 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ElEC | labour | SWR10356 | 6579 | M3 | 116829.882
10 | 9.24 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ElEC | labour | SWR10862 | 373 | M2 | 3446.52
11 | 16 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | ElEC | labour | SWR11089 | 48 | EA | 768
12 | 4 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-8.0Mtrs PSCC Poles 0.76 M x 0.76M x 1.52M (2.6" x 2.6" x 5.0') 0.88 cum | ElEC | labour | SWR11037 | 793 | EA | 3172
13 | 1 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ElEC | labour | SWR10868 | 6852 | TO | 6852
14 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ElEC | supply | SMR40009 | 2181 | TO | 2181
15 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ElEC | labour | SWR10877 | 851 | TO | 851
16 | 1 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ElEC | supply | SMR40010 | 1293 | TO | 1293
17 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ElEC | labour | SWR10879 | 482 | TO | 482
18 | 1 | Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ElEC | labour | SWR10867 | 1470 | TO | 1470
19 | 4 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Box pole 12 Mtr | ElEC | labour | SWR11267 | 3901.37 | EA | 15605.48
20 | 2.65 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ElEC | labour | SWR10356 | 6579 | M3 | 17434.35
21 | 2.31 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ElEC | labour | SWR10862 | 373 | M2 | 861.63
22 | 4 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | ElEC | labour | SWR11089 | 48 | EA | 192
23 | 5.063 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ElEC | labour | SWR10868 | 6852 | TO | 34691.676
24 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ElEC | supply | SMR40009 | 2181 | TO | 11042.403
25 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ElEC | labour | SWR10877 | 851 | TO | 4308.613
26 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ElEC | supply | SMR40010 | 1293 | TO | 6546.459
27 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ElEC | labour | SWR10879 | 482 | TO | 2440.366
28 | 5.063 | Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ElEC | labour | SWR10867 | 1470 | TO | 7442.61
29 | 13 | Erection of AB Switch and aligment complete Erection of 33 KV AB Switch including alignment and earthing | ElEC | labour | SWR10392 | 4500 | EA | 58500
30 | 34 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Note:-The requirement of 2nd coat is to be justified by the concerned Divisional Engineer /Executive Engineer before execution of this work Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | ElEC | labour | SWR10881 | 142 | EA | 4828
31 | 34 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | ElEC | labour | SWR12331 | 146.63 | EA | 4985.42
32 | 6 | Loading of 33 KV CTs/ PTs | ElEC | labour | SWR10200 | 165 | EA | 990
33 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ElEC | labour | SWR11861 | 3299.7 | EA | 3299.7
34 | 6 | Un loading of 33 KV CTs/ PTs | ElEC | labour | SWR10518 | 128 | EA | 768
35 | 2 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33kv single phase PT s | ElEC | labour | SWR10401 | 1079 | SET | 2158
36 | 12 | Loading of 33 KV, 10 KA LAs Station typ | ElEC | labour | SWR10266 | 41 | EA | 492
37 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ElEC | labour | SWR11861 | 3299.7 | EA | 3299.7
38 | 12 | Un loading of 33 KV, 10 KA LAs Station type | ElEC | labour | SWR10584 | 35 | EA | 420
39 | 4 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33 KV LAS station/Line type including earthing | ElEC | labour | SWR10396 | 880 | SET | 3520
40 | 2 | Loading of 33 KV VCBs along with Panel boards | ElEC | labour | SWR10198 | 1024 | EA | 2048
41 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ElEC | labour | SWR11861 | 3299.7 | EA | 3299.7
42 | 2 | Un loading of 33 KV VCBs along with Panel boards | ElEC | labour | SWR10516 | 1044.48 | EA | 2088.96
43 | 12.584 | Excavate-Pit for 33KV VCB | ElEC | labour | SWR23224 | 331 | M3 | 4165.304
44 | 14.52 | Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x 1.8 x 0.75 cum for VCB Plinth | ElEC | labour | SWR20685 | 5160 | M3 | 74923.2
45 | 2 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33 KV VCB with Control Panel | ElEC | labour | SWR10460 | 12500 | EA | 25000
46 | 2 | Loading and unloading of PTR on constructed plinth-Loading of 8MVA PTR | ElEC | labour | SWR10613 | 5805.84 | EA | 11611.68
47 | 2 | Transport of Power transformers (0 to 100 KM) from one place to another place in GHMC Area.(excluding of loading & unloading )-8MVA power transformer | ElEC | labour | SWR10854 | 21945 | EA | 43890
48 | 2 | Loading and unloading of PTR on constructed plinth-Unloading of 8MVA PTR | ElEC | labour | SWR10627 | 5805.84 | EA | 11611.68
49 | 700 | S/o rail poles 90/105lb (250x2N) | ElEC | supply | SMR22718 | 47.27 | KG | 33089
50 | 14 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Rail pole 90 lbs | ElEC | labour | SWR10344 | 3510 | EA | 49140
51 | 2 | Erection of PTR on constructed plinth-Erection of 8 MVA PTR. | ElEC | labour | SWR21321 | 49480.2 | EA | 98960.4
52 | 0.436 | Extention of 33KV Bay at 132/33KV Sub-station-Zebra condutor | ElEC | supply | SMR24910 | 299369 | KM | 130524.884
53 | 30 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing | ElEC | supply | SMR11915 | 2055 | SET | 61650
54 | 30 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of I-Bolts | ElEC | supply | SMR22473 | 294 | EA | 8820
55 | 45 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 "to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating . Sup T clamp LM6 Al alloy of 12 mm, 800 A | ElEC | supply | SMR40011 | 299 | EA | 13455
56 | 6 | Bus stringing Hoisting of Insulators and hardware, stretching the conductor and stringing of 33 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bussection of 4.5mt) Hoisting post ins&hrd wr 1panther 33kv | ElEC | labour | SWR21240 | 781 | EA | 4686
57 | 84 | Stringing of bus with panther conductor including jumpering etc., complete to all the equipment in SS fixing to all clamps and equipment.(3 Conductors) | ElEC | labour | SWR10404 | 327.68 | M | 27525.12
58 | 30 | Bus stringing Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | ElEC | labour | SWR10884 | 224 | EA | 6720
59 | 75 | Labour for Fixing of all types of clamps | ElEC | labour | SWR10917 | 65 | EA | 4875
60 | 25 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | ElEC | labour | SWR11039 | 928 | EA | 23200
61 | 8.68 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ElEC | labour | SWR10868 | 6852 | TO | 59475.36
62 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ElEC | supply | SMR40009 | 2181 | TO | 18931.08
63 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ElEC | labour | SWR10877 | 851 | TO | 7386.68
64 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ElEC | supply | SMR40010 | 1293 | TO | 11223.24
65 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ElEC | labour | SWR10879 | 482 | TO | 4183.76
66 | 8.68 | Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ElEC | labour | SWR10867 | 1470 | TO | 12759.6
67 | 25 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-R.S. Joists 150 x 150 mm | ElEC | labour | SWR10348 | 1952.61 | EA | 48815.25
68 | 27.75 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ElEC | labour | SWR10356 | 6579 | M3 | 182567.25
69 | 17.91 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ElEC | labour | SWR10862 | 373 | M2 | 6680.43
70 | 25 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | ElEC | labour | SWR11089 | 48 | EA | 1200
71 | 4.642 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | ElEC | labour | SWR10868 | 6852 | TO | 31806.984
72 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ElEC | supply | SMR40009 | 2181 | TO | 10124.202
73 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ElEC | labour | SWR10877 | 851 | TO | 3950.342
74 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ElEC | supply | SMR40010 | 1293 | TO | 6002.106
75 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ElEC | labour | SWR10879 | 482 | TO | 2237.444
76 | 4.642 | Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | ElEC | labour | SWR10867 | 1470 | TO | 6823.74
77 | 17 | Erection of AB Switch and aligment complete-Erection of 11KV 800A double throw AB Switches | ElEC | labour | SWR21277 | 3500 | EA | 59500
78 | 3 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | ElEC | labour | SWR10393 | 3200 | EA | 9600
79 | 2 | Loading of 11 KV CT - PT Sets | ElEC | labour | SWR10201 | 190 | EA | 380
80 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ElEC | labour | SWR11861 | 3299.7 | EA | 3299.7
81 | 2 | Un loading of 11 KV CT - PT Sets | ElEC | labour | SWR10519 | 101 | EA | 202
82 | 2 | Erection of 11 KV three phase PTs | ElEC | labour | SWR10402 | 800 | SET | 1600
83 | 24 | Loading of 11 KV, 10 KA LAs Station type | ElEC | labour | SWR10264 | 32 | EA | 768
84 | 2 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ElEC | labour | SWR11861 | 3299.7 | EA | 6599.4
85 | 24 | Un loading of 11 KV, 10 KA LAs Station type | ElEC | labour | SWR10582 | 32 | EA | 768
86 | 2 | Erection of 11 KV LAS station type including earthing | ElEC | labour | SWR10397 | 559 | SET | 1118
87 | 6 | Erection of 11 KV LAS line type including earthing | ElEC | labour | SWR10398 | 505 | SET | 3030
88 | 8 | Loading of 11 KV VCBs along with Panel boards | ElEC | labour | SWR10199 | 1024 | EA | 8192
89 | 4 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ElEC | labour | SWR11861 | 3299.7 | EA | 13198.8
90 | 8 | Un Loading of 11 KV VCBs along with Panel boards | ElEC | labour | SWR10517 | 1044.48 | EA | 8355.84
91 | 41.6 | Excavate-Pit for 33KV VCB | ElEC | labour | SWR23224 | 331 | M3 | 13769.6
92 | 48 | Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x 1.8 x 0.75 cum for VCB Plinth | ElEC | labour | SWR20685 | 5160 | M3 | 247680
93 | 8 | Erection of 11 KV VCB with Control Panel | ElEC | labour | SWR10461 | 12000 | EA | 96000
94 | 12 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing | ElEC | supply | SMR11915 | 2055 | SET | 24660
95 | 12 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of I-Bolts | ElEC | supply | SMR22473 | 294 | EA | 3528
96 | 45 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 "to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating . Sup T clamp LM6 Al alloy of 12 mm, 800 A | ElEC | supply | SMR40011 | 299 | EA | 13455
97 | 2 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 11 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 3.5mt) Hoisting post ins&hrd wr 1panther 11kv | ElEC | labour | SWR21241 | 507 | EA | 1014
98 | 63 | Stringing of bus with panther conductor including jumpering etc., complete to all the equipment in SS fixing to all clamps and equipment.(3 Conductors) | ElEC | labour | SWR10404 | 327.68 | M | 20643.84
99 | 45 | Bus stringing Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | ElEC | labour | SWR10884 | 224 | EA | 10080
100 | 57 | Labour for Fixing of all types of clamps | ElEC | labour | SWR10917 | 65 | EA | 3705
101 | 584 | Laying of earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication 75x 8mm MS Flat / GI Flat. Laying of earth mat,excavation 75x 8mm | ElEC | labour | SWR10920 | 65 | RMT | 37960
102 | 1010 | Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) Earthing for raisers of SS Flat 50x6 mm. | ElEC | labour | SWR10919 | 41 | RMT | 41410
103 | 36 | Supply of earthing pipe with materials Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | ElEC | supply | SMR11482 | 3486 | EA | 125496
104 | 36 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | ElEC | labour | SWR10357 | 1234.2 | EA | 44431.2
105 | 36 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINES-Providing of RCC collar | ElEC | labour | SWR10359 | 386 | EA | 13896
106 | 2 | Supply of Copper Flexible jumper with 75 X 8 of length 250 mm at neutral of Power tranformer end and 50 X 6 of length 50mm two Nos at double neutral end duly brasing with flexible jumper of capacity of 5kA/3 sec for power transformer neutral. SupCU Flexi jumper for Power T/F Neutral | ElEC | supply | SMR40033 | 4725 | EA | 9450
107 | 2 | Providing of earthing with various types of earth electrodes-Providing of double earthing for neutral with flexible copper jumpers including arrangement by fixing M.S.Channel 100x50mm. | ElEC | labour | SWR11892 | 1323 | EA | 2646
108 | 4 | Loading of LT AB Cable 3X16+25 Sqmm | ElEC | labour | SWR11702 | 200 | DR | 800
109 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ElEC | labour | SWR11861 | 3299.7 | EA | 3299.7
110 | 4 | Un loading of LT AB Cable 3X16+25 Sqmm | ElEC | labour | SWR11713 | 204 | DR | 816
111 | 80 | Providing of control cable trench as per DATA-XII | ElEC | labour | SWR22093 | 3148 | RMT | 251840
112 | 3074 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends . Lay-4C/10C 2.5Sqmm Control Cable | ElEC | labour | SWR11879 | 27 | M | 82998
113 | 270 | Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per specification (including cost of ferrules, lugs and glands) | ElEC | labour | SWR12510 | 27 | EA | 7290
114 | 4 | Marshalling Box Supply of FRP PT Marshalling Box | ElEC | supply | SMR40048 | 4463 | EA | 17852
115 | 4 | Marshalling Box Erection of Marshalling boxes | ElEC | labour | SWR10940 | 374.85 | EA | 1499.4
116 | 1 | Loading of 220 V Batterry with charger | ElEC | labour | SWR11166 | 1612 | SET | 1612
117 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ElEC | labour | SWR11861 | 3299.7 | EA | 3299.7
118 | 1 | Un loading of 220 V Batterry with charger | ElEC | labour | SWR11147 | 1024 | SET | 1024
119 | 1 | Batteries-Erection of 220 V, 200 AH battery in complete shape fit for charging . Conventional lead acid | ElEC | labour | SWR12350 | 7666 | EA | 7666
120 | 1 | Control Panels Supply of DC Annunciation & relay panel for 10 feeder panel including the cost of LED Indiacation lamps, VAA auxilairy relays, Electronic Hooters complete as per specification. | ElEC | supply | SMR40044 | 42500 | EA | 42500
121 | 1 | Supply of AC Supply panel inluding providing of changeover switch, SFU, metering unit, 32 A three phase MCB, 16 A Single phase MCB complete as per specification. Supply of AC Supply panel complete | ElEC | supply | SMR40045 | 42000 | EA | 42000
122 | 2 | Fixing of AC/DC Panel and giving Connections to the protection equipment and Metering circuits as per the specification and standards. The 3 1/2 core 25 Sqmm power cable required from distribution box to AC/DC panel in the control room is also to be supply | ElEC | labour | SWR20025 | 7871.85 | SET | 15743.7
123 | 8 | Yard lightning-Supply of stepped tubular poles single way made of steel of length 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9 mm, 2.1 mtrs with outer dia 76.1 mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79 kgf as per IS 2713 | ElEC | supply | SMR40051 | 13913 | EA | 111304
124 | 8 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE/CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA /OSRAM /SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty S-90W LED fixture set | ElEC | supply | SMR11594 | 8200 | EA | 65600
125 | 8 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | ElEC | labour | SWR11039 | 928 | EA | 7424
126 | 8 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE / CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA/OSRAM/SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty-Erection of tubular poles | ElEC | labour | SWR10955 | 1379 | EA | 11032
127 | 5.27 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ElEC | labour | SWR10356 | 6579 | M3 | 34671.33
128 | 8 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE/CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA /OSRAM /SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty. Fixing of Metal halide lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5 GI pipe complete Fixing of LED/Metal halide complete. | ElEC | labour | SWR10956 | 1268 | EA | 10144
129 | 45 | Supply of HBG metal-Supply & spreading of 20mm machine crushed metal (HBG) including cost of conveneyance of all materials, labour charges etc complete for finished item of work and directed by the engineer incharge | ElEC | labour | SWR10860 | 2113 | M3 | 95085
130 | 2 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M Ex of Hard pit w/o blast 0.75X0.9X1.95M | ElEC | labour | SWR11040 | 990.68 | EA | 1981.36
131 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | ElEC | supply | SMR40009 | 2181 | TO | 1635.75
132 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | ElEC | labour | SWR10877 | 851 | TO | 638.25
133 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | ElEC | labour | SMR40010 | 1293 | TO | 969.75
134 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | ElEC | labour | SWR10879 | 482 | TO | 361.5
135 | 1 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Box pole 12 Mtr | ElEC | labour | SWR11267 | 3901.37 | EA | 3901.37
136 | 2.22 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ElEC | labour | SWR10356 | 6579 | M3 | 14605.38
137 | 1.16 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | ElEC | labour | SWR10862 | 373 | M2 | 432.68
138 | 2 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | ElEC | labour | SWR11089 | 48 | EA | 96
139 | 1 | Construction of DTR Plinth-RCC Column type DTR Plinth of size 1'X1'X10',topslab 4'x4'x6" & beam size 4'X8'X8" upto 160KVA | ElEC | labour | SWR21843 | 25967.57 | EA | 25967.57
140 | 1 | Loading of 50,63, 75 & 100 KVA DTR | ElEC | labour | SWR10195 | 350 | EA | 350
141 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ElEC | labour | SWR11861 | 3299.7 | EA | 3299.7
142 | 1 | Un loading of 50,63, 75 & 100 KVA DTR | ElEC | labour | SWR10513 | 280 | EA | 280
143 | 1 | Erection of DTR's including loading and Unloading DTR on the Structure/Plinth etc-Erection of 3 Phase DTRs 63,75 & 100 KVA | ElEC | labour | SWR20905 | 1650 | EA | 1650
144 | 1 | Erection of AB Switch and aligment complete Erection of 11KV 200A TT type AB Switch including fixing of cross angles and alignment complete | ElEC | labour | SWR20102 | 1813.49 | EA | 1813.49
145 | 1 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erect. of 11kv HG Fuseset incl earthing | ElEC | labour | SWR10395 | 740.52 | SET | 740.52
146 | 40 | Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.-In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road-11KV 3x185 Sqmm Cable | ElEC | labour | SWR11920 | 465.46 | M | 18618.4
147 | 20 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-11 KV 3x185 Sqmm Cable | ElEC | labour | SWR11956 | 126.23 | M | 2524.6
148 | 2 | UG Cables Joints Making of Outdoor/Indoor End Termination OD/Idoor end termination 11kv 3x185 xlpe | ElEC | labour | SWR10390 | 2370.63 | EA | 4741.26
149 | 1 | Erection of LT distribution box including laying of LT cable from distribution box to LT OH line and DTR to distribution box including earthing of distribution box and crimping of lugs connecting of jumpers etc | ElEC | labour | SWR10674 | 1594.67 | EA | 1594.67
150 | 85 | LAYING OF 33KV, 11KV UG CABLE Excavation & laying of UG Cable in Single Run Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road-LT 3 1/2 x 185 Sqmm Cable | ElEC | labour | SWR11923 | 377.63 | M | 32098.55
151 | 15 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-LT 3 1/2 x 185 Sqmm Cable | ElEC | labour | SWR11959 | 85.43 | M | 1281.45
152 | 2 | Supply & fixing of Oout Door/Indoor end termination LT 3 1/2 x 185 Sqmm Cable | ElEC | labour | SWR10765 | 968.9 | EA | 1937.8
153 | 1 | Supply and fixing of Substation board of size 3'x2.5' indicating the layout of switchyard Sup &fix of board ind Switchyard layout | ElEC | labour | SWR20032 | 1654 | EA | 1654
154 | 1 | Supply and fixing of safety instructions/Substation operation instruction board. Sup& fix safety inst/SS Op. inst board | ElEC | labour | SWR22090 | 2205 | EA | 2205
155 | 750 | Control Panels Supplying & fabrication erection of 6mm Checkerd plates as per the field conditions Supply,fabricati of 6mm Checkerd plates | ElEC | labour | SWR10873 | 83 | KG | 62250
156 | 1 | T & P Supply of Wall clock standard make | ElEC | supply | SMR40059 | 578 | EA | 578
157 | 1 | S-10ft Aluminium Ladder | ElEC | supply | SMR12378 | 1654 | EA | 1654
158 | 1 | Sup Alluminium Ladder for indoor works | ElEC | supply | SMR40062 | 4410 | EA | 4410
159 | 30 | T & P Painting of Name Plates for any equipmen | ElEC | labour | SWR10963 | 122 | EA | 3660
160 | 1 | T & P Supply of Taparia Tool kit of Size 20”x10”x15” with tier arrangements Tool box with locking arrangement & key containing (1) Double Ended fix Spanner sets, (Ribbed) 6 x 7, 8 x 9, 10 x 11, 12 x 13, 14 x 15, 16 x 17, 18 x19, 20 x 22, 21 x 23, 24 x 27, 25 x28, 30 x 32, (2) Double Ended Ring Spanners sets, 6 x 7 , 8 x 9, 10 x 11, 12 x 13, 14 x 15. 16 x 17 , 18 x 19, 20 x 22 , 21 x 23, 24 x 27, 25 x28, 30 x 32 mm, (3) Adjustable Spanner 305 mm length least maximum opening 35mm chrome, (4) Pipe Wrench Length 350 mm 14”, (5) Soft faced Hammer with suitable handle 2 lb, (6) Hacksaw frame with metal handle heavy duty for 12" hacksaw blade with High Speed blade, (7) Insulated Screw drivers Transparent Green Handle Set Length 6”, 8” & 12”, (8) Star Screw Driver Transparent Green Handle Length 6”, (9) Insulated Wire Cutter, (10) Insulated Cutting Plier Length 8” with cable stripper insulated with thick C. A. sleeve confirming to IS: 4378 - 1990, (11) Long Nose Plier insulated with thick C.A. sleeve generally confirming to IS:3552-1989, (12) Tester type screw driver (special with neon bulb) generally confirm to IS: 5579- 1985 Grade:II handle yellow/ green colour overall length 130 mm, (13) Insulated Crimping Plier of all Taparia make. SupTaparia Tool kit complete as per Spec | ElEC | supply | SMR40063 | 4925 | SET | 4925
161 | 1 | T & P Sup Rechargeable LED torch light of Standard make | ElEC | supply | SMR40064 | 1733 | EA | 1733
162 | 1 | T & P-Steel almarah(61/2 X 3ft) Godrej | ElEC | supply | SMR40061 | 9818 | EA | 9818
163 | 1 | T & P-Table (3x6ft) Godrej | ElEC | supply | SMR40057 | 6050 | EA | 6050
164 | 4 | T & P-S type chairs (Godrej) | ElEC | supply | SMR40058 | 924 | EA | 3696
165 | 1 | T & P Sup Angle racks(18x36.6inches) Godrej | ElEC | suppply | SMR40060 | 1733 | EA | 1733
166 | 1 | T & P Supply of Hack saw (12 inches) | ElEC | suppply | SMR40065 | 289 | EA | 289
167 | 4 | Sup Earth Rods (8ft) Screw & clamp type | ElEC | suppply | SMR40066 | 578 | EA | 2312
168 | 2 | Supply of Hand Gloves | ElEC | suppply | SMR40067 | 289 | SET | 578
169 | 12 | SupRubber mats( 6'x3')size fo indoorSS | ElEC | suppply | SMR40068 | 1386 | EA | 16632
170 | 1 | Biometric Time attendence System & Telecom Sup Stand basic cell phone with charger | ElEC | suppply | SMR40069 | 1386 | EA | 1386
171 | 14 | Supply of Danger boards with clamps | ElEC | suppply | SMR40070 | 116 | EA | 1624
172 | 2 | Fire bucket stand with 3 buckets (8 -10 ltr capacity) | ElEC | suppply | SMR40088 | 1386 | SET | 2772
173 | 2 | Room fire extinguisher (2 ltrs capacity) for control room | ElEC | Supply | SMR40089 | 4620 | EA | 9240
174 | 4 | Sup TrollyMounted Co2 (6.5Kgs) Cylinders(IS-2878) | ElEC | Supply | SMR40087 | 9240 | EA | 36960
175 | 6 | Supply of Safety Helmet of standard make | ElEC | Supply | SMR40071 | 231 | EA | 1386
176 | 8 | Supply of LC Boards | ElEC | Supply | SMR40072 | 116 | EA | 928
177 | 4 | Supply of Gum Boots (pair) | ElEC | Supply | SMR40073 | 693 | EA | 2772
178 | 1 | Supply of 5000v megger | ElEC | Supply | SMR40074 | 13860 | EA | 13860
179 | 1 | Supply of Earth megger (1000v) | ElEC | Supply | SMR40075 | 8085 | EA | 8085
180 | 1 | Supply of Digital clamp meter. | ElEC | Supply | SMR40076 | 2888 | EA | 2888
181 | 1 | Name board of the 33/11kV Sub-Station(As per Standard Specification) Sup 33/11kv S.S Permanent name board | ElEC | Supply | SMR40086 | 10238 | EA | 10238
182 | 800 | Supply of Hot dip galvanized/zinc coated bolts & nuts including spring washers, pack washers and flat washers etc. | ElEC | Supply | SMR12488 | 90 | KG | 72000
183 | 2 | Fabrication of poles-Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | ElEC | labour | SWR10642 | 512.55 | EA | 1025.1
184 | 1 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-RS Joists 150x75/175 x 85 mm | ElEC | labour | SWR10346 | 1934 | EA | 1934
185 | 5760 | S-Supply of RS Joist Grider Pole (150x150mm) | ElEC | supply | SMR12302 | 59.25 | KG | 341280
186 | 1000 | S-Supply of RS Joist Pole (175x85mm) | ElEC | supply | SMR12303 | 60.75 | KG | 60750
187 | 5063 | S- Supply of MS Channel 100x50mm | ElEC | supply | SMR22745 | 57.45 | KGS | 290869.35
188 | 13 | S-Supply of 33KV 800A DB Break AB Switch | ElEC | supply | SMR12315 | 40658.78 | EA | 528564.14
189 | 8680 | S-Supply of RS Joist Grider Pole (150x150mm) | ElEC | supply | SMR12302 | 59.25 | KG | 514290
190 | 4642 | S- Supply of MS Channel 100x50mm | ElEC | supply | SMR22745 | 57.45 | KGS | 266682.9
191 | 17 | S-Supply of 11KV 800A DB Break AB Switch | ElEC | supply | SMR12316 | 30847.46 | EA | 524406.82
192 | 3 | S-Supply of 11KV 400A DB Break AB Switch | ElEC | supply | SMR12317 | 18150 | EA | 54450
193 | 3045 | S-Supply of MS Flat 75x8mm | ElEC | supply | SMR12321 | 56.42 | KG | 171798.9
194 | 2666 | S-Supply of MS Flat 50x6mm | ElEC | supply | SMR12322 | 56.5 | KG | 150629
195 | 750 | S-Supply of RS Joist Pole (175x85mm) | ElEC | supply | SMR12303 | 60.75 | KG | 45562.5
196 | 1 | S-Supply of 11KV 200A Tilting Type AB Switch | ElEC | supply | SMR12318 | 8991 | EA | 8991
197 | 1 | S-Supply of 11KV HG FuseSet for StationTransformer | ElEC | supply | SMR12324 | 1974 | EA | 1974
198 | 1 | S-Supply of LT Distribution Box (SMC) | ElEC | supply | SMR25200 | 7797 | EA | 7797
199 | 2 | S-Supply of 11KV 3x185 Heat Shble O/d End Term Kit | ElEC | supply | SMR25201 | 1182.97 | EA | 2365.94
200 | 40 | S-Supply of LT XLPE Cable 1C 150 sqmm | ElEC | supply | SMR25203 | 114.83 | M | 4593.2
201 | 100 | S-LT XLPE Cable 3 1/2 C 185 sqmm | ElEC | supply | SMR25204 | 547 | M | 54700
202 | 8 | survey line&cabl inc peg mark&tree clear | ElEC | labour | SWR22092 | 765 | KM | 6120
203 | 25 | S-M+3 Tower GALV | ElEC | supply | SMR11683 | 140674.3 | EA | 3516857.5
204 | 25 | Supply of material for Extension of 3Mtrs for M+3 (Galvanized) S-Mat. for Extn of M+3 Tower by 3M GALV | ElEC | supply | SMR11684 | 28520.64 | EA | 713016
205 | 25 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-M-Type Tower (1.2M x 1.2M x 3.3M ) 4.752cum | ElEC | labour | SWR12090 | 3592.95 | EA | 89823.75
206 | 25 | Erect- M+3 Tower GALV | ElEC | labour | SWR11850 | 64576 | EA | 1614400
207 | 25 | Erect-Extn of 3M for M+3 Tower GALV | ElEC | labour | SWR11851 | 5168.95 | EA | 129223.75
208 | 8 | LOADING of Conductor drums | ElEC | labour | SWR10191 | 202 | EA | 1616
209 | 4 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ElEC | labour | SWR11861 | 3299.7 | EA | 13198.8
210 | 8 | UNLOADING of Conductor drums | ElEC | labour | SWR10509 | 100 | EA | 800
211 | 8 | Paving out and stringing of conductor by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location-100 Sqmm Single Circuit (3 Conductors) | ElEC | labour | SWR10366 | 13856.7 | KM | 110853.6
212 | 32 | Formation of Cut points-Formation of Cut point for 33 KV Single Circuit line excluding pole erection and stays | ElEC | labour | SWR10981 | 1791.12 | EA | 57315.84
213 | 130 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-12Mtrs/Spun Pole 0.92 M x 0.92M x 2.3M (3.0" x 3.0" x 7.6") | ElEC | labour | SWR11041 | 1466.25 | EA | 190612.5
214 | 130 | Fabrication of materials including 2 coats of Red oxide painting-Top insulator fittings with channel and flat | ElEC | labour | SWR10325 | 44 | EA | 5720
215 | 2 | Fabrication of materials including 2 coats of Red oxide painting-Strut clamps with 75 x 8 mm MS Flat | ElEC | labour | SWR11262 | 84 | EA | 168
216 | 130 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Spun poles 12.5 Mtrs / 12.9Mtrs PSCC | ElEC | labour | SWR10350 | 4521.66 | EA | 587815.8
217 | 20 | Excavation of pits in all soils except hard rock requiring blasting-Stud Poles 0.6 M x 0.9 M x 1.5 M | ElEC | labour | SWR10106 | 645 | EA | 12900
218 | 20 | Erection of OH Lines including AB Cable (33KV, 11KV, LT) Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Erec of 9.1 Mts PSCC poles for stuts | ElEC | labour | SWR11083 | 2400 | EA | 48000
219 | 224.9 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ElEC | labour | SWR10356 | 6579 | M3 | 1479617.1
220 | 16.2 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ElEC | labour | SWR10356 | 6579 | M3 | 106579.8
221 | 155 | Painting of poles-Numbering of poles incl. cost of paint | ElEC | labour | SWR10378 | 32 | EA | 4960
222 | 130 | Supply of earthing pipe with materials-Supply of GI wire No 8 | ElEC | supply | SMR11486 | 105 | KG | 13650
223 | 130 | Cost of Pipes and slabs-Supply of 2" B class GI pipe | ElEC | supply | SMR40079 | 307 | M | 39910
224 | 130 | Supply of earthing pipe with materials S-GI Bolts & Nuts,Washers etc., | ElEC | supply | SMR11488 | 117.5 | KG | 15275
225 | 4 | survey line&cabl inc peg mark&tree clear | ElEC | labour | SWR22092 | 765 | KM | 3060
226 | 27 | Load-11/33KV XLPE UG Cable for all sizes | ElEC | labour | SWR11230 | 1024 | DR | 27648
227 | 14 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ElEC | labour | SWR11861 | 3299.7 | EA | 46195.8
228 | 27 | Unload-11/33KV XLPE UG Cable for all sizes | ElEC | labour | SWR11231 | 1024 | DR | 27648
229 | 2000 | Excavation & laying of UG Cable (Double Run) Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil/CC-33 KV 3x400 Sqmm Cable | ElEC | labour | SWR11972 | 749 | M | 1498000
230 | 1800 | Excavation & laying of UG Cable (Double Run) Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, Along the CC / BT multi layer road requiring compressor-33 KV 3x400 Sqmm Cable | ElEC | labour | SWR11980 | 1388.84 | M | 2499912
231 | 200 | Across the CC/ BT road crossing multi layer road requiring compressor (excluding the cost of Hume pipe)-33 KV 3x400 Sqmm Cable | ElEC | labour | SWR11988 | 1587.07 | M | 317414
232 | 4000 | Laying of 2nd cable in excavated trench | ElEC | labour | SWR10988 | 204.1 | M | 816400
233 | 40 | S&E-Smart RFID marker | ElEC | labour | SWR25089 | 2745 | EA | 109800
234 | 28 | UG Cables Joints 33 KV 3x400 Sqmm Cable Straight through joint 33kv 3x400 xlpe | ElEC | labour | SWR10382 | 5700.78 | EA | 159621.84
235 | 1500 | Supply of 6" B class GI pipe | ElEC | supply | SMR40081 | 1044 | M | 1566000
236 | 300 | Cost of Pipes and slabs-supply of 6" DWC pipe | ElEC | supply | SMR11610 | 1012 | M | 303600
237 | 400 | Cost of Pipes and slabs-Suppy of Hume pipe 9" size | ElEC | labour | SMR40001 | 125 | M | 50000
238 | 12 | Making of Outdoor/Indoor End Making 33 KV 3x400 Sqmm Cable Out Door/Indoor end termination TerminationOD/Idoor end termination 33kv 3x400 xlpe | ElEC | labour | SWR10387 | 2764.76 | EA | 33177.12
239 | 60 | Excavation & laying of UG Cable (Double Run) Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-33 KV 3x400 Sqmm Cable | ElEC | labour | SWR12004 | 323.85 | M | 19431
240 | 3000 | Hard Rock Cutting-11KV-Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours. | ElEC | labour | SWR21903 | 30 | M | 90000
241 | 40 | Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters , CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | ElEC | supply | SMR40085 | 484 | EA | 19360
242 | 3 | Erection of AB Switch and aligment complete Erection of 33 KV AB Switch including alignment and earthing | ElEC | labour | SWR10392 | 4500 | EA | 13500
243 | 3 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | ElEC | labour | SWR12331 | 146.63 | EA | 439.89
244 | 3 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Note:-The requirement of 2nd coat is to be justified by the concerned Divisional Engineer /Executive Engineer before execution of this work Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | ElEC | labour | SWR10881 | 142 | EA | 426
245 | 12 | Fabrication of poles-Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | ElEC | labour | SWR10642 | 512.55 | EA | 6150.6
246 | 18 | Painting of poles-Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | ElEC | labour | SWR10640 | 1132 | EA | 20376
247 | 12 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M Ex of Hard pit w/o blast 0.75X0.9X1.95M | ElEC | labour | SWR11040 | 990.68 | EA | 11888.16
248 | 3 | Assembly and erection of Structure as per specification which includes fixing of top channels and cross bracings, transport of all materials from road side to the location, earthing, back filling with earth ramming etc excluding pit excavation and concreting-33 KV DP Structure with 175x85/150x75mm RS joist | ElEC | labour | SWR11276 | 5670 | SET | 17010
249 | 6 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-RS Joists 150x75/175 x 85 mm | ElEC | labour | SWR10346 | 1934 | EA | 11604
250 | 155 | Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) Earthing for raisers of SS Flat 50x6 mm. | ElEC | labour | SWR10919 | 41 | RMT | 6355
251 | 11.282 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ElEC | labour | SWR10356 | 6579 | M3 | 74224.278
252 | 0.372 | Mass Concreting for pole-Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | ElEC | labour | SWR11890 | 3893 | M3 | 1448.196
253 | 0.975 | Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to theRS-Joist poles excluding cost of Mild Steel and transportcharges to substation site, including erection. Fabrication of struc.with welding. | ElEC | labour | SWR10869 | 3426 | TO | 3340.35
254 | 6 | Supply of earthing pipe with materials-Supply of CI eath pipe with 80mm dia,2.0 M Length | ElEC | supply | SMR11483 | 2789 | EA | 16734
255 | 6 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | ElEC | labour | SWR10357 | 1234.2 | EA | 7405.2
256 | 6 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINES-Providing of RCC collar | ElEC | labour | SWR10359 | 386 | EA | 2316
257 | 3 | Painting of poles-Painting of feeder name on support including cost of paint | ElEC | labour | SWR12101 | 53 | EA | 159
258 | 30 | Supply of earthing pipe with materials S-GI Bolts & Nuts,Washers etc., | ElEC | supply | SMR11488 | 117.5 | KG | 3525
259 | 130 | S-Supply of PSCC Spun Pole 12.5Mtr | ElEC | supply | SMR25238 | 15635.59 | EA | 2032626.7
260 | 20 | S-Supply of PSCC Pole 9.1Mtr 280kg | ElEC | supply | SMR25233 | 3109.41 | EA | 62188.2
261 | 3660 | S- Supply of MS Channel 100x50mm | ElEC | supply | SMR22745 | 57.45 | KGS | 210267
262 | 338 | S-MS Angle 65X65X6 | ElEC | supply | SMR25207 | 57.25 | KG | 19350.5
263 | 1484 | S-Supply of MS Flat 75x8mm | ElEC | supply | SMR12321 | 56.42 | KG | 83727.28
264 | 12 | Supply of 33KV 3x400Sqmm O/D End Kit | ElEC | supply | SMR22222 | 4554 | EA | 54648
265 | 28 | Supply of 33KV3x400Sqmm Straight thr kit | ElEC | supply | SMR22223 | 24151 | EA | 676228
266 | 3 | S-Supply of 33KV 800A DB Break AB Switch | ElEC | supply | SMR12315 | 40658.78 | EA | 121976.34
267 | 4500 | S-Supply of RS Joist Pole (175x85mm) | ElEC | supply | SMR12303 | 60.75 | KG | 273375
268 | 370 | S-Supply of MS Flat 50x6mm | ElEC | supply | SMR12322 | 56.5 | KG | 20905
269 | 975 | S- Supply of MS Channel 100x50mm | ElEC | supply | SMR22745 | 57.45 | KGS | 56013.75
270 | 130 | Fabrication of materials including 2 coats of Red oxide painting-1.53 mt. V.Cross arms with 100x50 mm MS Channel | ElEC | supply | SWR10312 | 158 | EA | 20540
271 | 130 | Fabrication of materials including 2 coats of Red oxide painting-Back clamps with 75 x 8 mm MS Flat | ElEC | supply | SWR10319 | 31 | EA | 4030
272 | 140 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M Ex of Hard pit w/o blast 0.75X0.9X1.95M | ElEC | labour | SWR11040 | 990.68 | EA | 138695.2
273 | 235 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | ElEC | labour | SWR11039 | 928 | EA | 218080
274 | 30 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-Stud Poles 0.6 M x 0.9 M x 1.5 M (0.81 cubmic meter) | ElEC | labour | SWR11038 | 612 | EA | 18360
275 | 140 | Erection of OH Lines including AB Cable (33KV, 11KV, LT) Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Errection of 11 M long PSCC pole | ElEC | labour | SWR10978 | 4336.85 | EA | 607159
276 | 235 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-9.1 M long PSCC pole | ElEC | labour | SWR10343 | 2400 | EA | 564000
277 | 30 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-8.0 m long PSCC poles for Strut | ElEC | labour | SWR21590 | 1500 | EA | 45000
278 | 108.2 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ElEC | labour | SWR10356 | 6579 | M3 | 711847.8
279 | 8 | LOADING of Conductor drums | ElEC | labour | SWR10191 | 202 | EA | 1616
280 | 4 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | ElEC | labour | SWR11861 | 3299.7 | EA | 13198.8
281 | 8 | UNLOADING of Conductor drums | ElEC | labour | SWR10509 | 100 | EA | 800
282 | 15 | Paving out and stringing of conductor by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location-55 Sqmm Single Circuit (3 Conductors) | ElEC | labour | SWR10365 | 9454.81 | KM | 141822.15
283 | 34 | Formation of Cut point for 11 KV Single Circuit line excluding pole erection and stays Formatn of Horiz Cut point for 11KV line | ElEC | labour | SWR10653 | 1435.81 | EA | 48817.54
284 | 375 | Painting of poles-Numbering of poles incl. cost of paint | ElEC | labour | SWR10378 | 32 | EA | 12000
285 | 12 | Fabrication of poles-Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | ElEC | labour | SWR10642 | 512.55 | EA | 6150.6
286 | 12 | Painting of poles-Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | ElEC | labour | SWR10640 | 1132 | EA | 13584
287 | 6 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M Ex of Hard pit w/o blast 0.75X0.9X1.95M | ElEC | labour | SWR11040 | 990.68 | EA | 5944.08
288 | 6 | Erection of OH Lines including AB Cable (33KV, 11KV, LT) Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Box pole 9/10/11 Mtr | ElEC | labour | SWR11266 | 2643.83 | EA | 15862.98
289 | 160 | Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) Earthing for raisers of SS Flat 50x6 mm. | ElEC | labour | SWR10919 | 41 | RMT | 6560
290 | 5.64 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | ElEC | labour | SWR10356 | 6579 | M3 | 37105.56
291 | 0.186 | Mass Concreting for pole-Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | ElEC | labour | SWR11890 | 3893 | M3 | 724.098
292 | 0.23 | Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to theRS-Joist poles excluding cost of Mild Steel and transportcharges to substation site, including erection. Fabrication of struc.with welding. | ElEC | labour | SWR10869 | 3426 | TO | 787.98
293 | 12 | Supply of earthing pipe with materials-Supply of CI eath pipe with 80mm dia,2.0 M Length | ElEC | labour | SMR11483 | 2789 | EA | 33468
294 | 12 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | ElEC | labour | SWR10357 | 1234.2 | EA | 14810.4
295 | 12 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINES-Providing of RCC collar | ElEC | labour | SWR10359 | 386 | EA | 4632
296 | 6 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | ElEC | labour | SWR10393 | 3200 | EA | 19200
297 | 6 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | ElEC | labour | SWR12331 | 146.63 | EA | 879.78
298 | 6 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Note:-The requirement of 2nd coat is to be justified by the concerned Divisional Engineer /Executive Engineer before execution of this work Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | ElEC | labour | SWR10881 | 142 | EA | 852
299 | 6 | Painting of poles-Painting of feeder name on support including cost of paint | ElEC | labour | SWR12101 | 53 | EA | 318
300 | 40 | Supply of earthing pipe with materials S-GI Bolts & Nuts,Washers etc., | ElEC | supply | SMR11488 | 117.5 | KG | 4700
301 | 140 | Supply of PSCC Pole 11Mtr 365 Kg | ElEC | supply | SMR25236 | 5399 | EA | 755860
302 | 235 | S-Supply of PSCC Pole 9.1Mtr 280kg | ElEC | supply | SMR25233 | 3109.41 | EA | 730711.35
303 | 30 | S-Supply of PSCC Pole 8Mtr 140kg | ElEC | supply | SMR25232 | 1580 | EA | 47400
304 | 1099 | S-Supply of 11KV V X-Arms with MS Channel 75x40 | ElEC | supply | SMR25219 | 561 | EA | 616539
305 | 1099 | Supply of 11KV Top Cleant for 9.1M(Vertical) | ElEC | supply | SMR25226 | 256 | EA | 281344
306 | 52 | S-Supply of 11KV Horizontal Cross Arms | ElEC | supply | SMR25223 | 528 | EA | 27456
307 | 1125 | S-Supply of LT/11KV MS Back Clamps | ElEC | supply | SMR25217 | 72 | SET | 81000
308 | 6 | S-Supply of 11KV 400A DB Break AB Switch | ElEC | supply | SMR12317 | 18150 | EA | 108900
309 | 3000 | S-Supply of RS Joist Pole (175x85mm) | ElEC | supply | SMR12303 | 60.75 | KG | 182250
310 | 384 | S-Supply of MS Flat 50x6mm | ElEC | supply | SMR12322 | 56.5 | KG | 21696
311 | 150 | S-Supply of MS Angle 50x50x6 | ElEC | supply | SMR25206 | 58.15 | KG | 8722.5
312 | 80 | S-Supply of MS Channel 75x40 mm | ElEC | supply | SMR25205 | 58.45 | KG | 4676
Electrical labour | [7 empty] | 32314782.577
Civil labour-WBS. No. S-1805-13-07-01-01-001
Sl.No. | Estimate Quantity (only Figures) | Item Detailed Specification Description | Work Type eg. Earth Work, Electrical works. etc (upto 200 Characters) | Item Short Description (upto 100 Characters) | APSS / Morth Cl. Number (upto 200 Characters) | Rate (INR) (Upto 2 Decimals ) | UOM (upto 50 Characters) | Amount
1 | 32 | Leveliing the site by cutting and levelling with the help of JCB including cost,conveyance of all materials,hire chareges etc complete for finished item of work as directed by Engineer-in-charge. | Civil | Labour | SWR34179 | 2165 | Hrs | 69280
2 | 358.34 | Earth Work Mass Excavation (hard rock) to a depth as directed, in soils such as hard rock requiring blasting in prohibited area and all conditions such as dry, wet, slurry etc.and in dense or hard soils, disposal and depositing of excavated soil with intial lead of 10 mt and intial lift of 2m or as directed, including cost and conveyance of all materials, ramping and lifting of materials, and labour charges, hire charges of machinery, tools & plants, bailing of water ( either sub soil water, stoMts water, rain water, surface water or of any kind) if any at any stage of work until all works below ground level is finished to the satisfaction ,and from work such as shoring, timbering, strutting with required supports etc. for the work and removal of form work after completion of work etc all complete as directed by the engineer-incharge. | Civil | Labour | SWR33018 | 1440 | cum | 516009.6
3 | 297 | Earth work excavation in all type of ordinary soils red earth, Hard gravelly soils, earth mixed with sand and sandy soils etc., in all conditions such as slushy and dry with initial leads and lifts for foundations. Ordinary Soil | Civil | Labour | SWR33015 | 486 | cum | 144342
4 | 103.338 | PCC (1:4:8) using 40 mm metal with concrete Mixture. All work upto Plinth level including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete as directed by Engineer incharge of the work | Civil | Labour | SWR33028 | 4719 | cum | 487652.022
5 | 142.5 | Coursed Rubble stone CRS masonry 2nd sort with hard granite stones in cement mortar CM (1:6) for basement, including cost and conveyance of all materials, labour charges, curing, all leads and lifts, etc, complete for finished item of work. | Civil | Labour | SWR33041 | 4869 | cum | 693832.5
6 |  | RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge
7 | 1.09 | RCC M20 Grade Footing 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33098 | 9471 | cum | 10323.39
8 | 1.58 | RCC M20 Grade Column 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33100 | 13220 | cum | 20887.6
9 | 1.15 | RCC M20 Grade plinth beam 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33099 | 12342 | cum | 14193.3
10 | 0.458 | Reinforcement steel Supplying, Cutting, bending, binding, placing in position and tying reinforcement steel in all heights including cost and conveyance of steel and binding wire etc,. With all leads and lifts, labour charges, etc., complete for finished item of work. | Civil | Labour | SWR33144 | 70687 | MT | 32374.646
11 | 107.582 | Brick masonry in CM (1:6) for superstructure using well burnt country made second class bricks of approved quality including cost and conveyance of all materials curing, scaffolding with all leads and lifts in all heights etc., complete for finished item of work | Civil | Labour | SWR33068 | 8249 | cum | 887443.918
12 | 83.426 | PCC (1:2:4) using 20mm size well graded HBG metal for foundations, including cost, conveyance of all materials,labour all leads and lifts,consolidation and all operations, formwork as required, curing,etc. complete for finished item of work | Civil | Labour | SWR33030 | 6089 | cum | 507980.914
13 | 834.5 | Plastering with CM 2 coats, 20 mm thick, base coat in CM (1:6), 16 mm thick and top coat in CM (1:4), 4mm thick with Dubara sponze finishing including cost of all materials, seigniorage charges, excluding conveyance charges of materials and including all operational, incidental and labour charges for mixing mortar, laying rendering smooth and thread lining, curing, rounding off junctions of wall and slab etc., complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33163 | 560 | Sqm | 467320
14 | 834.5 | Painting with two coats of Plastic Emulsn paint over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33356 | 210 | Sqm | 175245
15 | 271.85 | Painting with two coats of Surya Cem paint over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33329 | 85 | sqm | 23107.25
16 | 650 | Supplying and fixing Structural Steel angles channal etc.Manufacturing, Supplying and fixing of MS grill for (Gate and raillings) of approved design as per drawings, including cost and conveyance of all materials, labour charges etc.,complete for finished item of work as directed by the Engineer- in-charge. | Civil | Labour | SWR33145 | 128 | Kgs | 83200
17 | 3 | Supply and Fixng of MS Name Board including cost & conveyance of all materials,labour charges etc complete for finished item of work. | Civil | Labour | SWR33421 | 4326 | sqm | 12978
18 | 1 | Geophysical Investgation charges for water point by Geologist | Civil | Labour | SWR33608 | 5000 | EA | 5000
19 |  | Drilling of 165mm bore well with machine rig including deployment and hire charges of rig and other machinery and equipment labour charges , measuring the yeild of borewell including cost and conveyance etc complete
20 | 90 | Drill-165mm Bore Well 0 to 90 | Civil | Labour | SWR33609 | 336 | M | 30240
21 | 30 | Drill-165mm Bore Well 90M to 120M | Civil | Labour | SWR34830 | 369 | M | 11070
22 | 30 | Drill-165mm Bore Well 120M to 150M | Civil | Labour | SWR34831 | 394 | M | 11820
23 | 30 | Drill-165mm Bore Well 150M to 180M | Civil | Labour | SWR34832 | 492 | M | 14760
24 | 30 | Drill-165mm Bore Well 180M to 210M | Civil | Labour | SWR34833 | 623 | M | 18690
25 | 30 | Drill-165mm Bore Well 210M to 240M | Civil | Labour | SWR34834 | 754 | M | 22620
26 | 30 | Drill-165mm Bore Well 240M to 270M | Civil | Labour | SWR34835 | 918 | M | 27540
27 | 150 | Drill-165mm Bore Well 270M and above | Civil | Labour | SWR34836 | 1082 | M | 162300
28 | 40 | Supply and fixing of 160mm dia PVC casing of A class 6Kg point pressure including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR33611 | 883 | M | 35320
29 | 1 | Supply and erecting, ISI mark submersible 5.0 HP, three Phase 30 stages pumpset suitable for 106/156mm dia borewell including cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33640 | 48007 | EA | 48007
30 | 370 | Supply and fixing of HDPE pipe 40mm dia of 16Kg/cm2 including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR34410 | 180 | M | 66600
31 | 1 | Supply and erecting D.O.L Starter 415V ,3 phase,50Hz with SS enclouserincluding cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33645 | 7854 | EA | 7854
32 | 450 | Supply of 3 Core 2.5 Sqmm Flat Copper cable of ISI for Submersible Motors of makes Finolex / Polycab / Gold Medal / Million / Payal / Sun Light / Power Flex / Fortune Art | Civil | Labour | SWR33641 | 192 | M | 86400
33 | 6 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-28.60mm OD Pipe - SDR 11 | Civil | Labour | SWR34363 | 410 | M | 2460
34 | 1 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type - 25mm NB Size | Civil | Labour | SWR34346 | 466 | EA | 466
35 | 72.73 | Earth work excavation in all type of ordinary soils red earth, Hard gravelly soils, earth mixed with sand and sandy soils etc., in all conditions such as slushy and dry with initial leads and lifts for foundations. | Civil | Labour | SWR33015 | 486 | Cum | 35346.78
36 | 39.53 | PCC (1:4:8) using 40mm HBG metal for foundations and leveling course, including cost and conveyance of all materials, labour all leads and lifts, consolidation and all operations, formwork as required, curing, etc. complete for finished item w | Civil | Labour | SWR33028 | 4719 | Cum | 186542.07
37 | 27.37 | CRS Coursed Rubble Stone masonry 2nd sort with hard granite stones in cement mortar (1:6) for basement, including cost and conveyance of all materials, labour charges, curing, all leads and lifts, etc, complete for finished item of work. | Civil | Labour | SWR33041 | 4869 | Cum | 133264.53
38 | 133.29 | Supplying and filling the substation site with borrowed gravel, watering, ramming, thoroughly complying with the standard specification. | Civil | Labour | SWR33052 | 339 | Cum | 45185.31
39 |  | 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge
40 | 5.346 | a) RCC M20 Grade Footings 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33098 | 9471 | Cum | 50631.966
41 | 3.42 | b)RCC M20 Grade Columns 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33100 | 13220 | Cum | 45212.4
42 | 4.03 | c)RCC M20 Grade Plinth Beams 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33099 | 12342 | Cum | 49738.26
43 | 3.55 | D) RCC M20 Grade Roof Beams 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33121 | 12258 | Cum | 43515.9
44 | 0.58 | e) RCC M20 Grade Lintels 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33107 | 13050 | Cum | 7569
45 | 2.7 | f) RCC M20 Grade Sunshades 600mm wide and 75mm thick 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33114 | 1374 | Sqm | 3709.8
46 | 19.206 | g) RCC M20 Grade Roof Slab 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33128 | 10846 | Cum | 208308.276
47 | 4.55 | reinforcement steel Supplying, Cutting, bending, binding, placing in position and tying reinforcement steel in all heights including cost and conveyance of steel and binding wire etc,. With all leads and lifts, labour charges, etc., complete for finished item of work. | Civil | Labour | SWR33144 | 70687 | MT | 321625.85
48 | 59.32 | Brick masonry in CM (1:6) for superstructure using well burnt country made second class bricks of approved quality including cost and conveyance of all materials curing, scaffolding with all leads and lifts in all heights etc., complete for fin | Civil | Labour | SWR33068 | 8249 | Cum | 489330.68
49 | 536.48 | Plastering with CM 2 coats, 20 mm thick, base coat in CM (1:6), 16 mm thick and top coat in CM (1:4), 4mm thick with Dubara sponze finishing including cost of all materials, seigniorage charges, excluding conveyance charges of materials and including all operational, incidental and labour charges for mixing mortar, laying rendering smooth and thread lining, curing, rounding off junctions of wall and slab etc., complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33163 | 560 | Sqm | 300428.8
50 | 85.68 | Providing Structural steel tube box type 60x40x4mm thick including cost and conveyance of all materials, labour charges,curing etc. complete for finished item of work and as directed by the engineer-in-charge. | Civil | Labour | SWR33146 | 147 | Kgs | 12594.96
51 | 18 | Providing Roofing with Trapezoidal/Galvalume Sheet including cost and conveyance of all materials, labour charges,curing etc. complete for finished item of work and as directed by the engineer-in-charge. | Civil | Labour | SWR33402 | 600 | Sqm | 10800
52 | 18.9 | Providing Design R.C.M. drop wall of 40mm thickness with cm 1:2 and 6mm dia MS bars at 150mm both ways and chicken mesh in two coats 20mm thick each plastering including cost and conveyance of all materials with leads and lifts, scaffolding and curing, labo | Civil | Labour | SWR33203 | 3047 | Sqm | 57588.3
53 | 12.24 | Supply and fixing of MS ornamental safety grill of approved design including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33310 | 2990 | sqm | 36597.6
54 | 5.91 | Supply and fixing of doors with the MT Wood frames the door shall be made well seasoned mt wood of cross section 100x75mm. The shutter shall be made isi mark flushed door with decolam sheets pasted on both sides with PVC beading 40mm width all round.Frame shall be painted with two coats of synthetic enamel paint of approved color over one coat of primer over luppum with spary with 3 no 150mm brass hinges 1 no brass door stoper, 1 no 250mm brass aldrops. 2 no 300 mm aluminium tower bolts, 2 no 150mm brass fancy door handlers, 1 no keyless lockset with cp handel. The quoted rate shall include cost and conveyance of the meterials, fixig, labour carges, tools, handles,locking arrangementts and other fixtures & fittings for finished item work as directed by the Engineer - in- charge. | Civil | Labour | SWR33264 | 7314 | Sqm | 43225.74
55 | 20.25 | Raised pointing to the exposed surfaces of CRS masonry in cm 1:3 prop. including cost and conveyance of all materials, labour charges, all leads and lifts curing etc, complete for finished item of work. | Civil | Labour | SWR33184 | 124 | sqm | 2511
56 | 8.64 | Supplying and fixing Aluminium sliding windows with grill and fixed glass panels using anodised aluminium extruded sections of mat finish for frames and mullions made from approved aluminium sections 62x32x1.2mm at 0.73kg/Rm providing 5mm plain glass fix | Civil | Labour | SWR33277 | 3623 | sqm | 31302.72
57 | 16.56 | Supply and laying of Ceramic floor over of CM 1:3 20 mm thick including required materials and labour charges etc complete for item of work | Civil | Labour | SWR33224 | 914 | Sqm | 15135.84
58 | 121.92 | Flooring with double machine polished and hand cut Tandur blue stone 20mm thick of approved colour, quality and of minimum of 300x300mm size over a bed of cement mortar 1:3 20mm thick including cost of all materials, with all leads and lifts jointing and | Civil | Labour | SWR33219 | 786 | Sqm | 95829.12
59 | 6.74 | Supply and fixing of 4" high skirting of shabad stone to the walls including cost and conveyance of all materials, labour etc for finished item of work. | Civil | Labour | SWR33236 | 875 | Sqm | 5897.5
60 | 243.69 | Painting with two coats of OBD over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials labour charges etc., complete for finished item of work. | Civil | Labour | SWR33333 | 146 | Sqm | 35578.74
61 | 414.315 | Painting with two coats of Plastic emulsn paint 2 coat of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33356 | 210 | Sqm | 87006.15
62 | 129.92 | Providing impervious coat over RCC roof slab to requried slopes with 20mm thick in CM 1:3 mixed with approved brand of water proffing compound inclding cost and conveyance of all materials, labour charges, curing, rounding off junctions of wall and slab, all leads and lifts, etc . complete for finished item of work as directed by the Engineer - in - charge. | Civil | Labour | SWR33156 | 582 | sqm | 75613.44
63 | 60 | Supply & fixing of 25mm dia 2mm thick surface P.V.C. pipe (ISI MARK) Concealed in wall with all required accessories including masonary work and labour charges etc.complete. | Civil | Labour | SWR33441 | 108 | M | 6480
64 | 1 | Supply & fixing TPNDB Distribution board with IP-42 protection (Metal Door)suitable for 3 phase ELCB/RCCB/FP Isolator as incomer and 10kA SP MCBs as out going including internal connection and labour charges for surface / flush mounting etc Complete. | Civil | Labour | SWR33526 | 11353 | EA | 11353
65 | 10 | Supply & fixing Flush type of 6A 3 pin wall plug socket with 6A switch control on a common switch board with earth continuity including wire leads,earth connection along with all labour charges etc., complete | Civil | Labour | SWR33468 | 166 | EA | 1660
66 | 6 | Supply & fixing Flush type of 16A 3 pin and 6A 3pin plug Flush type socket with indicator lamp and 16Amps fuse unit and 16Amps switch control (5 in one )duly recessed in wall with wooden deep box of 6'' x 8'' x 2 1/2'' size covered with hylam sheet earth connection and all labour charges etc., complete on wall. | Civil | Labour | SWR33470 | 449 | EA | 2694
67 | 24 | Supply and Fixing of modular switch, LP,FP,EFP,Wiring with 2 runs of 14/0.3mm (1.0 sq.mm)Fire Retardant (FR) P.V.C. insulated flexible copper cable (ISI MARK) in existing pipe with 6A Flush type Switch,ceiling rose and 3mm thick hylam sheet covering to switch control box including all labour charges etc., complete for light points, bell , fan and exhaust fan points in Non-Residential Buildings. | Civil | Labour | SWR33457 | 676 | EA | 16224
68 | 12 | Supply & Fixing of 28W T5 fluorescent tube. | Civil | Labour | SWR33558 | 148 | EA | 1776
69 | 1 | Supply of 12" (300mm)ISI, 900 RPM light duty exhaust fan with metallic blades with Mark of makes Crompton / Bajaj / Havells / Orient. | Civil | Labour | SWR33571 | 2192 | EA | 2192
70 | 180 | Supply and run of 2 of 22/0.3mm (1.5 sq.mm) (FR) P.V.C. insulated flexible copper cable in existing pipe for mains including all labour charges complete. | Civil | Labour | SWR33496 | 75 | M | 13500
71 | 180 | Supply and run of 2 of 36/0.3mm (2.5 sq.mm) FR P.V.C. insulated flexible copper cable in existing pipe for mains including all labour charges complete. | Civil | Labour | SWR33497 | 103 | M | 18540
72 | 12 | Supply & fixing of batten holder /slanting holder in lieu of ceiling rose of light point complete with all connection and all labour charges with 40W bulb (for new installation). | Civil | Labour | SWR33484 | 141 | EA | 1692
73 | 4 | Supply & fixing of 1200mm (48'') sweep 230v,A.C 50 Hz.Ceiling fan with 3 Blades and double ball bearings with all standared accessories. | Civil | Labour | SWR33563 | 2277 | EA | 9108
74 | 4 | Supply & fixing of Electronic Regulator for ceiling fans 900/1200/1400mm sweep including cost of material, Electrical charges complete for finished item of work | Civil | Labour | SWR33564 | 589 | EA | 2356
75 | 1 | Providing independent EARTHING by excavating a trench to a depth of 2.1M in all solid,as per size specified in the Data,using 40mm dia 'B' class GI pipe of 2.5 Mtrs length with necessary accessories with hume pipe ring duly providing staggered holes including filling with equal proportion of salt and Charcoal in layers and all labour charges etc., compiete for small quarters. | Civil | Labour | SWR33596 | 5345 | EA | 5345
76 | 35 | Supplying, laying, jointing and testing 101.6 mm SWG SP-1 pipes of ISI make conforming to ISI 651 & 4127 with airtight cement joints in CM 1.5:1 prop. Including excavation of trenches and socket pits in any soil (except rock requiring blasting) up to 1524 mm(5'0") depth and refilling with watering and tamping. | Civil | Labour | SWR34281 | 755 | M | 26425
77 | 3 | Constructing 904.0 mm (3#0#) dia brick masonry inspection chamber as per IS - 4111: Part-1:1986 with cement mortar (1:6) prop using 2nd Class Clay Bricks of 225 mm thick from approved source having a minimum crushing strength of 5 N/sq.mm including plastering with cement mortar 1:3 prop; ½# thick both inside and outside fitted with 20# dia RCC manhole covers and frames including excavating pits up to a depth of 904 mm (3'-0") in all sorts of soils (excluding rock) and laying cement concrete (1:4:8) 150 mm thick using 40 mm HBG Metal and P.C.C. 1:2:4 benching and channel 100 mm thick as per Standard specification and including cost and conveyance of all materials like cement, sand, bricks, water etc., to site, cost of seigniorage charges on all materials and all incidental and operational, labour charges like mixing cement mortar, constructing masonry, lift charges, curing etc., complete for finished item of work as per Standard specification. | Civil | Labour | SWR34296 | 8766 | EA | 26298
78 | 4 | Supply & fixing of 110 mm dia - Door Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34381 | 128 | EA | 512
79 | 4 | Supply & fixing of 110 mm dia - Plain Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34380 | 100 | EA | 400
80 | 12 | Supply & fixing of 110 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand | Civil | Labour | SWR34377 | 462 | M | 5544
81 | 18 | Supply & fixing of 90 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand | Civil | Labour | SWR34378 | 410 | M | 7380
82 | 3 | Supplying & fixing 150 mm x 100 mm SWG gully traps conforming to ISI 651 & 4127 with C.I Grating & Cost. Brick masonry in CM 1:6 prop. Intermediate chamber and fitted with 304.8 mm x 288.6mm (12"x9") C.I Frame and hinged cover | Civil | Labour | SWR34286 | 767 | EA | 2301
83 | 1 | Supplying and Fixing of European Water Closet of 1st Quality | Civil | Labour | SWR34314 | 2228 | EA | 2228
84 | 6 | Supply & fixing 15 mm angle stop cock Indian make 400 grams Seiko/ Senior/ Nice/ Senior/ Nice or equivalent | Civil | Labour | SWR34328 | 721 | EA | 4326
85 | 4 | S&F 15 mm N.P bib tap Indian make 400 grams full turn Seiko/ Senior/ Nice or equivalent | Civil | Labour | SWR34329 | 296 | EA | 1184
86 | 1 | Supplying & Fixing Indian make Flat Back Wash Hand Basin (HSW/Parryware/ Neycer) 1st quality conforming to IS:2556-Part-4:1972 with waste fittings like rubber plug, chain, 32 mm nominal size C.P. Fitting with parallel pipe thread conforming to IS:2963-1979 and fitted with 15 mm nominal bore Chromium Plated Pillar Tap of 1st quality Indian make 400 grams Seiko/ Senior/ Nice/ Esso or equivalent complete with standard CI brackets including wooden block: 550 x 400 mm - Single C.P. Pillar cock | Civil | Labour | SWR34316 | 1717 | EA | 1717
87 | 2 | Supply & fixing 38.1 mm C.P waste coupling Half or Full Thread 1st Quality Indian make Parryware or equivalent | Civil | Labour | SWR34428 | 309 | EA | 618
88 | 2 | Supply & fixing of 4" (101.6 mm ) Nahany Trap ( Without Jali with inlet)UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34387 | 134 | EA | 268
89 | 1000 | Providing & Placing on Terrace (at all floor levels) polyethylene water storage tank with Double layer approved brand & manufacture with cover and suitable locking arrangement & making necessary holes for inlet & outlets and over flow pipes but with NECESSARY fittings & base support for tanks | Civil | Labour | SWR34375 | 10 | L | 10000
90 | 2 | Supply & fixing 31.75 mm dia PVC flexible waste pipe of 914.4 mm length of Ist quality | Civil | Labour | SWR34426 | 33 | EA | 66
91 | 45 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)- 15.90mm OD Pipe - SDR 11 | Civil | Labour | SWR34361 | 239 | M | 10755
92 | 40 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-22.20mm OD Pipe - SDR 11 | Civil | Labour | SWR34362 | 313 | M | 12520
93 | 65 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-28.60mm OD Pipe - SDR 11 | Civil | Labour | SWR34363 | 410 | M | 26650
94 | 4 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type - 25mm NB Size | Civil | Labour | SWR34346 | 466 | EA | 1864
95 | 4 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type -20mm NB Size | Civil | Labour | SWR34345 | 331 | EA | 1324
96 | 1 | Supply & fixing 25.4 mm dia & 609.6 mm long aluminium anodized towel rod with brackets and aluminium screws | Civil | Labour | SWR34430 | 489 | EA | 489
97 | 85.51 | Earth work excavation in all type of Ordinary soils red earth, Hard gravelly soils, earth mixed with sand and sandy soils etc., in all conditions such as slushy and dry with initial leads and lifts for foundations. Ordinary Soil | Civil | Labour | SWR33015 | 486 | cum | 41557.86
98 | 18.91 | PCC (1:4:8) using 40mm HBG metal for foundations and leveling course, including cost and conveyance of all materials, labour all leads and lifts, consolidation and all operations, formwork as required, curing, etc. complete for finished item w | Civil | Labour | SWR33028 | 4719 | cum | 89236.29
99 | 91.8 | Coursed Rubble stone masonry (CRS) 2nd sort with hard granite stones in cement mortar (1:6) for basement, including cost and conveyance of all materials, labour charges, curing, all leads and lifts, etc, complete for finished item of work. | Civil | Labour | SWR33041 | 4869 | cum | 446974.2
100 | 36 | PCC (1:3:6) using 40mm HBG metal for foundations and leveling course, including cost and conveyance of all materials, labour all leads and lifts, consolidation and all operations, formwork as required, curing, etc. complete for finished item w | Civil | Labour | SWR33029 | 5009 | cum | 180324
101 | 108 | Raised pointing to the exposed surfaces of CRS masonry in cm 1:3 prop. including cost and conveyance of all materials, labour charges, all leads and lifts curing etc, complete for finished item of work. | Civil | Labour | SWR33184 | 124 | sq.mm | 13392
102 | 787.5 | Supplying and filling the substation site with borrowed gravel, watering, ramming, thoroughly complying with the standard specification. | Civil | Labour | SWR33052 | 339 | cum | 266962.5
103 | 88.8 | Plastering with CM 2 coats, 20 mm thick, base coat in CM (1:6), 16 mm thick and top coat in CM (1:4), 4mm thick with Dubara sponze finishing including cost of all materials, seigniorage charges, excluding conveyance charges of materials and including all operational, incidental and labour charges for mixing mortar, laying rendering smooth and thread lining, curing, rounding off junctions of wall and slab etc., complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33163 | 560 | sq.mm | 49728
104 | 200.85 | Painting with two coats of Surya Cem paint over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33329 | 85 | sq.mm | 17072.25
105 | 120 | Supply&Fabrication and fixing of Welded wire mesh ( 2" x 2") of 3mm dia. with ISMC (75x40x4.4mm) and Pheriperal frame of ISA(35x35x3mm) incldg cost& conveyance painting with synthetic enamil paint two coats over a coat of red oxide primer etc complete for finished item of work.. | Civil | Labour | SWR33403 | 2310 | sq.mm | 277200
106 | 160 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-22.20mm OD Pipe - SDR 11 | Civil | Labour | SWR34362 | 313 | M | 50080
107 | 30 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type - 25mm NB Size | Civil | Labour | SWR34346 | 466 | EA | 13980
108 | 1 | Providing Consultancy services for arranging contour surveying with total station incuding preparation of boundary and contour levels with 2 Nos. Hard copies and soft copies complete for finished items of work | Civil | Labour | SWR33427 | 5665 | EA | 5665
109 | 579.3635 | Seigniorage Charges - Sand | Civil | Labour | SWR34470 | 40 | cum | 23174.5404
110 | 1848.5611 | Seigniorage Charges - Metal | Civil | Labour | SWR34471 | 97.5 | cum | 180234.7033
111 | 920.79 | Seigniorage Charges - Gravel | Civil | Labour | SWR34472 | 30 | cum | 27623.7
112 | 60 | Supply and fixing of RCC fencing poles of size 0.1mx0.1mx1.8m (security fencing of sub station), including cost and conveyance of all labour, materials,and hire chareges etc complete for finished item of work. | Civil | Labour | Swr33405 | 1444 | EA | 86640
113 | 1200 | Supply and fixing of galvanised barded wire (1 horizantal & 2 cross strands. including cost and conveyance of all labour, materials,and hire chareges etc complete for finished item of work. | Civil | Labour | Swr33408 | 16 | M | 19200
Civil labour | [7 empty] | 9152241.9157
Electrical and Civil labour |  |  |  |  | 18% GST Rs. |  |  | 41467024.4928

## Ref (hidden)
| Neknampur | Gouse Nagar | Kings colony | Noorinagar | Miralam park | Bairagiguda | Huda Colony | Satamrai | P&T Colony | Ohm Nagar | Laxmiguda | RDO Office | Mansoorabad | Sahebnagar | Badangpet | Bandlaguda | Kuntloor
ss | 6603626.5 | 6583873.1 | 6582773.1 | 6582773.1 | 6582773.1 | 6582773.1 | 6582773.1 | 6582773.1 | 6582773.1 | 6603626.5 | 6582773.1 | 6582773.1 | 6582773.1 | 6582773.1 | 6583873.1 | 6583873.1 | 6582773.1
33 kV | 16147495.14 | 6507629.74 | 4353562.11 | 7339599.78 | 2187415.59 | 12009944.53 | 4917368.12 | 4144102.79 | 3235755.84 | 5692612.42 | 2992783.46 | 2177822.05 | 12081016.52 | 15663980.94 | 19738990.72 | 5998597.52 | 20178478.65
11 kV | 7867360.79 | 4019985.96 | 4062795.22 | 4055710.84 | 4062795.22 | 4062795.22 | 4065655.23 | 4075345.65 | 4075345.65 | 4061430.46 | 4030635.22 | 4029125.22 | 3458829.72 | 2692726.41 | 3507023.35 | 2857725.87 | 5553530.82
33 kV BE
132 kV BE
elec | 30618482.43 | 17111488.8 | 14999130.43 | 17978083.72 | 12832983.91 | 22655512.85 | 15565796.45 | 14802221.54 | 13893874.59 | 16357669.38 | 13606191.78 | 12789720.37 | 22122619.34 | 24939480.45 | 29829887.17 | 15440196.49 | 32314782.57
Civil | 6355149.29 | 4232006.83 | 4231777.1 | 4231711.13 | 4231964.74 | 4231785.69 | 4231633.87 | 4231786.56 | 4231751.07 | 4231759.31 | 4232092.61 | 4231446.13 | 9148489.48 | 9152105.44 | 9152465.39 | 9152224.14 | 9152241.94
Total | 36973631.72 | 21343495.63 | 19230907.53 | 22209794.85 | 17064948.65 | 26887298.54 | 19797430.32 | 19034008.1 | 18125625.66 | 20589428.69 | 17838284.39 | 17021166.5 | 31271108.82 | 34091585.89 | 38982352.56 | 24592420.63 | 41467024.51
30618482.43

## Final BOQ ECGH (hidden)
Estimate Quantity (only Figures) | Item Detailed Specification Description | Work Type eg. Earth Work, Electrical works.. etc ( upto 200 Characters) | Item Short Description ( upto 100 Characters) | APSS / Morth Cl. Number ( upto 200 Characters) | Rate (INR) ( Upto 2 Decimals ) | UOM ( upto 50 Characters) | Amount (INR) ( Upto 2 Decimals )
1 | 33/11 kV Neknampur SS Electrical labour | Elect | Labour | NA | 30618482.43 | EA | 30618482.43
1 | 33/11 kV Neknampur SS Civil labour | Civil | Labour | NA | 6355149.29 | EA | 6355149.29
1 | 33/11 kV Ghouse Nagar SS Electrical labour | Elect | Labour | NA | 17111488.8 | EA | 17111488.8
1 | 33/11 kV Ghouse Nagar SS Civil labour | Civil | Labour | NA | 4232006.83 | EA | 4232006.83
1 | 33/11 kV Kings Colony SS Electrical labour | Elect | Labour | NA | 14999130.43 | EA | 14999130.43
1 | 33/11 kV Kings Colony SS Civil labour | Civil | Labour | NA | 4231777.1 | EA | 4231777.1
1 | 33/11 kV Noori Nagar SS Electrical labour | Elect | Labour | NA | 17978083.72 | EA | 17978083.72
1 | 33/11 kV Noori Nagar SS Civil labour | Civil | Labour | NA | 4231711.13 | EA | 4231711.13
1 | 33/11 kV Meeralam Park SS Electrical labour | Elect | Labour | NA | 12832983.91 | EA | 12832983.91
1 | 33/11 kV Meeralam Park SS Civil labour | Civil | Labour | NA | 4231964.74 | EA | 4231964.74
1 | 33/11 kV Bairagiguda SS Electrical labour | Elect | Labour | NA | 22655512.85 | EA | 22655512.85
1 | 33/11 kV Bairagiguda SS Civil labour | Civil | Labour | NA | 4231785.69 | EA | 4231785.69
1 | 33/11 kV Huda Colony SS Electrical labour | Elect | Labour | NA | 15565796.45 | EA | 15565796.45
1 | 33/11 kV Huda Colony SS Civil labour | Civil | Labour | NA | 4231633.87 | EA | 4231633.87
1 | 33/11 kV Satamrai SS Electrical labour | Elect | Labour | NA | 14802221.54 | EA | 14802221.54
1 | 33/11 kV Satamrai Nagar SS Civil labour | Civil | Labour | NA | 4231786.56 | EA | 4231786.56
1 | 33/11 kV P&T Colony SS Electrical labour | Elect | Labour | NA | 13893874.59 | EA | 13893874.59
1 | 33/11 kV P&T Colony SS Civil labour | Civil | Labour | NA | 4231751.07 | EA | 4231751.07
1 | 33/11 kV Ohm Nagar SS Electrical labour | Elect | Labour | NA | 16357669.38 | EA | 16357669.38
1 | 33/11 kV Ohm Nagar SS Civil labour | Civil | Labour | NA | 4231759.31 | EA | 4231759.31
1 | 33/11 kV Laxmiguda Housing Board Colony SS Electrical labour | Elect | Labour | NA | 13606191.78 | EA | 13606191.78
1 | 33/11 kV Laxmiguda Housing Board Colony SS Civil labour | Civil | Labour | NA | 4232092.61 | EA | 4232092.61
1 | 33/11 kV RDO Office SS Electrical labour | Elect | Labour | NA | 12789720.37 | EA | 12789720.37
1 | 33/11 kV RDO Office SS Civil labour | Civil | Labour | NA | 4231446.13 | EA | 4231446.13
1 | 33/11 kV Mansoorabad Peddacheruvu SS Electrical labour | Elect | Labour | NA | 22122619.34 | EA | 22122619.34
1 | 33/11 kV Mansoorabad Peddacheruvu SS Civil labour | Civil | Labour | NA | 9148489.48 | EA | 9148489.48
1 | 33/11 kV Sahebnagar SS Electrical labour | Elect | Labour | NA | 24939480.45 | EA | 24939480.45
1 | 33/11 kV Sahebnagar SS Civil labour | Civil | Labour | NA | 9152105.44 | EA | 9152105.44
1 | 33/11 kV Badangpet SS Electrical labour | Elect | Labour | NA | 29829887.17 | EA | 29829887.17
1 | 33/11 kV Badangpet SS Civil labour | Civil | Labour | NA | 9152465.39 | EA | 9152465.39
1 | 33/11 kV Bandlaguda SS Electrical labour | Elect | Labour | NA | 15440196.49 | EA | 15440196.49
1 | 33/11 kV Bandlaguda SS Civil labour | Civil | Labour | NA | 9152224.14 | EA | 9152224.14
1 | 33/11 kV Kuntloor SS Electrical labour | Elect | Labour | NA | 32314782.57 | EA | 32314782.57
1 | 33/11 kV Kuntloor SS Civil labour | Civil | Labour | NA | 9152241.94 | EA | 9152241.94

## 17. 8Th Battalion
Schedule for the work of " Erection of new 33/11kV Outdoor substation with 2x8MVA PTRs and also Construction of Control room, and other Civil works at 8th Battalion in Kondapur section of operation Kondapur division in cybercity circle in WCGH Division of Master Plan, Ranga Reddy Circle".
1. D.No :San No: 130, D no. 1350, Dt:09-11-2024
2. WBS No. Supply S-1800-13-04-01-01-001
Sl.No | Estimate Quantity(Only Figures) | PARTICULARS | Work Type | Item Short Description | SWR No/APSS/Morth cl.No | Rate (INR) (Upto 2 Decimals) | UOM | Amount
1 | 8 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") Exca Hard pit w/o blast 0.76X0.76X1.83M | Elecy | labour | SWR11039 | 928 | EA | 7424
2 | 8 | Excavation of pits in hard rock requiring blasting. (other than SS) 9.1Mtrs PSCC Pole 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") EXCAV. OF PIT HARD(2.6" x 2.6" x 6.0") | Elecy | labour | SWR10112 | 1770 | EA | 14160
3 | 5.76 | Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RSupply Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. Fabrication of struc.with power drilling | Elecy | labour | SWR10868 | 6852 | TO | 39467.52
4 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | Elecy | supply | SMR40009 | 2181 | TO | 12562.56
5 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | Elecy | labour | SWR10877 | 851 | TO | 4901.76
6 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | Elecy | supply | SMR40010 | 1293 | TO | 7447.68
7 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | Elecy | labour | SWR10879 | 482 | TO | 2776.32
8 | 5.76 | Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | Elecy | labour | SWR10867 | 1470 | TO | 8467.2
9 | 16 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. Erection of RS Joist 150 x 150 mm | Elecy | labour | SWR10348 | 1952.61 | EA | 31241.76
10 | 17.758 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | Elecy | labour | SWR10356 | 6579 | M3 | 116829.882
11 | 9.24 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | Elecy | labour | SWR10862 | 373 | M2 | 3446.52
12 | 16 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | Elecy | labour | SWR11089 | 48 | EA | 768
13 | 5.063 | Fabrication & erection of Channels Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RSupply Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. Fabrication of struc.with power drilling | Elecy | labour | SWR10868 | 6852 | TO | 34691.676
14 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | Elecy | supply | SMR40009 | 2181 | TO | 11042.403
15 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium. Labour for 1st coat Al. Painting. | Elecy | labour | SWR10877 | 851 | TO | 4308.613
16 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | Elecy | supply | SMR40010 | 1293 | TO | 6546.459
17 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | Elecy | labour | SWR10879 | 482 | TO | 2440.366
18 | 5.063 | Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | Elecy | labour | SWR10867 | 1470 | TO | 7442.61
19 | 13 | Erection of AB Switch and aligment complete Erection of 33 KV AB Switch including alignment and earthing | Elecy | labour | SWR10392 | 4500 | EA | 58500
20 | 38 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Note:-The requirement of 2nd coat is to be justified by the concerned Divisional Engineer /Executive Engineer before execution of this work Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elecy | labour | SWR10881 | 142 | EA | 5396
21 | 38 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch AB Switch Coil Earthing GI No. 8 Wire | Elecy | labour | SWR12331 | 146.63 | EA | 5571.94
22 | 6 | Loading of 33 KV CTs/ PTs | Elecy | labour | SWR10200 | 165 | EA | 990
23 | 6 | Un loading of 33 KV CTs/ PTs | Elecy | labour | SWR10518 | 128 | EA | 768
24 | 2 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33kv single phase PT s | Elecy | labour | SWR10401 | 1079 | SET | 2158
25 | 12 | Loading of 33 KV, 10 KA LAs Station type | Elecy | labour | SWR10266 | 41 | EA | 492
26 | 12 | Un loading of 33 KV, 10 KA LAs Station type | Elecy | labour | SWR10584 | 35 | EA | 420
27 | 4 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33 KV LAS station/Line type including earthing | Elecy | labour | SWR10396 | 880 | SET | 3520
28 | 2 | Loading of 33 KV VCBs along with Panel boards | Elecy | labour | SWR10198 | 1024 | EA | 2048
29 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Above 10 Km and upto 20 Km with Lorry for each trip Transport of Cond Drum,VCBs >10 & <20Km | Elecy | labour | SWR11861 | 3299.7 | EA | 3299.7
30 | 2 | Un loading of 33 KV VCBs along with Panel boards | Elecy | labour | SWR10516 | 1044.48 | EA | 2088.96
31 | 12.58 | Excavate-Pit for 33KV VCB | Elecy | labour | SWR23224 | 331 | M3 | 4163.98
32 | 14.52 | Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x 1.8 x 0.75 cum for VCB Plinth | Elecy | labour | SWR20685 | 5160 | M3 | 74923.2
33 | 2 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33 KV VCB with Control Panel | Elecy | labour | SWR10460 | 12500 | EA | 25000
34 | 2 | Loading and unloading of PTR on constructed plinth LOADING of 8 MVA PTR | Elecy | labour | SWR10613 | 5805.84 | EA | 11611.68
35 | 2 | Transport of Power transformers (0 to 100 KM) from one place to another place in GHMC Area.(excluding of loading & unloading ) Transport of 8 MVA power transformer | Elecy | labour | SWR10854 | 21945 | EA | 43890
36 | 2 | UNLOADING of 8 MVA PTR | Elecy | labour | SWR10627 | 5805.84 | EA | 11611.68
37 | 700 | S/o rail poles 90/105lb (250x2N) | Elecy | supply | SMR22718 | 47.27 | KG | 33089
38 | 4 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Erection of Rail Pole 90Lbs | Elecy | labour | SWR10344 | 3510 | EA | 14040
39 | 2 | Erection of PTR on constructed plinth Erection of 8 MVA PTR. | Elecy | labour | SWR21321 | 49480.2 | EA | 98960.4
40 | 0.44 | Extention of 33KV Bay at 132/33KV Sub-station 33KV Bay Extn: Supply Zebra Conductor | Elecy | supply | SMR24910 | 299369 | KM | 131722.36
41 | 30 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing. | Elecy | supply | SMR11915 | 2055 | SET | 61650
42 | 30 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of I-Bolts | Elecy | supply | SMR22473 | 294 | EA | 8820
43 | 45 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 "to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating . Sup T clamp LM6 Al alloy of 12 mm, 800 A | Elecy | supply | SMR40011 | 299 | EA | 13455
44 | 6 | Bus stringing Hoisting of Insulators and hardware, stretching the conductor and stringing of 33 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bussection of 4.5mt) Hoisting post ins&hrd wr 1panther 33kv | Elecy | labour | SWR21240 | 781 | EA | 4686
45 | 218.67 | Stringing of bus with panther conductor including jumpering etc., complete to all the equipment in SS fixing to all clamps and equipment.(3 Conductors) Stringing of bus with panther conductor | Elecy | labour | SWR10404 | 327.68 | M | 71653.7856
46 | 30 | Bus stringing Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | Elecy | labour | SWR10884 | 224 | EA | 6720
47 | 75 | Labour for Fixing of all types of clamps | Elecy | labour | SWR10917 | 65 | EA | 4875
48 | 29 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Elecy | labour | SWR11039 | 928 | EA | 26912
49 | 10.12 | Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RSupply Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. Fabrication of struc.with power drilling | Elecy | labour | SWR10868 | 6852 | TO | 69342.24
50 | 10.12 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | Elecy | supply | SMR40009 | 2181 | TO | 22071.72
51 | 10.12 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | Elecy | labour | SWR10877 | 851 | TO | 8612.12
52 | 10.12 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | Elecy | supply | SMR40010 | 1293 | TO | 13085.16
53 | 10.12 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | Elecy | labour | SWR10879 | 482 | TO | 4877.84
54 | 10.12 | Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | Elecy | labour | SWR10867 | 1470 | TO | 14876.4
55 | 29 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Erection of RS Joist 150 x 150 mm | Elecy | labour | SWR10348 | 1952.61 | EA | 56625.69
56 | 32.19 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Mass concreting of supports incl. cement | Elecy | labour | SWR10356 | 6579 | M3 | 211778.01
57 | 16.75 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | Elecy | labour | SWR10862 | 373 | M2 | 6247.75
58 | 29 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. Ptg of coping with 2cts white cmnt inclu | Elecy | labour | SWR11089 | 48 | EA | 1392
59 | 5.588 | Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RSupply Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. Fabrication of struc.with power drilling | Elecy | labour | SWR10868 | 6852 | TO | 38288.976
60 | 5.588 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | Elecy | Supply | SMR40009 | 2181 | TO | 12187.428
61 | 5.588 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | Elecy | labour | SWR10877 | 851 | TO | 4755.388
62 | 5.588 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | Elecy | Supply | SMR40010 | 1293 | TO | 7225.284
63 | 5.588 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | Elecy | labour | SWR10879 | 482 | TO | 2693.416
64 | 5.588 | Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | Elecy | labour | SWR10867 | 1470 | TO | 8214.36
65 | 21 | Erection of 11KV 800A double throw AB Switches | Elecy | labour | SWR21277 | 3500 | EA | 73500
66 | 3 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Elecy | labour | SWR10393 | 3200 | EA | 9600
67 | 2 | Loading of 11 KV CT - PT Sets | Elecy | labour | SWR10201 | 190 | EA | 380
68 | 2 | Un loading of 11 KV CT - PT Sets | Elecy | labour | SWR10519 | 101 | EA | 202
69 | 2 | Erection of 11 KV three phase PTs | Elecy | labour | SWR10402 | 800 | SET | 1600
70 | 30 | Loading of 11 KV, 10 KA LAs Station type | Elecy | labour | SWR10264 | 32 | EA | 960
71 | 30 | Un Loading of 11 KV, 10 KA LAs Station type | Elecy | labour | SWR10582 | 32 | EA | 960
72 | 2 | Erection of 11 KV LAS station type including earthing | Elecy | labour | SWR10397 | 559 | SET | 1118
73 | 8 | Erection of 11 KV LAS line type including earthing | Elecy | labour | SWR10398 | 505 | SET | 4040
74 | 10 | Loading of 11 KV VCBs along with Panel boards | Elecy | labour | SWR10199 | 1024 | EA | 10240
75 | 5 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Transport of Cond Drum,VCBs >10 & <20Km | Elecy | labour | SWR11861 | 3299.7 | EA | 16498.5
76 | 10 | Un Loading of 11 KV VCBs along with Panel boards | Elecy | labour | SWR10517 | 1044.48 | EA | 10444.8
77 | 52 | Excavate-Pit for 33KV VCB | Elecy | labour | SWR23224 | 331 | M3 | 17212
78 | 60 | Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x 1.8 x 0.75 cum for VCB Plinth | Elecy | labour | SWR20685 | 5160 | M3 | 309600
79 | 10 | Erection of 11 KV VCB with Control Panel | Elecy | labour | SWR10461 | 12000 | EA | 120000
80 | 12 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing. | Elecy | Supply | SMR11915 | 2055 | SET | 24660
81 | 12 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367- 1961) Supply of I-Bolts | Elecy | Supply | SMR22473 | 294 | EA | 3528
82 | 45 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367- 1961) Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 " to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating . Sup T clamp LM6 Al alloy of 12 mm, 800 A | Elecy | Supply | SMR40011 | 299 | EA | 13455
83 | 2 | Bus Stringing Hoisting of Insulators and hardware, stretching the conductor and stringing of 11 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 3.5mt) Hoisting post ins&hrd wr 1panther 11kv | Elecy | labour | SWR21241 | 507 | EA | 1014
84 | 45 | Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | Elecy | labour | SWR10884 | 224 | EA | 10080
85 | 57 | Labour for Fixing of all types of clamps | Elecy | labour | SWR10917 | 65 | EA | 3705
86 | 696 | Laying of earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication 75x 8mm MS Flat / GI Flat. Laying of earth mat,excavation 75x 8mm | Elecy | labour | SWR10920 | 65 | RMT | 45240
87 | 1247 | Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) Earthing for raisers of SS Flat 50x6 mm. | Elecy | labour | SWR10919 | 41 | RMT | 51127
88 | 36 | Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Elecy | supply | SMR11482 | 3486 | EA | 125496
89 | 36 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elecy | labour | SWR10357 | 1234.2 | EA | 44431.2
90 | 36 | Providing of RCC collar to earth pit Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINESupply Providing of RCC collar | Elecy | labour | SWR10359 | 386 | EA | 13896
91 | 2 | Supply of Copper Flexible jumper with 75 X 8 of length 250 mm at neutral of Power tranformer end and 50 X 6 of length 50mm two Nos at double neutral end duly brasing with flexible jumper of capacity of 5kA/3 sec for power transformer neutral. SupCU Flexi jumper for Power T/F Neutral | Elecy | Supply | SMR40033 | 4725 | EA | 9450
92 | 2 | Providing of double earthing for neutral with flexible copper jumpers including arrangement by fixing M.S.Channel 100x50mm. | Elecy | labour | SWR11892 | 1323 | EA | 2646
93 | 4 | Loading of LT AB Cable 3X16+25 Sqmm | Elecy | labour | SWR11702 | 200 | DR | 800
94 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Transport of Cond Drum,VCBs>10 & <20Km | Elecy | labour | SWR11861 | 3299.7 | EA | 3299.7
95 | 4 | Un loading of LT AB Cable 3X16+25 Sqmm Drum | Elecy | labour | SWR11713 | 204 | DR | 816
96 | 90 | Providing of cable trench as per DATA-XII | Elecy | labour | SWR22093 | 3148 | RMT | 283320
97 | 3312 | Control Cable Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends . Lay-4C/10C 2.5Sqmm Control Cable | Elecy | labour | SWR11879 | 27 | M | 89424
98 | 270 | Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per specification (including cost of ferrules, lugs and glands) L-Cable Termination to Switchgear | Elecy | labour | SWR12510 | 27 | EA | 7290
99 | 4 | Supply of FRP PT Marshalling Box | Elecy | Supply | SMR40048 | 4463 | EA | 17852
100 | 4 | Erection of Marshalling boxes | Elecy | labour | SWR10940 | 374.85 | EA | 1499.4
101 | 1 | Loading of 220 V Batterry with charger | Elecy | labour | SWR11166 | 1612 | SET | 1612
102 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Transport of Cond Drum,VCBs>10 & <20Km | Elecy | labour | SWR11861 | 3299.7 | EA | 3299.7
103 | 1 | Un loading of 220 V Batterry with charger | Elecy | labour | SWR11147 | 1024 | SET | 1024
104 | 1 | Erection of 220 V, 80 AH battery in complete shape fit for charging . Conventional lead acid | Elecy | labour | SWR12295 | 7666 | EA | 7666
105 | 1 | Control Panels Supply of DC Annunciation & relay panel for 10 feeder panel including the cost of LED Indiacation lamps, VAA auxilairy relays, Electronic Hooters complete as per specification. Supply of DC Anunc.relay panel 8 feeders | Elecy | Supply | SMR40044 | 42500 | EA | 42500
106 | 1 | Supply of AC Supply panel inluding providing of changeover switch, SFU, metering unit, 32 A three phase MCB, 16 A Single phase MCB complete as per specification. Supply of AC Supply panel complete | Elecy | Supply | SMR40045 | 42000 | EA | 42000
107 | 8 | Supply of stepped tubular poles single way made of steel of length 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9 mm, 2.1 mtrs with outer dia 76.1 mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79 kgf as per IS 2713. Supply 9mtrs tubular poles single way | Elecy | Supply | SMR40051 | 13913 | EA | 111304
108 | 8 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE/CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA /OSRAM /SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty Supply 90W LED fixture set | Elecy | Supply | SMR11594 | 8200 | EA | 65600
109 | 8 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") Exca Hard pit w/o blast 0.76X0.76X1.83M | Elecy | labour | SWR11039 | 928 | EA | 7424
110 | 8 | Erection of tubular poles | Elecy | labour | SWR10955 | 1379 | EA | 11032
111 | 5.27 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Mass concreting of supports incl. cement | Elecy | labour | SWR10356 | 6579 | M3 | 34671.33
112 | 8 | Fixing of LED/Metal halide complete. | Elecy | labour | SWR10956 | 1268 | EA | 10144
113 | 45 | Supply & spreading of 20mm machine crushed metal (HBG) including cost of conveneyance of all materials, labour charges etc complete for finished item of work and directed by the engineer incharge Supply & Spreading of 20mm HBG metal | Elecy | labour | SWR10860 | 2113 | M3 | 95085
114 | 2 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M Ex of Hard pit w/o blast 0.75X0.9X1.95M | Elecy | labour | SWR11040 | 990.68 | EA | 1981.36
115 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete . Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | Elecy | Supply | SMR40009 | 2181 | TO | 1635.75
116 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | Elecy | labour | SWR10877 | 851 | TO | 638.25
117 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. (*)Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | Elecy | Supply | SMR40010 | 1293 | TO | 969.75
118 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. (*) Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium Labour for 2nd coat Al. Painting. | Elecy | labour | SWR10879 | 482 | TO | 361.5
119 | 1 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Erect-12Meter Box pole | Elecy | labour | SWR11267 | 3901.37 | EA | 3901.37
120 | 2.22 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc Mass concreting of supports incl. cement | Elecy | labour | SWR10356 | 6579 | M3 | 14605.38
121 | 1.16 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | Elecy | labour | SWR10862 | 373 | M2 | 432.68
122 | 2 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. Ptg of coping with 2cts white cmnt inclu | Elecy | labour | SWR11089 | 48 | EA | 96
123 | 1 | Construction of DTR Plinth RCC Column type DTR Plinth of size 1'X1'X10',topslab 4'x4'x6" & beam size 4'X8'X8" upto 160KVA Column type DTR Plinth topslab 4'x4'x6" | Elecy | labour | SWR21843 | 25967.57 | EA | 25967.57
124 | 1 | LOADING of 50,63,75&100kva DTR | Elecy | labour | SWR10195 | 350 | EA | 350
125 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Transport of Cond Drum,VCBs>10 & <20Km | Elecy | labour | SWR11861 | 3299.7 | EA | 3299.7
126 | 1 | UNLOADING of 50,63,75&100kva DTR | Elecy | labour | SWR10513 | 280 | EA | 280
127 | 1 | Erection of DTR's including loading and Unloading DTR on the Structure/Plinth etc Erection of 3 Phase DTRs 63,75 & 100 KVA E/r 3ph DTR inclu L&Un-L,T&C on plinth | Elecy | labour | SWR20905 | 1650 | EA | 1650
128 | 1 | Erection of AB Switch and aligment complete Erection of 11KV 200A TT type AB Switch including fixing of cross angles and alignment complete | Elecy | labour | SWR20102 | 1813.49 | EA | 1813.49
129 | 1 | Erect. of 11kv HG Fuseset incl earthing | Elecy | labour | SWR10395 | 740.52 | SET | 740.52
130 | 40 | Excavation & laying of UG Cable in Single Run Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders /Normal soil / CC/BT Road Lay-SR 11KV 3x185sqmm UG Cb HG/BC/CC/BT | Elecy | labour | SWR11920 | 465.46 | M | 18618.4
131 | 20 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) Raise-SR 11KV 3x185sqmm UG Cb on support | Elecy | labour | SWR11956 | 126.23 | M | 2524.6
132 | 2 | UG Cables Joints Making of Outdoor/Indoor End Termination OD/Idoor end termination 11kv 3x185 xlpe | Elecy | labour | SWR10390 | 2370.63 | EA | 4741.26
133 | 1 | Erection of LT distribution box including laying of LT cable from distribution box to LT OH line and DTR to distribution box including earthing of distribution box and crimping of lugs connecting of jumpers etc Erection of LT distribution box | Elecy | labour | SWR10674 | 1594.67 | EA | 1594.67
134 | 85 | Excavation & laying of UG Cable in Single Run Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders /Normal soil / CC/BT Road Lay-SR LT 3.5x95sqmm UG Cb HG/BC/CC/BT | Elecy | labour | SWR11925 | 377.63 | M | 32098.55
135 | 15 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) Raise-SR LT 3.5x95sqmm UG CB ON SUPPORT | Elecy | labour | SWR11961 | 85.43 | M | 1281.45
136 | 2 | UG Cables Joints Making of Outdoor/Indoor End Termination Sup of 31/2x185Sqmm UG O/D end term kits | Elecy | supply | SMR40140 | 550 | EA | 1100
137 | 2 | UG Cables Joints Making of Outdoor/Indoor End Termination Fixing of Oout Door/Indoor end termination LT 3 1/2 x185 Sqmm Cable OD/Idoor end termination LT 3 1/2 x 185 | Elecy | labour | SWR10765 | 968.9 | EA | 1937.8
138 | 1 | Supply and fixing of Substation board of size 3'x2.5' indicating the layout of switchyard Sup &fix of board ind Switchyard layout | Elecy | labour | SWR20032 | 1654 | EA | 1654
139 | 1 | Supply and fixing of safety instructions/Substation operation instruction board. Sup& fix safety inst/SS Op. inst board | Elecy | labour | SWR22090 | 2205 | EA | 2205
140 | 750 | Control Panels Supplying & fabrication erection of 6mm Checkerd plates as per the field conditions Supply,fabricati of 6mm Checkerd plates | Elecy | labour | SWR10873 | 83 | KG | 62250
141 | 1 | T & P Supply of Wall clock standard make | Elecy | supply | SMR40059 | 578 | EA | 578
142 | 1 | Supply 10ft Aluminium Ladder | Elecy | supply | SMR12378 | 1654 | EA | 1654
143 | 1 | Sup Alluminium Ladder for indoor works | Elecy | Supply | SMR40062 | 4410 | EA | 4410
144 | 30 | T & P Painting of Name Plates for any equipmen | Elecy | labour | SWR10963 | 122 | EA | 3660
145 | 1 | T & P Supply of Taparia Tool kit of Size 20”x10”x15” with tier arrangements Tool box with locking arrangement & key containing (1) Double Ended fix Spanner sets, (Ribbed) 6 x 7, 8 x 9, 10 x 11, 12 x 13, 14 x 15, 16 x 17, 18 x19, 20 x 22, 21 x 23, 24 x 27, 25 x28, 30 x 32, (2) Double Ended Ring Spanners sets, 6 x 7 , 8 x 9, 10 x 11, 12 x 13, 14 x 15. 16 x 17 , 18 x 19, 20 x 22 , 21 x 23, 24 x 27, 25 x28, 30 x 32 mm, (3) Adjustable Spanner 305 mm length least maximum opening 35mm chrome, (4) Pipe Wrench Length 350 mm 14”, (5) Soft faced Hammer with suitable handle 2 lb, (6) Hacksaw frame with metal handle heavy duty for 12" hacksaw blade with High Speed blade, (7) Insulated Screw drivers Transparent Green Handle Set Length 6”, 8” & 12”, (8) Star Screw Driver Transparent Green Handle Length 6”, (9) Insulated Wire Cutter, (10) Insulated Cutting Plier Length 8” with cable stripper insulated with thick C. A. sleeve confirming to IS: 4378 - 1990, (11) Long Nose Plier insulated with thick C.A. sleeve generally confirming to IS:3552-1989, (12) Tester type screw driver (special with neon bulb) generally confirm to IS: 5579- 1985 Grade:II handle yellow/ green colour overall length 130 mm, (13) Insulated Crimping Plier of all Taparia make. SupTaparia Tool kit complete as per Spec | Elecy | supply | SMR40063 | 4925 | SET | 4925
146 | 1 | T & P Sup Rechargeable LED torch light of Standard make | Elecy | supply | SMR40064 | 1733 | EA | 1733
147 | 1 | T & P Sup Steel almarah(61/2 X 3ft) Godrej | Elecy | supply | SMR40061 | 9818 | EA | 9818
148 | 1 | T & P Supply of Table (3x6ft) Godrej | Elecy | supply | SMR40057 | 6050 | EA | 6050
149 | 4 | T & P Supply of S type chairs (Godrej) | Elecy | supply | SMR40058 | 924 | EA | 3696
150 | 1 | T & P Sup Angle racks(18x36.6inches) Godrej | Elecy | supply | SMR40060 | 1733 | EA | 1733
151 | 1 | T & P Supply of Hack saw (12 inches) | Elecy | supply | SMR40065 | 289 | EA | 289
152 | 4 | Sup Earth Rods (8ft) Screw & clamp type | Elecy | supply | SMR40066 | 578 | EA | 2312
153 | 2 | Supply of Hand Gloves | Elecy | supply | SMR40067 | 289 | SET | 578
154 | 12 | SupRubber mats( 6'x3')size fo indoorSS | Elecy | supply | SMR40068 | 1386 | EA | 16632
155 | 1 | Biometric Time attendence System & Telecom Sup Stand basic cell phone with charger | Elecy | supply | SMR40069 | 1386 | EA | 1386
156 | 14 | Supply of Danger boards with clamps | Elecy | supply | SMR40070 | 116 | EA | 1624
157 | 2 | Supply of Materials Fire bucket stand with 3 buckets (8 -10 ltr capacity) Sup Fire Buckets Stand with Buckets | Elecy | supply | SMR40088 | 1386 | SET | 2772
158 | 2 | Room fire extinguisher (2 ltrs capacity) for control room Sup Fire Extinguisher for Control Room | Elecy | supply | SMR40089 | 4620 | EA | 9240
159 | 4 | Sup TrollyMounted Co2 (6.5Kgs) Cylinders(ISupply 2878) | Elecy | supply | SMR40087 | 9240 | EA | 36960
160 | 6 | Supply of Safety Helmet of standard make | Elecy | supply | SMR40071 | 231 | EA | 1386
161 | 8 | Supply of LC Boards | Elecy | supply | SMR40072 | 116 | EA | 928
162 | 4 | Supply of Gum Boots (pair) | Elecy | supply | SMR40073 | 693 | EA | 2772
163 | 1 | Supply of 5000v megger | Elecy | supply | SMR40074 | 13860 | EA | 13860
164 | 1 | Supply of Earth megger (1000v) | Elecy | supply | SMR40075 | 8085 | EA | 8085
165 | 1 | Supply of Digital clamp meter. | Elecy | supply | SMR40076 | 2888 | EA | 2888
166 | 1 | Name board of the 33/11kV Sub-Station(As per Standard Specification) Sup 33/11kv S.S Permanent name board | Elecy | supply | SMR40086 | 10238 | EA | 10238
167 | 800 | Supply of Hot dip galvanized/zinc coated bolts & nuts including spring washers, pack washers and flat washers etc. Supply Hot dip gal./Zinc bolts & nuts washer | Elecy | supply | SMR12488 | 90 | KG | 72000
168 | 4 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rockboulders) 8.0Mtrs PSCC Poles 0.76 M x 0.76M x 1.52M (2.6" x 2.6" x 5.0') 0.88 cum Ex of Hard pit w/o blast 0.76X0.76X1.52M | Elecy | labour | SWR11037 | 793 | EA | 3172
169 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | Elecy | supply | SMR40009 | 2181 | TO | 2181
170 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., completeLabour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | Elecy | labour | SWR10877 | 851 | TO | 851
171 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete (*)Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | Elecy | supply | SMR40010 | 1293 | TO | 1293
172 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete (*) Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | Elecy | labour | SWR10879 | 482 | TO | 482
173 | 3.51 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Mass concreting of supports incl. cement | Elecy | labour | SWR10356 | 6579 | M3 | 23092.29
174 | 2.31 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | Elecy | labour | SWR10862 | 373 | M2 | 861.63
175 | 4 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. Ptg of coping with 2cts white cmnt inclu | Elecy | labour | SWR11089 | 48 | EA | 192
176 | 5 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Erection of RS Joists 150x75/175 x 85 mm | Elecy | labour | SWR10346 | 1934 | EA | 9670
177 | 2 | Fixing of AC/DC Panel and giving Connections to the protection equipment and Metering circuits as per the specification and standards. The 3 1/2 core 25 Sqmm power cable required from distribution box to AC/DC panel in the control room is also to be supply | Elecy | labour | SWR20025 | 7871.85 | SET | 15743.7
178 | 2 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Elecy | labour | SWR10642 | 512.55 | EA | 1025.1
179 | 5760 | Supply RS Joist Grider Pole (150x150mm) | Elecy | Supply | SMR12302 | 59.25 | KG | 341280
180 | 5063 | Supply MS Channel 100x50mm | Elecy | Supply | SMR22745 | 57.45 | KGS | 290869.35
181 | 13 | Supply 33KV 800A DB Break AB Switch | Elecy | Supply | SMR12315 | 40658.78 | EA | 528564.14
182 | 10120 | Supply RS Joist Grider Pole (150x150mm) | Elecy | Supply | SMR12302 | 59.25 | KG | 599610
183 | 5588 | Supply MS Channel 100x50mm | Elecy | Supply | SMR22745 | 57.45 | KGS | 321030.6
184 | 21 | Supply 11KV 800A DB Break AB Switch | Elecy | Supply | SMR12316 | 30847.46 | EA | 647796.66
185 | 3 | Supply 11KV 400A DB Break AB Switch | Elecy | Supply | SMR12317 | 18150 | EA | 54450
186 | 3275 | Supply MS Flat 75x8mm | Elecy | Supply | SMR12321 | 56.42 | KG | 184775.5
187 | 2995 | Supply MS Flat 50x6mm | Elecy | Supply | SMR12322 | 56.5 | KG | 169217.5
188 | 750 | Supply RS Joist Pole (175x85mm) | Elecy | Supply | SMR12303 | 60.75 | KG | 45562.5
189 | 1 | Supply 11KV 200A Tilting Type AB Switch | Elecy | Supply | SMR12318 | 8991 | EA | 8991
190 | 1 | Supply 11KV HG FuseSet for StationTransformer | Elecy | Supply | SMR12324 | 1974 | EA | 1974
191 | 1 | Supply LT Distribution Box (SMC) | Elecy | Supply | SMR25200 | 7797 | EA | 7797
192 | 2 | Supply 11KV 3x185 Heat Shble O/d End Term Kit | Elecy | Supply | SMR25201 | 1182.97 | EA | 2365.94
193 | 40 | Supply LT 1Core 120Ssqmm XLPE Al. Cable | Elecy | Supply | SMR25030 | 3118.66 | M | 124746.4
194 | 1000 | Supply RS Joist Pole (175x85mm) | Elecy | Supply | SMR12303 | 60.75 | KG | 60750
195 | 100 | Supply of LT XLPE Cable 3 1/2 C 185 sqmm | Elecy | Supply | SMR25204 | 547 |  | 54700
196 | 6.29 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) (other than SS) Earth work excav hard rock bould <3cum | Elecy | labour | SWR10856 | 1318.35 | M3 | 8292.4215
197 | 7.26 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Mass concreting of supports incl. cement | Elecy | labour | SWR10356 | 6579 | M3 | 47763.54
198 | 1.8 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | Elecy | supply | SMR40009 | 2181 | TO | 3925.8
199 | 1.8 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. (*)Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | Elecy | supply | SMR40010 | 1293 | TO | 2327.4
200 | 1.8 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | Elecy | labour | SWR10877 | 851 | TO | 1531.8
201 | 1.8 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. (*) Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium Labour for 2nd coat Al. Painting. | Elecy | labour | SWR10879 | 482 | TO | 867.6
202 | 2 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Erection of RS Joist 150 x 150 mm | Elecy | labour | SWR10348 | 1952.61 | EA | 3905.22
203 | 895 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends . Lay-4C/10C 2.5Sqmm Control Cable | Elecy | labour | SWR11879 | 27 | M | 24165
204 | 2 | Sup MS Powder coated CT Marshalling Box | Elecy | supply | SMR40047 | 3675 | EA | 7350
205 | 2 | Erection of Marshalling boxes | Elecy | labour | SWR10940 | 374.85 | EA | 749.7
206 | 12 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing. Supply Tension HW 3Bolt 1Zebra/Pnthr 150mm | Elecy | supply | SMR11915 | 2055 | SET | 24660
207 | 32 | Laying of earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication 75x 8mm MS Flat / GI Flat. Laying of earth mat,excavation 75x 8mm | Elecy | labour | SWR10920 | 65 | RMT | 2080
208 | 5 | Supply of earthing pipe with materials Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication Supply CI Pipe earthing 100mm dia 2.75m long | Elecy | supply | SMR11482 | 3486 | EA | 17430
209 | 5 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4Mts.) duly filling with bentonite, earth , running of earth wireetc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height ERECT. OF LINESupply Providing of earthing | Elecy | labour | SWR10357 | 1234.2 | EA | 6171
210 | 5 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X0.50 M height ERECT. OF LINESupply Providing of RCC collar | Elecy | labour | SWR10359 | 386 | EA | 1930
211 | 6 | Bus Stringing Hoisting of Insulators and hardware, stretching the conductorand stringing of 33 kV bus comprising of three phases withSingle Zebra/panther conductor to a tension of 450kgs.(Bussection of 4.5mt) Hoisting post ins&hrd wr 1panther 33kv | Elecy | labour | SWR21240 | 781 | EA | 4686
212 | 200 | Cable terminations to the switch gear marshalling boxes/panelterminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per specification (including cost of ferrules, lugs and glands) Lay-Cable Terminations to Switchgear | Elecy | labour | SWR11880 | 34.43 | EA | 6886
213 | 1 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33 KV LAS station/Line type including earthing Erect of 33kv LA stn type incl earthing | Elecy | labour | SWR10396 | 880 | SET | 880
214 | 1 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33kv VCB with Control Panel | Elecy | labour | SWR10460 | 12500 | EA | 12500
215 | 7.5 | Supply of HBG metal Supply & spreading of 20mm machine crushed metal (HBG)including cost of conveneyance of all materials, labour charges etc complete for finished item of work and directed by the engineer incharge Supply & Spreading of 20mm HBG metal | Elecy | labour | SWR10860 | 2113 | M3 | 15847.5
216 | 2 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Painting of operating rods of 33kV, 11kV AB switches withpost office red colour (including cost of paint) Painting AB switch OP rods with PO red | Elecy | labour | SWR10881 | 142 | EA | 284
217 | 1 | LOADING of 33 KV VCBs&Panel boards | Elecy | labour | SWR10198 | 1024 | EA | 1024
218 | 1 | UNLOADING of 33 KV VCBs&Panel boards | Elecy | labour | SWR10516 | 1044.48 | EA | 1044.48
219 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excludingof loading unloading) Transport of Cond Drum,VCBs upto 10Km | Elecy | labour | SWR11860 | 2720.34 | EA | 2720.34
220 | 2 | Erection of 33kv ABSwitch including alignment and earthing | Elecy | labour | SWR10392 | 4500 | EA | 9000
221 | 2 | Excavation of pits in all soils except hard rock requiring blasting 12Mtrs/Spun Pole 0.92 M x 0.92M x 2.3M (3.0" x 3.0" x 7.6") 1.94 cum EXCAVATION OF PIT(3.0" x 3.0" x 7.6") | Elecy | labour | SWR10109 | 842.78 | EA | 1685.56
222 | 48 | Labour for Fixing of all types of clamps | Elecy | labour | SWR10917 | 65 | EA | 3120
223 | 20 | Stringing of bus with panther conductor including jumpering etc., complete to all the equipment in SS fixing to all clampsand equipment.(3 Conductors) Stringing of bus with panther conductor | Elecy | labour | SWR10404 | 327.68 | M | 6553.6
224 | 45 | Fabrication of materials including 2 coats of Red oxide painting Fab Back clamps with 50 x 6 mm MS Flat | Elecy | labour | SWR10320 | 15 | EA | 675
225 | 2.114 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metalincluding the cost of metal, sand, Cement and curing etc. Mass concreting of supports incl. cement | Elecy | labour | SWR10356 | 6579 | M3 | 13908.006
226 | 1.8 | Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to theRSupply Joist poles excluding cost of Mild Steel and transportcharges to substation site, including erection. Fabrication of struc.with welding. | Elecy | labour | SWR10869 | 3426 | TO | 6166.8
227 | 1000 | Supply RS Joist Grider Pole (150x150mm) | Elecy | Supply | SMR12302 | 59.25 | KG | 59250
228 | 150 | Supply MS Flat 75x8mm | Elecy | Supply | SMR12321 | 56.42 | KG | 8463
229 | 90 | Supply MS Flat 50x6mm | Elecy | Supply | SMR12322 | 56.5 | KG | 5085
230 | 800 | Supply MS Channel 100x50mm | Elecy | Supply | SMR22745 | 57.45 | KGS | 45960
231 | 2 | Supply 33KV 800A DB Break AB Switch | Elecy | Supply | SMR12315 | 40658.78 | EA | 81317.56
232 | 9.4 | survey line&cabl inc peg mark&tree clear | Elecy | labour | SWR22092 | 765 | KM | 7191
233 | 10 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. Erect-12Meter Box pole | Elecy | labour | SWR11267 | 3901.37 | EA | 39013.7
234 | 20 | Fabrication of poles: Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. Fabrication of 175x85/150x75mm RS joist | Elecy | labour | SWR10642 | 512.55 | EA | 10251
235 | 20 | Painting of poles Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables Painting of RS Joist(1C RO, 2C Al.Paint) | Elecy | labour | SWR10640 | 1132 | EA | 22640
236 | 9.73 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Mass concreting of supports incl. cement | Elecy | labour | SWR10356 | 6579 | M3 | 64013.67
237 | 2 | Formation of Cut point for 33 KV Double circuit line excluding pole erection and stays Formation of 33kvline vertical cutpoint | Elecy | labour | SWR10466 | 3198.72 | EA | 6397.44
238 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Elecy | Supply | SMR40009 | 2181 | TO | 1635.75
239 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Elecy | labour | SWR10877 | 851 | TO | 638.25
240 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. (*)Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. | Elecy | Supply | SMR40010 | 1293 | TO | 969.75
241 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. (*) Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium Labour for 2nd coat Al. Painting. | Elecy | labour | SWR10879 | 482 | TO | 361.5
242 | 6 | LOADING of 33 KV Pin insulators | Elecy | labour | SWR10211 | 3 | EA | 18
243 | 6 | UNLOADING of 33 KV Pin insulators | Elecy | labour | SWR10529 | 3 | EA | 18
244 | 1 | LOADING of 33KV Metal partSupply bag of 25no | Elecy | labour | SWR10618 | 65 | BAG | 65
245 | 50 | Supply of earthing pipe with materials Supply GI Bolts & Nuts,Washers etc., | Elecy | Supply | SMR11488 | 117.5 | KG | 5875
246 | 32 | Load-11/33KV XLPE UG Cable for all sizes | Elecy | labour | SWR11230 | 1024 | DR | 32768
247 | 32 | Unload-11/33KV XLPE UG Cable all sizes | Elecy | labour | SWR11231 | 1024 | DR | 32768
248 | 9400 | Excavation & laying of UG Cable in Single Run Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. Along the CC / BT multi layer road requiring compresso Lay-SR 33KV 3x400sqmm UG Cb CC/BT Compsr | Elecy | labour | SWR11927 | 1175.56 | M | 11050264
249 | 100 | Excavation & laying of UG Cable in Single Run Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) Raise-SR 33KV 3x400sqmm UG Cb on support | Elecy | labour | SWR11954 | 135.66 | M | 13566
250 | 10 | Making of Outdoor/Indoor End Making 33 KV 3x400 Sqmm Cable Out Door/Indoor end termination TerminationOD/Idoor end termination 33kv 3x400 xlpe | Elecy | labour | SWR10387 | 2764.76 | EA | 27647.6
251 | 35 | UG Cables Joints 33 KV 3x400 Sqmm Cable Straight through joint 33kv 3x400 xlpe | Elecy | labour | SWR10382 | 5700.78 | EA | 199527.3
252 | 3 | Erection of 33kv ABSwitch including alignment and earthing | Elecy | labour | SWR10392 | 4500 | EA | 13500
253 | 3 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Painting of operating rods of 33kV, 11kV AB switches withpost office red colour (including cost of paint) Painting AB switch OP rods with PO red | Elecy | labour | SWR10881 | 142 | EA | 426
254 | 9 | Supply of earthing pipe with materials Supply CI Pipe earthing 50mm dia 2m long | Elecy | Supply | SMR11484 | 2441 | EA | 21969
255 | 9 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINESupply Providing of RCC collar | Elecy | labour | SWR10359 | 386 | EA | 3474
256 | 9 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height ERECT. OF LINESupply Providing of earthing | Elecy | labour | SWR10357 | 1234.2 | EA | 11107.8
257 | 80 | Supply Earthing GI flat 25x3 mm incl material | Elecy | Supply | SMR11485 | 105 | KG | 8400
258 | 16 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Above 10 Km and upto 20 Km with Lorry for each trip | Elecy | labour | SWR11861 | 3299.7 | EA | 52795.2
259 | 3 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Elecy | labour | SWR12331 | 146.63 | EA | 439.89
260 | 0.75 | Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to theRSupply Joist poles excluding cost of Mild Steel and transportcharges to substation site, including erection. Fabrication of struc.with welding. | Elecy | labour | SWR10869 | 3426 | TO | 2569.5
261 | 3 | Supply 33KV 800A DB Break AB Switch | Elecy | supply | SMR12315 | 40658.78 | EA | 121976.34
262 | 5000 | Supply RS Joist Pole (175x85mm) | Elecy | supply | SMR12303 | 60.75 | KG | 303750
263 | 500 | Supply MS Channel 100x50mm | Elecy | supply | SMR22745 | 57.45 | KGS | 28725
264 | 250 | Supply MS Flat 50x6mm | Elecy | supply | SMR12322 | 56.5 | KG | 14125
265 | 35 | Supply of 33KV3x400Sqmm Straight thr kit | Elecy | supply | SMR22223 | 24151 | EA | 845285
266 | 10 | Supply of 33KV 3x400Sqmm O/D End Kit | Elecy | supply | SMR22222 | 4554 | EA | 45540
267 | 8 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 12Mtrs/Spun Pole 0.92 M x 0.92M x 2.3M (3.0" x 3.0" x 7.6") | Elecy | labour | SWR11041 | 1466.25 | EA | 11730
268 | 8 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. Erect-12Meter Box pole | Elecy | labour | SWR11267 | 3901.37 | EA | 31210.96
269 | 16 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. Fabrication of 175x85/150x75mm RS joist | Elecy | labour | SWR10642 | 512.55 | EA | 8200.8
270 | 16 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables Painting of RS Joist(1C RO, 2C Al.Paint) | Elecy | labour | SWR10640 | 1132 | EA | 18112
271 | 8.87 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Mass concreting of supports incl. cement | Elecy | labour | SWR10356 | 6579 | M3 | 58355.73
272 | 4800 | Excavation & laying of UG Cable in Single Run Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. Along the CC / BT multi layer road requiring compressor Lay-SR 11KV 3x300sqmm UG Cb CC/BT Compsr | Elecy | labour | SWR11928 | 1073.94 | M | 5154912
273 | 200 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) Raise-SR 11KV 3x300sqmm UG Cb on support | Elecy | labour | SWR11955 | 144.08 | M | 28816
274 | 10 | Making 11 KV 3x300 Sqmm Cable Out Door/Indoor end termination OD/Idoor end termination 11kv 3x300 xlpe | Elecy | labour | SWR10391 | 2370.63 | EA | 23706.3
275 | 10 | Straight through joint 11kv 3x300 xlpe | Elecy | labour | SWR10386 | 3725.45 | EA | 37254.5
276 | 4 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Elecy | labour | SWR10393 | 3200 | EA | 12800
277 | 4 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Painting of operating rods of 33kV, 11kV AB switches withpost office red colour (including cost of paint) Painting AB switch OP rods with PO red | Elecy | labour | SWR10881 | 142 | EA | 568
278 | 10 | Supply of Danger boards with clamps | Elecy | Supply | SMR40070 | 116 | EA | 1160
279 | 12 | Supply CI Pipe earthing 50mm dia 2m long | Elecy | Supply | SMR11484 | 2441 | EA | 29292
280 | 12 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINESupply Providing of RCC collar | Elecy | labour | SWR10359 | 386 | EA | 4632
281 | 12 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4Mts.) duly filling with bentonite, earth , running of earth wireetc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height ERECT. OF LINESupply Providing of earthing | Elecy | labour | SWR10357 | 1234.2 | EA | 14810.4
282 | 80 | Supply of earthing pipe with materials Supply of GI Flat 25X3 mm including material | Elecy | Supply | SMR11485 | 105 | KG | 8400
283 | 10 | Load-11/33KV XLPE UG Cable for all sizes | Elecy | labour | SWR11230 | 1024 | DR | 10240
284 | 10 | Unload-11/33KV XLPE UG Cable all sizes | Elecy | labour | SWR11231 | 1024 | DR | 10240
285 | 4 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Elecy | labour | SWR12331 | 146.63 | EA | 586.52
286 | 5 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Above 10 Km and upto 20 Km with Lorry for each trip Transport of Cond Drum,VCBs >10 & <20Km | Elecy | labour | SWR11861 | 3299.7 | EA | 16498.5
287 | 4000 | Supply RS Joist Pole (175x85mm) | Elecy | Supply | SMR12303 | 60.75 | KG | 243000
288 | 700 | Supply MS Channel 100x50mm | Elecy | Supply | SMR22745 | 57.45 | KG | 40215
289 | 350 | Supply MS Flat 75x8mm | Elecy | Supply | SMR12321 | 56.42 | KG | 19747
290 | 200 | Supply MS Flat 50x6mm | Elecy | Supply | SMR12322 | 56.5 | KG | 11300
291 | 10 | Supply 11KV 3x300 Heat Shble str thr JointKit | Elecy | Supply | SMR25210 | 4110.17 | EA | 41101.7
292 | 10 | Supply 11KV 3x300 Heat Shble O/d End Term Kit | Elecy | Supply | SMR25208 | 1372.88 | EA | 13728.8
293 | 4 | Supply 11KV 400A Conv ABSwitch with Insulatorsub total | Elecy | Supply | SMR25211 | 11754 | EA | 47016
Electrical Amount | [7 empty] | 26535555.0141
\
1 | 32 | Leveliing the site by cutting and levelling with the help of JCB including cost,conveyance of all materials,hire chareges etc complete for finished item of work as directed by Engineer-in-charge. | Civil | Labour | SWR34179 | 2165 | Hrs | 69280
2 | 149.95 | Earth Work Mass Excavation (hard rock) to a depth as directed, in soils such as hard rock requiring blasting in prohibited area and all conditions such as dry, wet, slurry etc.and in dense or hard soils, disposal and depositing of excavated soil with intial lead of 10 mt and intial lift of 2m or as directed, including cost and conveyance of all materials, ramping and lifting of materials, and labour charges, hire charges of machinery, tools & plants, bailing of water ( either sub soil water, stoMts water, rain water, surface water or of any kind) if any at any stage of work until all works below ground level is finished to the satisfaction ,and from work such as shoring, timbering, strutting with required supports etc. for the work and removal of form work after completion of work etc all complete as directed by the engineer-incharge. | Civil | Labour | SWR33018 | 1440 | cum | 215928
3 | 115.65 | Earth work excavation in all type of ordinary soils red earth, Hard gravelly soils, earth mixed with sand and sandy soils etc., in all conditions such as slushy and dry with initial leads and lifts for foundations. Ordinary Soil | Civil | Labour | SWR33015 | 486 | cum | 56205.9
4 | 22.79 | PCC (1:4:8) using 40 mm metal with concrete Mixture. All work upto Plinth level including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete as directed by Engineer incharge of the work | Civil | Labour | SWR33028 | 4688 | cum | 106839.52
5 | 108.3 | Coursed Rubble stone CRS masonry 2nd sort with hard granite stones in cement mortar CM (1:6) for basement, including cost and conveyance of all materials, labour charges, curing, all leads and lifts, etc, complete for finished item of work. | Civil | Labour | SWR33041 | 4833 | cum | 523413.9
6 |  | RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge
7 | 1.09 | RCC M20 Grade Footing 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33098 | 9439 | cum | 10288.51
8 | 1.58 | RCC M20 Grade Column 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33100 | 13188 | cum | 20837.04
9 | 1.15 | RCC M20 Grade plinth beam 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33099 | 12310 | cum | 14156.5
10 | 0.46 | Reinforcement steel Supplying, Cutting, bending, binding, placing in position and tying reinforcement steel in all heights including cost and conveyance of steel and binding wire etc,. With all leads and lifts, labour charges, etc., complete for finished item of work. | Civil | Labour | SWR33144 | 70687 | MT | 32516.02
11 | 66.71 | Brick masonry in CM (1:6) for superstructure using well burnt country made second class bricks of approved quality including cost and conveyance of all materials curing, scaffolding with all leads and lifts in all heights etc., complete for finished item of work | Civil | Labour | SWR33068 | 8248 | cum | 550224.08
12 | 6.98 | PCC (1:2:4) using 20mm size well graded HBG metal for foundations, including cost, conveyance of all materials,labour all leads and lifts,consolidation and all operations, formwork as required, curing,etc. complete for finished item of work | Civil | Labour | SWR33030 | 6057 | cum | 42277.86
13 | 630.95 | Plastering with CM 2 coats, 20 mm thick, base coat in CM (1:6), 16 mm thick and top coat in CM (1:4), 4mm thick with Dubara sponze finishing including cost of all materials, seigniorage charges, excluding conveyance charges of materials and including all operational, incidental and labour charges for mixing mortar, laying rendering smooth and thread lining, curing, rounding off junctions of wall and slab etc., complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33163 | 560 | Sqm | 353332
14 | 27 | Painting with two coats of Plastic Emulsn paint over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33356 | 210 | Sqm | 5670
15 | 781.85 | Painting with two coats of Surya Cem paint over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33329 | 85 | Sqm | 66457.25
16 | 380 | Supplying and fixing Structural Steel angles channal etc.Manufacturing, Supplying and fixing of MS grill for (Gate and raillings) of approved design as per drawings, including cost and conveyance of all materials, labour charges etc.,complete for finished item of work as directed by the Engineer- in-charge. | Civil | Labour | SWR33145 | 128 | Kgs | 48640
17 | 3 | Supply and Fixng of MS Name Board including cost & conveyance of all materials,labour charges etc complete for finished item of work. | Civil | Labour | SWR33421 | 4326 | sqm | 12978
18 | 1 | Geophysical Investgation charges for water point by Geologist | Civil | Labour | SWR33608 | 5000 | EA | 5000
19 |  | Drilling of 165mm bore well with machine rig including deployment and hire charges of rig and other machinery and equipment labour charges , measuring the yeild of borewell including cost and conveyance etc complete
| 90 | Drill-165mm Bore Well 0 to 90 | Civil | Labour | SWR33609 | 336 | M | 30240
| 30 | Drill-165mm Bore Well 90M to 120M | Civil | Labour | SWR34830 | 369 | M | 11070
| 30 | Drill-165mm Bore Well 120M to 150M | Civil | Labour | SWR34831 | 394 | M | 11820
| 30 | Drill-165mm Bore Well 150M to 180M | Civil | Labour | SWR34832 | 492 | M | 14760
| 30 | Drill-165mm Bore Well 180M to 210M | Civil | Labour | SWR34833 | 623 | M | 18690
| 30 | Drill-165mm Bore Well 210M to 240M | Civil | Labour | SWR34834 | 754 | M | 22620
| 30 | Drill-165mm Bore Well 240M to 270M | Civil | Labour | SWR34835 | 918 | M | 27540
| 100 | Drill-165mm Bore Well 270M and above | Civil | Labour | SWR34836 | 1082 | M | 108200
20 | 40 | Supply and fixing of 160mm dia PVC casing of A class 6Kg point pressure including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR33611 | 883 | M | 35320
21 | 1 | Supply and erecting, ISI mark submersible 5.0 HP, three Phase 30 stages pumpset suitable for 106/156mm dia borewell including cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33640 | 48007 | EA | 48007
22 | 312 | Supply and fixing of HDPE pipe 40mm dia of 16Kg/cm2 including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR34410 | 180 | M | 56160
23 | 1 | Supply and erecting D.O.L Starter 415V ,3 phase,50Hz with SS enclouserincluding cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33645 | 7854 | EA | 7854
24 | 360 | Supply of 3 Core 2.5 Sqmm Flat Copper cable of ISI for Submersible Motors of makes Finolex / Polycab / Gold Medal / Million / Payal / Sun Light / Power Flex / Fortune Art | Civil | Labour | SWR33641 | 192 | M | 69120
25 | 6 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-28.60mm OD Pipe - SDR 11 | Civil | Labour | SWR34363 | 410 | M | 2460
26 | 1 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type - 25mm NB Size | Civil | Labour | SWR34346 | 466 | EA | 466
27 | 64.95 | Earth work excavation in all type of ordinary soils red earth, Hard gravelly soils, earth mixed with sand and sandy soils etc., in all conditions such as slushy and dry with initial leads and lifts for foundations. | Civil | Labour | SWR33015 | 486 | Cum | 31565.7
28 | 13.54 | PCC (1:4:8) using 40mm HBG metal for foundations and leveling course, including cost and conveyance of all materials, labour all leads and lifts, consolidation and all operations, formwork as required, curing, etc. complete for finished item w | Civil | Labour | SWR33028 | 4688 | Cum | 63475.52
29 | 26.08 | CRS Coursed Rubble Stone masonry 2nd sort with hard granite stones in cement mortar (1:6) for basement, including cost and conveyance of all materials, labour charges, curing, all leads and lifts, etc, complete for finished item of work. | Civil | Labour | SWR33041 | 4833 | Cum | 126044.64
30 | 51.88 | Supplying and filling the substation site with borrowed gravel, watering, ramming, thoroughly complying with the standard specification. | Civil | Labour | SWR33052 | 309 | Cum | 16030.92
31 |  | 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge
32 | 3.56 | a) RCC M20 Grade Footings 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33098 | 9439 | Cum | 33602.84
33 | 2.28 | b)RCC M20 Grade Columns 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33100 | 13188 | Cum | 30068.64
34 | 2.25 | c)RCC M20 Grade Plinth Beams 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33099 | 12310 | Cum | 27697.5
35 | 3.17 | D) RCC M20 Grade Roof Beams 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33121 | 12226 | Cum | 38756.42
36 | 0.58 | e) RCC M20 Grade Lintels 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33107 | 13018 | Cum | 7550.44
37 | 2.7 | f) RCC M20 Grade Sunshades 600mm wide and 75mm thick 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33114 | 1372 | Sqm | 3704.4
38 | 15.22 | g) RCC M20 Grade Roof Slab 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33128 | 10814 | Cum | 164589.08
39 | 3 | reinforcement steel Supplying, Cutting, bending, binding, placing in position and tying reinforcement steel in all heights including cost and conveyance of steel and binding wire etc,. With all leads and lifts, labour charges, etc., complete for finished item of work. | Civil | Labour | SWR33144 | 70687 | MT | 212061
40 | 38.36 | Brick masonry in CM (1:6) for superstructure using well burnt country made second class bricks of approved quality including cost and conveyance of all materials curing, scaffolding with all leads and lifts in all heights etc., complete for fin | Civil | Labour | SWR33068 | 8248 | Cum | 316393.28
41 | 517.26 | Plastering with CM 2 coats, 20 mm thick, base coat in CM (1:6), 16 mm thick and top coat in CM (1:4), 4mm thick with Dubara sponze finishing including cost of all materials, seigniorage charges, excluding conveyance charges of materials and including all operational, incidental and labour charges for mixing mortar, laying rendering smooth and thread lining, curing, rounding off junctions of wall and slab etc., complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33163 | 560 | Sqm | 289665.6
42 | 16.56 | Providing Design R.C.M. drop wall of 40mm thickness with cm 1:2 and 6mm dia MS bars at 150mm both ways and chicken mesh in two coats 20mm thick each plastering including cost and conveyance of all materials with leads and lifts, scaffolding and curing, labo | Civil | Labour | SWR33203 | 3044 | Sqm | 50408.64
43 | 12.24 | Supply and fixing of MS ornamental safety grill of approved design including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33310 | 2990 | sqm | 36597.6
44 | 5.91 | Supply and fixing of doors with the MT Wood frames the door shall be made well seasoned mt wood of cross section 100x75mm. The shutter shall be made isi mark flushed door with decolam sheets pasted on both sides with PVC beading 40mm width all round.Frame shall be painted with two coats of synthetic enamel paint of approved color over one coat of primer over luppum with spary with 3 no 150mm brass hinges 1 no brass door stoper, 1 no 250mm brass aldrops. 2 no 300 mm aluminium tower bolts, 2 no 150mm brass fancy door handlers, 1 no keyless lockset with cp handel. The quoted rate shall include cost and conveyance of the meterials, fixig, labour carges, tools, handles,locking arrangementts and other fixtures & fittings for finished item work as directed by the Engineer - in- charge. | Civil | Labour | SWR33264 | 7314 | Sqm | 43225.74
45 | 20.25 | Raised pointing to the exposed surfaces of CRS masonry in cm 1:3 prop. including cost and conveyance of all materials, labour charges, all leads and lifts curing etc, complete for finished item of work. | Civil | Labour | SWR33184 | 124 | sqm | 2511
46 | 8.64 | Supplying and fixing Aluminium sliding windows with grill and fixed glass panels using anodised aluminium extruded sections of mat finish for frames and mullions made from approved aluminium sections 62x32x1.2mm at 0.73kg/Rm providing 5mm plain glass fix | Civil | Labour | SWR33277 | 3623 | sqm | 31302.72
47 | 16.56 | Supply and laying of Ceramic floor over of CM 1:3 20 mm thick including required materials and labour charges etc complete for item of work | Civil | Labour | SWR33224 | 914 | Sqm | 15135.84
48 | 121.92 | Flooring with double machine polished and hand cut Tandur blue stone 20mm thick of approved colour, quality and of minimum of 300x300mm size over a bed of cement mortar 1:3 20mm thick including cost of all materials, with all leads and lifts jointing and | Civil | Labour | SWR33219 | 785 | Sqm | 95707.2
49 | 6.74 | Supply and fixing of 4" high skirting of shabad stone to the walls including cost and conveyance of all materials, labour etc for finished item of work. | Civil | Labour | SWR33236 | 875 | Sqm | 5897.5
50 | 243.69 | Painting with two coats of OBD over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials labour charges etc., complete for finished item of work. | Civil | Labour | SWR33333 | 146 | Sqm | 35578.74
51 | 349.52 | Painting with two coats of Plastic emulsn paint 2 coat of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33356 | 210 | Sqm | 73399.2
52 | 101.17 | Providing impervious coat over RCC roof slab to requried slopes with 20mm thick in CM 1:3 mixed with approved brand of water proffing compound inclding cost and conveyance of all materials, labour charges, curing, rounding off junctions of wall and slab, all leads and lifts, etc . complete for finished item of work as directed by the Engineer - in - charge. | Civil | Labour | SWR33156 | 582 | Sqm | 58880.94
53 | 60 | Supply & fixing of 25mm dia 2mm thick surface P.V.C. pipe (ISI MARK) Concealed in wall with all required accessories including masonary work and labour charges etc.complete. | Civil | Labour | SWR33441 | 108 | M | 6480
54 | 1 | Supply & fixing TPNDB Distribution board with IP-42 protection (Metal Door)suitable for 3 phase ELCB/RCCB/FP Isolator as incomer and 10kA SP MCBs as out going including internal connection and labour charges for surface / flush mounting etc Complete. | Civil | Labour | SWR33526 | 11353 | EA | 11353
55 | 10 | Supply & fixing Flush type of 6A 3 pin wall plug socket with 6A switch control on a common switch board with earth continuity including wire leads,earth connection along with all labour charges etc., complete | Civil | Labour | SWR33468 | 166 | EA | 1660
56 | 6 | Supply & fixing Flush type of 16A 3 pin and 6A 3pin plug Flush type socket with indicator lamp and 16Amps fuse unit and 16Amps switch control (5 in one )duly recessed in wall with wooden deep box of 6'' x 8'' x 2 1/2'' size covered with hylam sheet earth connection and all labour charges etc., complete on wall. | Civil | Labour | SWR33470 | 449 | EA | 2694
57 | 24 | Supply and Fixing of modular switch, LP,FP,EFP,Wiring with 2 runs of 14/0.3mm (1.0 sq.mm)Fire Retardant (FR) P.V.C. insulated flexible copper cable (ISI MARK) in existing pipe with 6A Flush type Switch,ceiling rose and 3mm thick hylam sheet covering to switch control box including all labour charges etc., complete for light points, bell , fan and exhaust fan points in Non-Residential Buildings. | Civil | Labour | SWR33457 | 676 | EA | 16224
58 | 12 | Supply & Fixing of 28W T5 fluorescent tube. | Civil | Labour | SWR33558 | 148 | EA | 1776
59 | 1 | Supply of 12" (300mm)ISI, 900 RPM light duty exhaust fan with metallic blades with Mark of makes Crompton / Bajaj / Havells / Orient. | Civil | Labour | SWR33571 | 2192 | EA | 2192
60 | 180 | Supply and run of 2 of 22/0.3mm (1.5 sq.mm) (FR) P.V.C. insulated flexible copper cable in existing pipe for mains including all labour charges complete. | Civil | Labour | SWR33496 | 75 | M | 13500
61 | 180 | Supply and run of 2 of 36/0.3mm (2.5 sq.mm) FR P.V.C. insulated flexible copper cable in existing pipe for mains including all labour charges complete. | Civil | Labour | SWR33497 | 103 | M | 18540
62 | 12 | Supply & fixing of batten holder /slanting holder in lieu of ceiling rose of light point complete with all connection and all labour charges with 40W bulb (for new installation). | Civil | Labour | SWR33484 | 141 | EA | 1692
63 | 4 | Supply & fixing of 1200mm (48'') sweep 230v,A.C 50 Hz.Ceiling fan with 3 Blades and double ball bearings with all standared accessories. | Civil | Labour | SWR33563 | 2277 | EA | 9108
64 | 4 | Supply & fixing of Electronic Regulator for ceiling fans 900/1200/1400mm sweep including cost of material, Electrical charges complete for finished item of work | Civil | Labour | SWR33564 | 589 | EA | 2356
65 | 1 | Providing independent EARTHING by excavating a trench to a depth of 2.1M in all solid,as per size specified in the Data,using 40mm dia 'B' class GI pipe of 2.5 Mtrs length with necessary accessories with hume pipe ring duly providing staggered holes including filling with equal proportion of salt and Charcoal in layers and all labour charges etc., compiete for small quarters. | Civil | Labour | SWR33596 | 5345 | EA | 5345
66 | 35 | Supplying, laying, jointing and testing 101.6 mm SWG SP-1 pipes of ISI make conforming to ISI 651 & 4127 with airtight cement joints in CM 1.5:1 prop. Including excavation of trenches and socket pits in any soil (except rock requiring blasting) up to 1524 mm(5'0") depth and refilling with watering and tamping. | Civil | Labour | SWR34281 | 755 | M | 26425
67 | 3 | Constructing 904.0 mm (3#0#) dia brick masonry inspection chamber as per IS - 4111: Part-1:1986 with cement mortar (1:6) prop using 2nd Class Clay Bricks of 225 mm thick from approved source having a minimum crushing strength of 5 N/sq.mm including plastering with cement mortar 1:3 prop; ½# thick both inside and outside fitted with 20# dia RCC manhole covers and frames including excavating pits up to a depth of 904 mm (3'-0") in all sorts of soils (excluding rock) and laying cement concrete (1:4:8) 150 mm thick using 40 mm HBG Metal and P.C.C. 1:2:4 benching and channel 100 mm thick as per Standard specification and including cost and conveyance of all materials like cement, sand, bricks, water etc., to site, cost of seigniorage charges on all materials and all incidental and operational, labour charges like mixing cement mortar, constructing masonry, lift charges, curing etc., complete for finished item of work as per Standard specification. | Civil | Labour | SWR34296 | 8766 | EA | 26298
68 | 4 | Supply & fixing of 110 mm dia - Door Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34381 | 128 | EA | 512
69 | 4 | Supply & fixing of 110 mm dia - Plain Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34380 | 100 | EA | 400
70 | 12 | Supply & fixing of 110 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand | Civil | Labour | SWR34377 | 462 | M | 5544
71 | 18 | Supply & fixing of 90 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand | Civil | Labour | SWR34378 | 410 | M | 7380
72 | 3 | Supplying & fixing 150 mm x 100 mm SWG gully traps conforming to ISI 651 & 4127 with C.I Grating & Cost. Brick masonry in CM 1:6 prop. Intermediate chamber and fitted with 304.8 mm x 288.6mm (12"x9") C.I Frame and hinged cover | Civil | Labour | SWR34286 | 767 | EA | 2301
73 | 1 | Supplying and Fixing of European Water Closet of 1st Quality | Civil | Labour | SWR34314 | 2228 | EA | 2228
74 | 6 | Supply & fixing 15 mm angle stop cock Indian make 400 grams Seiko/ Senior/ Nice/ Senior/ Nice or equivalent | Civil | Labour | SWR34328 | 721 | EA | 4326
75 | 4 | S&F 15 mm N.P bib tap Indian make 400 grams full turn Seiko/ Senior/ Nice or equivalent | Civil | Labour | SWR34329 | 296 | EA | 1184
76 | 1 | Supplying & Fixing Indian make Flat Back Wash Hand Basin (HSW/Parryware/ Neycer) 1st quality conforming to IS:2556-Part-4:1972 with waste fittings like rubber plug, chain, 32 mm nominal size C.P. Fitting with parallel pipe thread conforming to IS:2963-1979 and fitted with 15 mm nominal bore Chromium Plated Pillar Tap of 1st quality Indian make 400 grams Seiko/ Senior/ Nice/ Esso or equivalent complete with standard CI brackets including wooden block: 550 x 400 mm - Single C.P. Pillar cock | Civil | Labour | SWR34316 | 1717 | EA | 1717
77 | 2 | Supply & fixing 38.1 mm C.P waste coupling Half or Full Thread 1st Quality Indian make Parryware or equivalent | Civil | Labour | SWR34428 | 309 | EA | 618
78 | 2 | Supply & fixing of 4" (101.6 mm ) Nahany Trap ( Without Jali with inlet)UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34387 | 134 | EA | 268
79 | 1000 | Providing & Placing on Terrace (at all floor levels) polyethylene water storage tank with Double layer approved brand & manufacture with cover and suitable locking arrangement & making necessary holes for inlet & outlets and over flow pipes but with NECESSARY fittings & base support for tanks | Civil | Labour | SWR34375 | 10 | L | 10000
80 | 2 | Supply & fixing 31.75 mm dia PVC flexible waste pipe of 914.4 mm length of Ist quality | Civil | Labour | SWR34426 | 33 | EA | 66
81 | 45 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)- 15.90mm OD Pipe - SDR 11 | Civil | Labour | SWR34361 | 239 | M | 10755
82 | 40 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-22.20mm OD Pipe - SDR 11 | Civil | Labour | SWR34362 | 313 | M | 12520
83 | 65 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-28.60mm OD Pipe - SDR 11 | Civil | Labour | SWR34363 | 410 | M | 26650
84 | 4 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type - 25mm NB Size | Civil | Labour | SWR34346 | 466 | EA | 1864
85 | 4 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type -20mm NB Size | Civil | Labour | SWR34345 | 331 | EA | 1324
86 | 1 | Supply & fixing 25.4 mm dia & 609.6 mm long aluminium anodized towel rod with brackets and aluminium screws | Civil | Labour | SWR34430 | 489 | EA | 489
87 | 85.51 | Earth work excavation in all type of Ordinary soils red earth, Hard gravelly soils, earth mixed with sand and sandy soils etc., in all conditions such as slushy and dry with initial leads and lifts for foundations. Ordinary Soil | Civil | Labour | SWR33015 | 486 | cum | 41557.86
88 | 18.91 | PCC (1:4:8) using 40mm HBG metal for foundations and leveling course, including cost and conveyance of all materials, labour all leads and lifts, consolidation and all operations, formwork as required, curing, etc. complete for finished item w | Civil | Labour | SWR33028 | 4688 | cum | 88650.08
89 | 91.8 | Coursed Rubble stone masonry (CRS) 2nd sort with hard granite stones in cement mortar (1:6) for basement, including cost and conveyance of all materials, labour charges, curing, all leads and lifts, etc, complete for finished item of work. | Civil | Labour | SWR33041 | 4833 | cum | 443669.4
90 | 36 | PCC (1:3:6) using 40mm HBG metal for foundations and leveling course, including cost and conveyance of all materials, labour all leads and lifts, consolidation and all operations, formwork as required, curing, etc. complete for finished item w | Civil | Labour | SWR33029 | 4978 | cum | 179208
91 | 108 | Raised pointing to the exposed surfaces of CRS masonry in cm 1:3 prop. including cost and conveyance of all materials, labour charges, all leads and lifts curing etc, complete for finished item of work. | Civil | Labour | SWR33184 | 124 | sq.mm | 13392
92 | 787.5 | Supplying and filling the substation site with borrowed gravel, watering, ramming, thoroughly complying with the standard specification. | Civil | Labour | SWR33052 | 309 | cum | 243337.5
93 | 88.8 | Plastering with CM 2 coats, 20 mm thick, base coat in CM (1:6), 16 mm thick and top coat in CM (1:4), 4mm thick with Dubara sponze finishing including cost of all materials, seigniorage charges, excluding conveyance charges of materials and including all operational, incidental and labour charges for mixing mortar, laying rendering smooth and thread lining, curing, rounding off junctions of wall and slab etc., complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33163 | 560 | sq.mm | 49728
94 | 200.85 | Painting with two coats of Surya Cem paint over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33329 | 85 | sq.mm | 17072.25
95 | 120 | Supply&Fabrication and fixing of Welded wire mesh ( 2" x 2") of 3mm dia. with ISMC (75x40x4.4mm) and Pheriperal frame of ISA(35x35x3mm) incldg cost& conveyance painting with synthetic enamil paint two coats over a coat of red oxide primer etc complete for finished item of work.. | Civil | Labour | SWR33403 | 2310 | sq.mm | 277200
96 | 160 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-22.20mm OD Pipe - SDR 11 | Civil | Labour | SWR34362 | 313 | M | 50080
97 | 30 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type - 25mm NB Size | Civil | Labour | SWR34346 | 466 | EA | 13980
98 | 1 | Providing Consultancy services for arranging contour surveying with total station incuding preparation of boundary and contour levels with 2 Nos. Hard copies and soft copies complete for finished items of work | Civil | Labour | SWR33427 | 5665 | EA | 5665
99 | 425.08 | Seigniorage Charges - Sand | Civil | Labour | SWR34470 | 40 | cum | 17003.2
100 | 1434.28 | Seigniorage Charges - Metal | Civil | Labour | SWR34471 | 97.5 | cum | 139842.3
101 | 839.38 | Seigniorage Charges - Gravel | Civil | Labour | SWR34472 | 30 | cum | 25181.4
102 | 60 | Supply and fixing of RCC fencing poles of size 0.1mx0.1mx1.8m (security fencing of sub station), including cost and conveyance of all labour, materials,and hire chareges etc complete for finished item of work. | Civil | Labour | SWR33405 | 1444 | EA | 86640
103 | 1200 | Supply and fixing of galvanised barded wire (1 horizantal & 2 cross strands. including cost and conveyance of all labour, materials,and hire chareges etc complete for finished item of work. | Civil | Labour | SWR33408 | 16 | M | 19200
Civil Labour | [7 empty] | 6355418.67
Electrical and Civil labour | [7 empty] | 32890973.6841
|  |  |  | Grand Total Rs. |  |  |  | 39246392.3541
[5 empty] | total Electrical+ civil schedule amount without GST |  |  | 32890973.6841
[5 empty] | with GST |  |  | #REF!

## 18. Hafeezpet
Schedule for the work of "Erection of new 33/11kV Outdoor substation with 2x8MVA PTRs and also Construction of Control room, and other Civil works at Hafeezpet RTO Office in Kondapur section of operation Kondapur division in cybercity circle, in Master plan Sub-division 1 of WCGH Division in Rangareddy circle under T&D improvement works"
1. D.No :S n No: 129/ D No. 1349, Dt:09-11-2024
2. WBS No. S-1799-13-04-01-01-001
Sl.No | Estimate Quantity(Only Figures) | PARTICULARS | Work Type | Item Short Description | SWR No/APSS/Morth cl.No | Rate (INR) (Upto 2 Decimals) | UOM | Amount
1 | 8 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") Exca Hard pit w/o blast 0.76X0.76X1.83M | Elecy | labour | SWR11039 | 928 | EA | 7424
2 | 8 | Excavation of pits in hard rock requiring blasting. (other than SS) 9.1Mtrs PSCC Pole 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") EXCAV. OF PIT HARD(2.6" x 2.6" x 6.0") | Elecy | labour | SWR10112 | 1770 | EA | 14160
3 | 5.76 | Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. Fabrication of struc.with power drilling | Elecy | labour | SWR10868 | 6852 | TO | 39467.52
4 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | Elecy | supply | SMR40009 | 2181 | TO | 12562.56
5 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | Elecy | labour | SWR10877 | 851 | TO | 4901.76
6 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | Elecy | supply | SMR40010 | 1293 | TO | 7447.68
7 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | Elecy | labour | SWR10879 | 482 | TO | 2776.32
8 | 5.76 | Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | Elecy | labour | SWR10867 | 1470 | TO | 8467.2
9 | 16 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. Erection of RS Joist 150 x 150 mm | Elecy | labour | SWR10348 | 1952.61 | EA | 31241.76
10 | 17.758 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | Elecy | labour | SWR10356 | 6579 | M3 | 116829.882
11 | 9.24 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | Elecy | labour | SWR10862 | 373 | M2 | 3446.52
12 | 16 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | Elecy | labour | SWR11089 | 48 | EA | 768
13 | 5.063 | Fabrication & erection of Channels Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. Fabrication of struc.with power drilling | Elecy | labour | SWR10868 | 6852 | TO | 34691.676
14 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | Elecy | supply | SMR40009 | 2181 | TO | 11042.403
15 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium. Labour for 1st coat Al. Painting. | Elecy | labour | SWR10877 | 851 | TO | 4308.613
16 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | Elecy | supply | SMR40010 | 1293 | TO | 6546.459
17 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | Elecy | labour | SWR10879 | 482 | TO | 2440.366
18 | 5.063 | Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | Elecy | labour | SWR10867 | 1470 | TO | 7442.61
19 | 13 | Erection of AB Switch and aligment complete Erection of 33 KV AB Switch including alignment and earthing | Elecy | labour | SWR10392 | 4500 | EA | 58500
20 | 38 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Note:-The requirement of 2nd coat is to be justified by the concerned Divisional Engineer /Executive Engineer before execution of this work Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elecy | labour | SWR10881 | 142 | EA | 5396
21 | 38 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch AB Switch Coil Earthing GI No. 8 Wire | Elecy | labour | SWR12331 | 146.63 | EA | 5571.94
22 | 6 | Loading of 33 KV CTs/ PTs | Elecy | labour | SWR10200 | 165 | EA | 990
23 | 6 | Un loading of 33 KV CTs/ PTs | Elecy | labour | SWR10518 | 128 | EA | 768
24 | 2 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33kv single phase PT s | Elecy | labour | SWR10401 | 1079 | SET | 2158
25 | 12 | Loading of 33 KV, 10 KA LAs Station type | Elecy | labour | SWR10266 | 41 | EA | 492
26 | 12 | Un loading of 33 KV, 10 KA LAs Station type | Elecy | labour | SWR10584 | 35 | EA | 420
27 | 4 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33 KV LAS station/Line type including earthing | Elecy | labour | SWR10396 | 880 | SET | 3520
28 | 2 | Loading of 33 KV VCBs along with Panel boards | Elecy | labour | SWR10198 | 1024 | EA | 2048
29 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Above 10 Km and upto 20 Km with Lorry for each trip Transport of Cond Drum,VCBs >10 & <20Km | Elecy | labour | SWR11861 | 3299.7 | EA | 3299.7
30 | 2 | Un loading of 33 KV VCBs along with Panel boards | Elecy | labour | SWR10516 | 1044.48 | EA | 2088.96
31 | 12.58 | Excavate-Pit for 33KV VCB | Elecy | labour | SWR23224 | 331 | M3 | 4163.98
32 | 14.52 | Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x 1.8 x 0.75 cum for VCB Plinth | Elecy | labour | SWR20685 | 5160 | M3 | 74923.2
33 | 2 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33 KV VCB with Control Panel | Elecy | labour | SWR10460 | 12500 | EA | 25000
34 | 2 | Loading and unloading of PTR on constructed plinth LOADING of 8 MVA PTR | Elecy | labour | SWR10613 | 5805.84 | EA | 11611.68
35 | 2 | Transport of Power transformers (0 to 100 KM) from one place to another place in GHMC Area.(excluding of loading & unloading ) Transport of 8 MVA power transformer | Elecy | labour | SWR10854 | 21945 | EA | 43890
36 | 2 | UNLOADING of 8 MVA PTR | Elecy | labour | SWR10627 | 5805.84 | EA | 11611.68
37 | 700 | S/o rail poles 90/105lb (250x2N) | Elecy | supply | SMR22718 | 47.27 | KG | 33089
38 | 4 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Erection of Rail Pole 90Lbs | Elecy | labour | SWR10344 | 3510 | EA | 14040
39 | 2 | Erection of PTR on constructed plinth Erection of 8 MVA PTR. | Elecy | labour | SWR21321 | 49480.2 | EA | 98960.4
40 | 0.44 | Extention of 33KV Bay at 132/33KV Sub-station 33KV Bay Extn: S-Zebra Conductor | Elecy | supply | SMR24910 | 299369 | KM | 131722.36
41 | 30 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing. | Elecy | supply | SMR11915 | 2055 | SET | 61650
42 | 30 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of I-Bolts | Elecy | supply | SMR22473 | 294 | EA | 8820
43 | 45 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 "to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating . Sup T clamp LM6 Al alloy of 12 mm, 800 A | Elecy | supply | SMR40011 | 299 | EA | 13455
44 | 6 | Bus stringing Hoisting of Insulators and hardware, stretching the conductor and stringing of 33 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bussection of 4.5mt) Hoisting post ins&hrd wr 1panther 33kv | Elecy | labour | SWR21240 | 781 | EA | 4686
45 | 218.67 | Stringing of bus with panther conductor including jumpering etc., complete to all the equipment in SS fixing to all clamps and equipment.(3 Conductors) Stringing of bus with panther conductor | Elecy | labour | SWR10404 | 327.68 | M | 71653.7856
46 | 30 | Bus stringing Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | Elecy | labour | SWR10884 | 224 | EA | 6720
47 | 75 | Labour for Fixing of all types of clamps | Elecy | labour | SWR10917 | 65 | EA | 4875
48 | 29 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Elecy | labour | SWR11039 | 928 | EA | 26912
49 | 10.12 | Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. Fabrication of struc.with power drilling | Elecy | labour | SWR10868 | 6852 | TO | 69342.24
50 | 10.12 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | Elecy | supply | SMR40009 | 2181 | TO | 22071.72
51 | 10.12 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | Elecy | labour | SWR10877 | 851 | TO | 8612.12
52 | 10.12 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | Elecy | supply | SMR40010 | 1293 | TO | 13085.16
53 | 10.12 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | Elecy | labour | SWR10879 | 482 | TO | 4877.84
54 | 10.12 | Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | Elecy | labour | SWR10867 | 1470 | TO | 14876.4
55 | 29 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Erection of RS Joist 150 x 150 mm | Elecy | labour | SWR10348 | 1952.61 | EA | 56625.69
56 | 32.19 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Mass concreting of supports incl. cement | Elecy | labour | SWR10356 | 6579 | M3 | 211778.01
57 | 16.75 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | Elecy | labour | SWR10862 | 373 | M2 | 6247.75
58 | 29 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. Ptg of coping with 2cts white cmnt inclu | Elecy | labour | SWR11089 | 48 | EA | 1392
59 | 5.588 | Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. Fabrication of struc.with power drilling | Elecy | labour | SWR10868 | 6852 | TO | 38288.976
60 | 5.588 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | Elecy | Supply | SMR40009 | 2181 | TO | 12187.428
61 | 5.588 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | Elecy | labour | SWR10877 | 851 | TO | 4755.388
62 | 5.588 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | Elecy | Supply | SMR40010 | 1293 | TO | 7225.284
63 | 5.588 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | Elecy | labour | SWR10879 | 482 | TO | 2693.416
64 | 5.588 | Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | Elecy | labour | SWR10867 | 1470 | TO | 8214.36
65 | 21 | Erection of 11KV 800A double throw AB Switches | Elecy | labour | SWR21277 | 3500 | EA | 73500
66 | 3 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Elecy | labour | SWR10393 | 3200 | EA | 9600
67 | 2 | Loading of 11 KV CT - PT Sets | Elecy | labour | SWR10201 | 190 | EA | 380
68 | 2 | Un loading of 11 KV CT - PT Sets | Elecy | labour | SWR10519 | 101 | EA | 202
69 | 2 | Erection of 11 KV three phase PTs | Elecy | labour | SWR10402 | 800 | SET | 1600
70 | 30 | Loading of 11 KV, 10 KA LAs Station type | Elecy | labour | SWR10264 | 32 | EA | 960
71 | 30 | Un Loading of 11 KV, 10 KA LAs Station type | Elecy | labour | SWR10582 | 32 | EA | 960
72 | 2 | Erection of 11 KV LAS station type including earthing | Elecy | labour | SWR10397 | 559 | SET | 1118
73 | 8 | Erection of 11 KV LAS line type including earthing | Elecy | labour | SWR10398 | 505 | SET | 4040
74 | 10 | Loading of 11 KV VCBs along with Panel boards | Elecy | labour | SWR10199 | 1024 | EA | 10240
75 | 5 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Transport of Cond Drum,VCBs >10 & <20Km | Elecy | labour | SWR11861 | 3299.7 | EA | 16498.5
76 | 10 | Un Loading of 11 KV VCBs along with Panel boards | Elecy | labour | SWR10517 | 1044.48 | EA | 10444.8
77 | 52 | Excavate-Pit for 33KV VCB | Elecy | labour | SWR23224 | 331 | M3 | 17212
78 | 60 | Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x 1.8 x 0.75 cum for VCB Plinth | Elecy | labour | SWR20685 | 5160 | M3 | 309600
79 | 10 | Erection of 11 KV VCB with Control Panel | Elecy | labour | SWR10461 | 12000 | EA | 120000
80 | 12 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing. | Elecy | Supply | SMR11915 | 2055 | SET | 24660
81 | 12 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367- 1961) Supply of I-Bolts | Elecy | Supply | SMR22473 | 294 | EA | 3528
82 | 45 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367- 1961) Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 " to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating . Sup T clamp LM6 Al alloy of 12 mm, 800 A | Elecy | Supply | SMR40011 | 299 | EA | 13455
83 | 2 | Bus Stringing Hoisting of Insulators and hardware, stretching the conductor and stringing of 11 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 3.5mt) Hoisting post ins&hrd wr 1panther 11kv | Elecy | labour | SWR21241 | 507 | EA | 1014
84 | 45 | Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | Elecy | labour | SWR10884 | 224 | EA | 10080
85 | 57 | Labour for Fixing of all types of clamps | Elecy | labour | SWR10917 | 65 | EA | 3705
86 | 696 | Laying of earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication 75x 8mm MS Flat / GI Flat. Laying of earth mat,excavation 75x 8mm | Elecy | labour | SWR10920 | 65 | RMT | 45240
87 | 1247 | Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) Earthing for raisers of SS Flat 50x6 mm. | Elecy | labour | SWR10919 | 41 | RMT | 51127
88 | 36 | Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Elecy | Supply | SMR11482 | 3486 | EA | 125496
89 | 36 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elecy | labour | SWR10357 | 1234.2 | EA | 44431.2
90 | 36 | Providing of RCC collar to earth pit Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINES-Providing of RCC collar | Elecy | labour | SWR10359 | 386 | EA | 13896
91 | 2 | Supply of Copper Flexible jumper with 75 X 8 of length 250 mm at neutral of Power tranformer end and 50 X 6 of length 50mm two Nos at double neutral end duly brasing with flexible jumper of capacity of 5kA/3 sec for power transformer neutral. SupCU Flexi jumper for Power T/F Neutral | Elecy | Supply | SMR40033 | 4725 | EA | 9450
92 | 2 | Providing of double earthing for neutral with flexible copper jumpers including arrangement by fixing M.S.Channel 100x50mm. | Elecy | labour | SWR11892 | 1323 | EA | 2646
93 | 4 | Loading of LT AB Cable 3X16+25 Sqmm | Elecy | labour | SWR11702 | 200 | DR | 800
94 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Transport of Cond Drum,VCBs>10 & <20Km | Elecy | labour | SWR11861 | 3299.7 | EA | 3299.7
95 | 4 | Un loading of LT AB Cable 3X16+25 Sqmm Drum | Elecy | labour | SWR11713 | 204 | DR | 816
96 | 90 | Providing of cable trench as per DATA-XII | Elecy | labour | SWR22093 | 3148 | RMT | 283320
97 | 3312 | Control Cable Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends . Lay-4C/10C 2.5Sqmm Control Cable | Elecy | labour | SWR11879 | 27 | M | 89424
98 | 270 | Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per specification (including cost of ferrules, lugs and glands) L-Cable Termination to Switchgear | Elecy | labour | SWR12510 | 27 | EA | 7290
99 | 4 | Supply of FRP PT Marshalling Box | Elecy | Supply | SMR40048 | 4463 | EA | 17852
100 | 4 | Erection of Marshalling boxes | Elecy | labour | SWR10940 | 374.85 | EA | 1499.4
101 | 1 | Loading of 220 V Batterry with charger | Elecy | labour | SWR11166 | 1612 | SET | 1612
102 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Transport of Cond Drum,VCBs>10 & <20Km | Elecy | labour | SWR11861 | 3299.7 | EA | 3299.7
103 | 1 | Un loading of 220 V Batterry with charger | Elecy | labour | SWR11147 | 1024 | SET | 1024
104 | 1 | Erection of 220 V, 80 AH battery in complete shape fit for charging . Conventional lead acid | Elecy | labour | SWR12295 | 7666 | EA | 7666
105 | 1 | Control Panels Supply of DC Annunciation & relay panel for 10 feeder panel including the cost of LED Indiacation lamps, VAA auxilairy relays, Electronic Hooters complete as per specification. Supply of DC Anunc.relay panel 8 feeders | Elecy | Supply | SMR40044 | 42500 | EA | 42500
106 | 1 | Supply of AC Supply panel inluding providing of changeover switch, SFU, metering unit, 32 A three phase MCB, 16 A Single phase MCB complete as per specification. Supply of AC Supply panel complete | Elecy | Supply | SMR40045 | 42000 | EA | 42000
107 | 8 | Supply of stepped tubular poles single way made of steel of length 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9 mm, 2.1 mtrs with outer dia 76.1 mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79 kgf as per IS 2713. Supply 9mtrs tubular poles single way | Elecy | Supply | SMR40051 | 13913 | EA | 111304
108 | 8 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE/CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA /OSRAM /SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty S-90W LED fixture set | Elecy | Supply | SMR11594 | 8200 | EA | 65600
109 | 8 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") Exca Hard pit w/o blast 0.76X0.76X1.83M | Elecy | labour | SWR11039 | 928 | EA | 7424
110 | 8 | Errection of tubular poles | Elecy | labour | SWR10955 | 1379 | EA | 11032
111 | 5.27 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Mass concreting of supports incl. cement | Elecy | labour | SWR10356 | 6579 | M3 | 34671.33
112 | 8 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE/CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA /OSRAM /SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty. Fixing of Metal halide lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5 GI pipe complete Fixing of LED/Metal halide complete. | Elecy | labour | SWR10956 | 1268 | EA | 10144
113 | 45 | Supply & spreading of 20mm machine crushed metal (HBG) including cost of conveneyance of all materials, labour charges etc complete for finished item of work and directed by the engineer incharge Supply & Spreading of 20mm HBG metal | Elecy | labour | SWR10860 | 2113 | M3 | 95085
114 | 2 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M Ex of Hard pit w/o blast 0.75X0.9X1.95M | Elecy | labour | SWR11040 | 990.68 | EA | 1981.36
115 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete . Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | Elecy | Supply | SMR40009 | 2181 | TO | 1635.75
116 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | Elecy | labour | SWR10877 | 851 | TO | 638.25
117 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. (*)Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | Elecy | Supply | SMR40010 | 1293 | TO | 969.75
118 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. (*) Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium Labour for 2nd coat Al. Painting. | Elecy | labour | SWR10879 | 482 | TO | 361.5
119 | 1 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Erect-12Meter Box pole | Elecy | labour | SWR11267 | 3901.37 | EA | 3901.37
120 | 2.22 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc Mass concreting of supports incl. cement | Elecy | labour | SWR10356 | 6579 | M3 | 14605.38
121 | 1.16 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | Elecy | labour | SWR10862 | 373 | M2 | 432.68
122 | 2 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. Ptg of coping with 2cts white cmnt inclu | Elecy | labour | SWR11089 | 48 | EA | 96
123 | 1 | Construction of DTR Plinth RCC Column type DTR Plinth of size 1'X1'X10',topslab 4'x4'x6" & beam size 4'X8'X8" upto 160KVA Column type DTR Plinth topslab 4'x4'x6" | Elecy | labour | SWR21843 | 25967.57 | EA | 25967.57
124 | 1 | LOADING of 50,63,75&100kva DTR | Elecy | labour | SWR10195 | 350 | EA | 350
125 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Transport of Cond Drum,VCBs>10 & <20Km | Elecy | labour | SWR11861 | 3299.7 | EA | 3299.7
126 | 1 | UNLOADING of 50,63,75&100kva DTR | Elecy | labour | SWR10513 | 280 | EA | 280
127 | 1 | Erection of DTR's including loading and Unloading DTR on the Structure/Plinth etc Erection of 3 Phase DTRs 63,75 & 100 KVA E/r 3ph DTR inclu L&Un-L,T&C on plinth | Elecy | labour | SWR20905 | 1650 | EA | 1650
128 | 1 | Erection of AB Switch and aligment complete Erection of 11KV 200A TT type AB Switch including fixing of cross angles and alignment complete | Elecy | labour | SWR20102 | 1813.49 | EA | 1813.49
129 | 1 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erect. of 11kv HG Fuseset incl earthing | Elecy | labour | SWR10395 | 740.52 | SET | 740.52
130 | 40 | Excavation & laying of UG Cable in Single Run Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders /Normal soil / CC/BT Road Lay-SR 11KV 3x185sqmm UG Cb HG/BC/CC/BT | Elecy | labour | SWR11920 | 465.46 | M | 18618.4
131 | 20 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) Raise-SR 11KV 3x185sqmm UG Cb on support | Elecy | labour | SWR11956 | 126.23 | M | 2524.6
132 | 2 | UG Cables Joints Making of Outdoor/Indoor End Termination OD/Idoor end termination 11kv 3x185 xlpe | Elecy | labour | SWR10390 | 2370.63 | EA | 4741.26
133 | 1 | Erection of LT distribution box including laying of LT cable from distribution box to LT OH line and DTR to distribution box including earthing of distribution box and crimping of lugs connecting of jumpers etc Erection of LT distribution box | Elecy | labour | SWR10674 | 1594.67 | EA | 1594.67
134 | 85 | Excavation & laying of UG Cable in Single Run Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road Lay-SR LT 3.5x95sqmm UG Cb HG/BC/CC/BT | Elecy | labour | SWR11925 | 377.63 | M | 32098.55
135 | 15 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) Raise-SR LT 3.5x95sqmm UG CB ON SUPPORT | Elecy | labour | SWR11961 | 85.43 | M | 1281.45
136 | 2 | UG Cables Joints Making of Outdoor/Indoor End Termination Sup of 31/2x185Sqmm UG O/D end term kits | Elecy | supply | SMR40140 | 550 | EA | 1100
137 | 2 | UG Cables Joints Making of Outdoor/Indoor End Termination Fixing of Out Door/Indoor end termination LT 3 1/2 x185 Sqmm Cable OD/Idoor end termination LT 3 1/2 x 185 | Elecy | labour | SWR10765 | 968.9 | EA | 1937.8
138 | 1 | Fixing of Substation board of size 3'x2.5' indicating the layout of switchyard Sup &fix of board ind Switchyard layout | Elecy | labour | SWR20032 | 1654 | EA | 1654
139 | 1 | Supply and fixing of safety instructions/Substation operation instruction board. Sup& fix safety inst/SS Op. inst board | Elecy | labour | SWR22090 | 2205 | EA | 2205
140 | 750 | Control Panels Supplying & fabrication erection of 6mm Checkerd plates as per the field conditions Supply,fabricati of 6mm Checkerd plates | Elecy | labour | SWR10873 | 83 | KG | 62250
141 | 1 | T & P Supply of Wall clock standard make | Elecy | Supply | SMR40059 | 578 | EA | 578
142 | 1 | S-10ft Aluminium Ladder | Elecy | supply | SMR12378 | 1654 | EA | 1654
143 | 1 | Sup Alluminium Ladder for indoor works | Elecy | Supply | SMR40062 | 4410 | EA | 4410
144 | 30 | T & P Painting of Name Plates for any equipmen | Elecy | labour | SWR10963 | 122 | EA | 3660
145 | 1 | T & P Supply of Taparia Tool kit of Size 20”x10”x15” with tier arrangements Tool box with locking arrangement & key containing (1) Double Ended fix Spanner sets, (Ribbed) 6 x 7, 8 x 9, 10 x 11, 12 x 13, 14 x 15, 16 x 17, 18 x19, 20 x 22, 21 x23, 24 x 27, 25 x28, 30 x 32, (2) Double Ended Ring Spanners sets, 6 x 7 , 8 x 9, 10 x 11, 12 x 13, 14 x 15. 16 x 17 , 18 x 19, 20 x 22 , 21 x 23, 24 x 27, 25 x28, 30 x 32 mm, (3) Adjustable Spanner 305 mm length least maximum opening 35mm chrome, (4) Pipe Wrench Length 350 mm 14”, (5) Soft faced Hammer with suitable handle 2 lb, (6) Hacksaw frame with metal handle heavy duty for 12" hacksaw blade with High Speed blade, (7) Insulated Screw drivers Transparent Green Handle Set Length 6”, 8” & 12”, (8) Star Screw Driver Transparent Green Handle Length 6”, (9) Insulated Wire Cutter, (10) Insulated Cutting Plier Length 8” with cable stripper insulated with thick C. A. sleeve confirming to IS: 4378 - 1990, (11) Long Nose Plier insulated with thick C.A. sleeve generally confirming to IS:3552-1989, (12) Tester type screw driver (special with neon bulb) generally confirm to IS: 5579- 1985 Grade:II handle yellow/ green colour overall length 130 mm, (13) Insulated Crimping Plier of all Taparia make. SupTaparia Tool kit complete as per Spec | Elecy | supply | SMR40063 | 4925 | SET | 4925
146 | 1 | T & P Sup Rechargeable LED torch light of Standard make | Elecy | supply | SMR40064 | 1733 | EA | 1733
147 | 1 | T & P Sup Steel almarah(61/2 X 3ft) Godrej | Elecy | supply | SMR40061 | 9818 | EA | 9818
148 | 1 | T & P Supply of Table (3x6ft) Godrej | Elecy | supply | SMR40057 | 6050 | EA | 6050
149 | 4 | T & P Supply of S type chairs (Godrej) | Elecy | supply | SMR40058 | 924 | EA | 3696
150 | 1 | T & P Sup Angle racks(18x36.6inches) Godrej | Elecy | supply | SMR40060 | 1733 | EA | 1733
151 | 1 | T & P Supply of Hack saw (12 inches) | Elecy | supply | SMR40065 | 289 | EA | 289
152 | 4 | Sup Earth Rods (8ft) Screw & clamp type | Elecy | supply | SMR40066 | 578 | EA | 2312
153 | 2 | Supply of Hand Gloves | Elecy | supply | SMR40067 | 289 | SET | 578
154 | 12 | SupRubber mats( 6'x3')size fo indoorSS | Elecy | supply | SMR40068 | 1386 | EA | 16632
155 | 1 | Biometric Time attendence System & Telecom Sup Stand basic cell phone with charger | Elecy | supply | SMR40069 | 1386 | EA | 1386
156 | 14 | Supply of Danger boards with clamps | Elecy | supply | SMR40070 | 116 | EA | 1624
157 | 2 | Supply of Materials Fire bucket stand with 3 buckets (8 -10 ltr capacity) Sup Fire Buckets Stand with Buckets | Elecy | supply | SMR40088 | 1386 | SET | 2772
158 | 2 | Room fire extinguisher (2 ltrs capacity) for control room Sup Fire Extinguisher for Control Room | Elecy | supply | SMR40089 | 4620 | EA | 9240
159 | 4 | Sup TrollyMounted Co2 (6.5Kgs) Cylinders(IS-2878) | Elecy | supply | SMR40087 | 9240 | EA | 36960
160 | 6 | Supply of Safety Helmet of standard make | Elecy | supply | SMR40071 | 231 | EA | 1386
161 | 8 | Supply of LC Boards | Elecy | supply | SMR40072 | 116 | EA | 928
162 | 4 | Supply of Gum Boots(pair) | Elecy | supply | SMR40073 | 693 | EA | 2772
163 | 1 | Supply of 5000v megger | Elecy | supply | SMR40074 | 13860 | EA | 13860
164 | 1 | Supply of Earth megger (1000v) | Elecy | supply | SMR40075 | 8085 | EA | 8085
165 | 1 | Supply of Digital clamp meter. | Elecy | supply | SMR40076 | 2888 | EA | 2888
166 | 1 | Name board of the 33/11kV Sub-Station(As per Standard Specification) Sup 33/11kv S.S Permanent name board | Elecy | supply | SMR40086 | 10238 | EA | 10238
167 | 800 | Supply of Hot dip galvanized/zinc coated bolts & nuts including spring washers, pack washers and flat washers etc. S-Hot dip gal./Zinc bolts & nuts washer | Elecy | supply | SMR12488 | 90 | KG | 72000
168 | 4 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rockboulders) 8.0Mtrs PSCC Poles 0.76 M x 0.76M x 1.52M (2.6" x 2.6" x 5.0') 0.88 cum Ex of Hard pit w/o blast 0.76X0.76X1.52M | Elecy | labour | SWR11037 | 793 | EA | 3172
169 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | Elecy | supply | SMR40009 | 2181 | TO | 2181
170 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., completeLabour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | Elecy | labour | SWR10877 | 851 | TO | 851
171 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete (*)Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | Elecy | supply | SMR40010 | 1293 | TO | 1293
172 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete (*) Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | Elecy | labour | SWR10879 | 482 | TO | 482
173 | 3.51 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Mass concreting of supports incl. cement | Elecy | labour | SWR10356 | 6579 | M3 | 23092.29
174 | 2.31 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | Elecy | labour | SWR10862 | 373 | M2 | 861.63
175 | 4 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. Ptg of coping with 2cts white cmnt inclu | Elecy | labour | SWR11089 | 48 | EA | 192
176 | 5 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Erection of RS Joists 150x75/175 x 85 mm | Elecy | labour | SWR10346 | 1934 | EA | 9670
177 | 2 | Fixing of AC/DC Panel and giving Connections to the protection equipment and Metering circuits as per the specification and standards. The 3 1/2 core 25 Sqmm power cable required from distribution box to AC/DC panel in the control room is also to be supply | Elecy | labour | SWR20025 | 7871.85 | SET | 15743.7
178 | 2 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Elecy | labour | SWR10642 | 512.55 | EA | 1025.1
179 | 5760 | Supply RS Joist Grider Pole (150x150mm) | Elecy | Supply | SMR12302 | 59.25 | KG | 341280
180 | 5063 | Supply MS Channel 100x50mm | Elecy | Supply | SMR22745 | 57.45 | KGS | 290869.35
181 | 13 | Supply 33KV 800A DB Break AB Switch | Elecy | Supply | SMR12315 | 40658.78 | EA | 528564.14
182 | 10120 | Supply RS Joist Grider Pole (150x150mm) | Elecy | Supply | SMR12302 | 59.25 | KG | 599610
183 | 5588 | Supply MS Channel 100x50mm | Elecy | Supply | SMR22745 | 57.45 | KGS | 321030.6
184 | 21 | Supply 11KV 800A DB Break AB Switch | Elecy | Supply | SMR12316 | 30847.46 | EA | 647796.66
185 | 3 | Supply 11KV 400A DB Break AB Switch | Elecy | Supply | SMR12317 | 18150 | EA | 54450
186 | 3275 | Supply MS Flat 75x8mm | Elecy | Supply | SMR12321 | 56.42 | KG | 184775.5
187 | 2995 | Supply MS Flat 50x6mm | Elecy | Supply | SMR12322 | 56.5 | KG | 169217.5
188 | 750 | Supply RS Joist Pole (175x85mm) | Elecy | Supply | SMR12303 | 60.75 | KG | 45562.5
189 | 1 | Supply 11KV 200A Tilting Type AB Switch | Elecy | Supply | SMR12318 | 8991 | EA | 8991
190 | 1 | Supply 11KV HG FuseSet for StationTransformer | Elecy | Supply | SMR12324 | 1974 | EA | 1974
191 | 1 | Supply LT Distribution Box (SMC) | Elecy | Supply | SMR25200 | 7797 | EA | 7797
192 | 2 | Supply 11KV 3x185 Heat Shble O/d End Term Kit | Elecy | Supply | SMR25201 | 1182.97 | EA | 2365.94
193 | 40 | Supply LT 1Core 120Ssqmm XLPE Al. Cable | Elecy | Supply | SMR25030 | 3118.66 | M | 124746.4
194 | 1000 | Supply RS Joist Pole (175x85mm) | Elecy | Supply | SMR12303 | 60.75 | KG | 60750
195 | 100 | Supply LT XLPE Cable 3 1/2 C 185 sqmm | Elecy | Supply | SMR25204 | 547 | M | 54700
196 | 6.29 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) (other than SS) Earth work excav hard rock bould <3cum | Elecy | labour | SWR10856 | 1318.35 | M3 | 8292.4215
197 | 7.26 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Mass concreting of supports incl. cement | Elecy | labour | SWR10356 | 6579 | M3 | 47763.54
198 | 1.8 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | Elecy | supply | SMR40009 | 2181 | TO | 3925.8
199 | 1.8 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. (*)Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | Elecy | supply | SMR40010 | 1293 | TO | 2327.4
200 | 1.8 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | Elecy | labour | SWR10877 | 851 | TO | 1531.8
201 | 1.8 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. (*) Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium Labour for 2nd coat Al. Painting. | Elecy | labour | SWR10879 | 482 | TO | 867.6
202 | 2 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Erection of RS Joist 150 x 150 mm | Elecy | labour | SWR10348 | 1952.61 | EA | 3905.22
203 | 895 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends . Lay-4C/10C 2.5Sqmm Control Cable | Elecy | labour | SWR11879 | 27 | M | 24165
204 | 2 | Sup MS Powder coated CT Marshalling Box | Elecy | supply | SMR40047 | 3675 | EA | 7350
205 | 2 | Erection of Marshalling boxes | Elecy | labour | SWR10940 | 374.85 | EA | 749.7
206 | 12 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing. S-Tension HW 3Bolt 1Zebra/Pnthr 150mm | Elecy | supply | SMR11915 | 2055 | SET | 24660
207 | 32 | Laying of earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication 75x 8mm MS Flat / GI Flat. Laying of earth mat,excavation 75x 8mm | Elecy | labour | SWR10920 | 65 | RMT | 2080
208 | 5 | Supply of earthing pipe with materials Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specification S-CI Pipe earthing 100mm dia 2.75m long | Elecy | supply | SMR11482 | 3486 | EA | 17430
209 | 5 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4Mts.) duly filling with bentonite, earth , running of earth wireetc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height ERECT. OF LINES-Providing of earthing | Elecy | labour | SWR10357 | 1234.2 | EA | 6171
210 | 5 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X0.50 M height ERECT. OF LINES-Providing of RCC collar | Elecy | labour | SWR10359 | 386 | EA | 1930
211 | 6 | Bus Stringing Hoisting of Insulators and hardware, stretching the conductorand stringing of 33 kV bus comprising of three phases withSingle Zebra/panther conductor to a tension of 450kgs.(Bussection of 4.5mt) Hoisting post ins&hrd wr 1panther 33kv | Elecy | labour | SWR21240 | 781 | EA | 4686
212 | 200 | Cable terminations to the switch gear marshalling boxes/panelterminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per specification (including cost of ferrules, lugs and glands) Lay-Cable Terminations to Switchgear | Elecy | labour | SWR11880 | 34.43 | EA | 6886
213 | 1 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33 KV LAS station/Line type including earthing Erect of 33kv LA stn type incl earthing | Elecy | labour | SWR10396 | 880 | SET | 880
214 | 1 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33kv VCB with Control Panel | Elecy | labour | SWR10460 | 12500 | EA | 12500
215 | 7.5 | Supply of HBG metal Supply & spreading of 20mm machine crushed metal (HBG)including cost of conveneyance of all materials, labour charges etc complete for finished item of work and directed by the engineer incharge Supply & Spreading of 20mm HBG metal | Elecy | labour | SWR10860 | 2113 | M3 | 15847.5
216 | 2 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Painting of operating rods of 33kV, 11kV AB switches withpost office red colour (including cost of paint) Painting AB switch OP rods with PO red | Elecy | labour | SWR10881 | 142 | EA | 284
217 | 1 | LOADING of 33 KV VCBs&Panel boards | Elecy | labour | SWR10198 | 1024 | EA | 1024
218 | 1 | UNLOADING of 33 KV VCBs&Panel boards | Elecy | labour | SWR10516 | 1044.48 | EA | 1044.48
219 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excludingof loading unloading) Transport of Cond Drum,VCBs upto 10Km | Elecy | labour | SWR11860 | 2720.34 | EA | 2720.34
220 | 2 | Erection of 33kv ABSwitch including alignment and earthing | Elecy | labour | SWR10392 | 4500 | EA | 9000
221 | 2 | Excavation of pits in all soils except hard rock requiring blasting 12Mtrs/Spun Pole 0.92 M x 0.92M x 2.3M (3.0" x 3.0" x 7.6") 1.94 cum EXCAVATION OF PIT(3.0" x 3.0" x 7.6") | Elecy | labour | SWR10109 | 842.78 | EA | 1685.56
222 | 48 | Labour for Fixing of all types of clamps | Elecy | labour | SWR10917 | 65 | EA | 3120
223 | 20 | Stringing of bus with panther conductor including jumpering etc., complete to all the equipment in SS fixing to all clamps and equipment.(3 Conductors) Stringing of bus with panther conductor | Elecy | labour | SWR10404 | 327.68 | M | 6553.6
224 | 45 | Fabrication of materials including 2 coats of Red oxide painting Fab Back clamps with 50 x 6 mm MS Flat | Elecy | labour | SWR10320 | 15 | EA | 675
225 | 2.114 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metalincluding the cost of metal, sand, Cement and curing etc. Mass concreting of supports incl. cement | Elecy | labour | SWR10356 | 6579 | M3 | 13908.006
226 | 1.8 | Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S. Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to theRS-Joist poles excluding cost of Mild Steel and transportcharges to substation site, including erection. Fabrication of struc.with welding. | Elecy | labour | SWR10869 | 3426 | TO | 6166.8
227 | 1000 | Supply RS Joist Grider Pole (150x150mm) | Elecy | Supply | SMR12302 | 59.25 | KG | 59250
228 | 150 | Supply MS Flat 75x8mm | Elecy | Supply | SMR12321 | 56.42 | KG | 8463
229 | 90 | Supply MS Flat 50x6mm | Elecy | Supply | SMR12322 | 56.5 | KG | 5085
230 | 800 | Supply MS Channel 100x50mm | Elecy | Supply | SMR22745 | 57.45 | KGS | 45960
231 | 2 | Supply 33KV 800A DB Break AB Switch | Elecy | Supply | SMR12315 | 40658.78 | EA | 81317.56
232 | 11 | survey line&cabl inc peg mark&tree clear | Elecy | labour | SWR22092 | 765 | KM | 8415
233 | 75 | Supply of M+3 Tower (Galvanized) | Elecy | labour | SMR11683 | 140674.3 | EA | 10550572.5
234 | 75 | Supply of material for Extension of 3Mtrs for M+3 (Galvanized) | Elecy | labour | SMR11684 | 28520.64 | EA | 2139048
235 | 75 | Erection of M+3 Tower (Galvanized) | Elecy | labour | SWR11850 | 64576 | EA | 4843200
236 | 75 | Erection of Extension of 3Mtrs for M+3 (Galvanized) | Elecy | labour | SWR11851 | 5168.95 | EA | 387671.25
237 | 356.4 | Earth work excavation of pits in hard murram/rock boulders | Elecy | labour | SWR20959 | 1530 | M3 | 545292
238 | 4 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 12Mtrs/Spun Pole 0.92 M x 0.92M x 2.3M (3.0" x 3.0" x 7.6") Exc of Hard pit w/o blast 0.92X0.92X2.3M | Elecy | labour | SWR11041 | 1466.25 | EA | 5865
239 | 4 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Erect-12Meter Box pole | Elecy | labour | SWR11267 | 3901.37 | EA | 15605.48
240 | 8 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. Fabrication of 175x85/150x75mm RS joist | Elecy | labour | SWR10642 | 512.55 | EA | 4100.4
241 | 8 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables Painting of RS Joist(1C RO, 2C Al.Paint) | Elecy | labour | SWR10640 | 1132 | EA | 9056
242 | 4.41 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement. Mass concreting of supports incl. cement | Elecy | labour | SWR10356 | 6579 | M3 | 29013.39
243 | 25 | Formation of Cut point for 33 KV Double circuit line excluding pole erection and stays Formation of 33kvline vertical cutpoint | Elecy | labour | SWR10466 | 3198.72 | EA | 79968
244 | 6.55 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | Elecy | labour | SMR40009 | 2181 | TO | 14285.55
245 | 6.55 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | Elecy | labour | SWR10877 | 851 | TO | 5574.05
246 | 6.55 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | Elecy | labour | SMR40010 | 1293 | TO | 8469.15
247 | 6.55 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | Elecy | labour | SWR10879 | 482 | TO | 3157.1
248 | 11 | Paving out and stringing of conductor by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location. 100 Sqmm Single Circuit (3 Conductors) Stringing 100sqmm 33/11kv Line 3 Cond SC | Elecy | labour | SWR10366 | 13856.7 | KM | 152423.7
249 | 660 | LOADING of 33 KV Pin insulators | Elecy | labour | SWR10211 | 3 | CRT | 1980
250 | 660 | UNLOADING of 33 KV Pin insulators | Elecy | labour | SWR10529 | 3 | CRT | 1980
251 | 5 | LOADING of 33KV Metal parts-bag of 25no | Elecy | labour | SWR10618 | 65 | BAG | 325
252 | 4 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Transport of Cond Drum,VCBs >20 & <30Km | Elecy | labour | SWR11862 | 3691.38 | EA | 14765.52
253 | 50 | S-GI Bolts & Nuts,Washers etc., | Elecy | labour | SMR11488 | 117.5 | KG | 5875
254 | 5 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Transport of Cond Drum,VCBs >20 & <30Km | Elecy | labour | SWR11862 | 3691.38 | EA | 18456.9
255 | 7 | Load-11/33KV XLPE UG Cable for all sizes | Elecy | labour | SWR11230 | 1024 | DR | 7168
256 | 7 | Unload-11/33KV XLPE UG Cable all sizes | Elecy | labour | SWR11231 | 1024 | DR | 7168
257 | 940 | Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, Along the CC / BT multi layer road requiring compressor Lay-DR 33KV 3x400sqmm UG Cb CC/BT Compsr | Elecy | labour | SWR11980 | 1388.84 | M | 1305509.6
258 | 60 | Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) Raise-DR 33KV 3x400sqmm UG Cb on support | Elecy | labour | SWR12004 | 323.85 | M | 19431
259 | 940 | Lay-2nd Cable in Excavated Trench | Elecy | labour | SWR10988 | 204.1 | M | 191854
260 | 10 | Making 33 KV 3x400 Sqmm Cable Out Door/Indoor end termination | Elecy | labour | SWR10387 | 2764.76 | EA | 27647.6
261 | 10 | Straight through joint 33kv 3x400 xlpe | Elecy | labour | SWR10382 | 5700.78 | EA | 57007.8
262 | 3 | Erection of 33 KV AB Switch including alignment and earthing | Elecy | labour | SWR10392 | 4500 | EA | 13500
263 | 3 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Painting of operating rods of 33kV, 11kV AB switches withpost office red colour (including cost of paint) Painting AB switch OP rods with PO red | Elecy | labour | SWR10881 | 142 | EA | 426
264 | 10 | LOADING of Conductor drums | Elecy | labour | SWR10191 | 202 | EA | 2020
265 | 10 | UNLOADING of Conductor drums | Elecy | labour | SWR10509 | 100 | EA | 1000
266 | 3 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch AB Switch Coil Earthing GI No. 8 Wire | Elecy | labour | SWR12331 | 146.63 | EA | 439.89
267 | 6.55 | Fabrication of Main and Auxiliary structures with welding using raw steel such as RS joist, M.S.Angles, Plates, Channels, including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elecy | labour | SWR10869 | 3426 | TO | 22440.3
268 | 100 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 12Mtrs/Spun Pole 0.92 M x 0.92M x 2.3M (3.0" x 3.0" x 7.6") Exc of Hard pit w/o blast 0.92X0.92X2.3M | Elecy | labour | SWR11041 | 1466.25 | EA | 146625
269 | 100 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation - Spun poles 12.5 Mtrs / 12.9Mtrs PSCC Erection of Spun pole 12.5Mt | Elecy | labour | SWR10350 | 4521.66 | EA | 452166
270 | 110.89 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | Elecy | labour | SWR10356 | 6579 | M3 | 729545.31
271 | 3 | S-33KV 800A DB Break AB Switch | Elecy | supply | SMR12315 | 40658.78 | EA | 121976.34
272 | 2000 | S-RS Joist Pole (175x85mm) | Elecy | supply | SMR12303 | 60.75 | KG | 121500
273 | 3500 | S- MS Channel 100x50mm | Elecy | supply | SMR22745 | 57.45 | KGS | 201075
274 | 1350 | S-MS Flat 75x8mm | Elecy | supply | SMR12321 | 56.42 | KG | 76167
275 | 200 | S-MS Flat 50x6mm | Elecy | supply | SMR12322 | 56.5 | KG | 11300
276 | 10 | Supply of 33KV3x400Sqmm Straight thr kit | Elecy | supply | SMR22223 | 24151 | EA | 241510
277 | 10 | Supply of 33KV 3x400Sqmm O/D End Kit | Elecy | supply | SMR22222 | 4554 | EA | 45540
278 | 100 | S-PSCC Spun Pole 12.5Mtr | Elecy | supply | SMR25238 | 15635.59 | EA | 1563559
279 | 1500 | S-MS Angle 65X65X6 | Elecy | supply | SMR25207 | 57.25 | KG | 85875
280 | 4 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 12Mtrs/Spun Pole 0.92 M x 0.92M x 2.3M (3.0" x 3.0" x 7.6") Exc of Hard pit w/o blast 0.92X0.92X2.3M | Elecy | labour | SWR11041 | 1466.25 | EA | 5865
281 | 4 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Erect-12Meter Box pole | Elecy | labour | SWR11267 | 3901.37 | EA | 15605.48
282 | 8 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. Fabrication of 175x85/150x75mm RS joist | Elecy | labour | SWR10642 | 512.55 | EA | 4100.4
283 | 8 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables Painting of RS Joist(1C RO, 2C Al.Paint) | Elecy | labour | SWR10640 | 1132 | EA | 9056
284 | 4.41 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | Elecy | labour | SWR10356 | 6579 | M3 | 29013.39
285 | 3800 | Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, Along the CC / BT multi layer road requiring compressor Lay-DR 11KV 3x300sqmm UG Cb CC/BT Compsr | Elecy | labour | SWR11981 | 1264.64 | M | 4805632
286 | 200 | Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) Raise-DR 11KV 3x300sqmm UG Cb on support | Elecy | labour | SWR12005 | 275.4 | M | 55080
287 | 8 | Making 11 KV 3x300 Sqmm Cable Out Door/Indoor end termination OD/Idoor end termination 11kv 3x300 xlpe | Elecy | labour | SWR10391 | 2370.63 | EA | 18965.04
288 | 16 | Straight through joint 11kv 3x300 xlpe | Elecy | labour | SWR10386 | 3725.45 | EA | 59607.2
289 | 2 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Elecy | labour | SWR10393 | 3200 | EA | 6400
290 | 2 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Note:-The requirement of 2nd coat is to be justified by the concerned Divisional Engineer /Executive Engineer before execution of this work Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elecy | labour | SWR10881 | 142 | EA | 284
291 | 20 | Supply of earthing pipe with materials S-Earthing GI flat 25x3 mm incl material | Elecy | labour | SMR11485 | 105 | KG | 2100
292 | 8 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Above 20 Km and upto 30 Km with Lorry for each trip Transport of Cond Drum,VCBs>20 & <30Km | Elecy | labour | SWR11862 | 3691.38 | EA | 29531.04
293 | 10 | Supply of Danger boards with clamps | Elecy | labour | SMR40070 | 116 | EA | 1160
294 | 6 | S-CI Pipe earthing 50mm dia 2m long | Elecy | labour | SMR11484 | 2441 | EA | 14646
295 | 6 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINES-Providing of RCC collar | Elecy | labour | SWR10359 | 386 | EA | 2316
296 | 6 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elecy | labour | SWR10357 | 1234.2 | EA | 7405.2
297 | 100 | Supply of earthing pipe with materials Supply of GI Flat 25X3 mm including material | Elecy | labour | SMR11485 | 105 | KG | 10500
298 | 16 | Load-11/33KV XLPE UG Cable for all sizes | Elecy | labour | SWR11230 | 1024 | DR | 16384
299 | 16 | Unload-11/33KV XLPE UG Cable all sizes | Elecy | labour | SWR11231 | 1024 | DR | 16384
300 | 0.8 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | Elecy | labour | SMR40009 | 2181 | TO | 1744.8
301 | 0.8 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | Elecy | labour | SWR10877 | 851 | TO | 680.8
302 | 0.8 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | Elecy | labour | SMR40010 | 1293 | TO | 1034.4
303 | 0.8 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | Elecy | labour | SWR10879 | 482 | TO | 385.6
304 | 3800 | Lay-2nd Cable in Excavated Trench | Elecy | labour | SWR10988 | 204.1 | M | 775580
305 | 0.8 | Fabrication of Main and Auxiliary structures with welding using raw steel such as RS joist, M.S.Angles, Plates, Channels, including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elecy | labour | SWR10869 | 3426 | TO | 2740.8
306 | 2000 | S-RS Joist Pole (175x85mm) | Elecy | supply | SMR12303 | 60.75 | KG | 121500
307 | 500 | S- MS Channel 100x50mm | Elecy | supply | SMR22745 | 57.45 | KGS | 28725
308 | 150 | S-MS Flat 75x8mm | Elecy | supply | SMR12321 | 56.42 | KG | 8463
309 | 150 | S-MS Flat 50x6mm | Elecy | supply | SMR12322 | 56.5 | KG | 8475
310 | 16 | S-11KV 3x300 Heat Shble str thr JointKit | Elecy | supply | SMR25210 | 4110.17 | EA | 65762.72
311 | 8 | S-11KV 3x300 Heat Shble O/d End Term Kit | Elecy | supply | SMR25208 | 1372.88 | EA | 10983.04
312 | 2 | S-11KV 400A Conv ABSwitch with Insulator | Elecy | supply | SMR25211 | 11754 | EA | 23508
Electrical Labour | [7 empty] | 38105376.8541
WBS. No. S-1799-13-07-01-01-001(Civil)
SL.NO. | Estimate Quantity (only Figures) | Item Detailed Specification Description | Work Type eg. Earth Work, Electrical works. etc (upto 200 Characters) | Item Short Description (upto 100 Characters) | APSS / Morth Cl. Number (upto 200 Characters) | Rate (INR) (Upto 2 Decimals ) | UOM (upto 50 Characters) | Amount
1 | 32 | Leveliing the site by cutting and levelling with the help of JCB including cost,conveyance of all materials,hire chareges etc complete for finished item of work as directed by Engineer-in-charge. | Civil | Labour | SWR34179 | 2165 | Hrs | 69280
2 | 149.95 | Earth Work Mass Excavation (hard rock) to a depth as directed, in soils such as hard rock requiring blasting in prohibited area and all conditions such as dry, wet, slurry etc.and in dense or hard soils, disposal and depositing of excavated soil with intial lead of 10 mt and intial lift of 2m or as directed, including cost and conveyance of all materials, ramping and lifting of materials, and labour charges, hire charges of machinery, tools & plants, bailing of water ( either sub soil water, stoMts water, rain water, surface water or of any kind) if any at any stage of work until all works below ground level is finished to the satisfaction ,and from work such as shoring, timbering, strutting with required supports etc. for the work and removal of form work after completion of work etc all complete as directed by the engineer-incharge. | Civil | Labour | SWR33018 | 1440 | cum | 215928
3 | 115.65 | Earth work excavation in all type of soils red earth, Hard gravelly soils, earth mixed with sand and sandy soils etc., in all conditions such as slushy and dry with initial leads and lifts for foundations. Ordinary Soil | Civil | Labour | SWR33015 | 486 | cum | 56205.9
4 | 22.79 | Plain Cement concrete (1:4:8) using 40mm HBG metal for foundations and leveling course, including cost and conveyance of all materials, labour all leads and lifts, consolidation and all operations, formwork as required, curing, etc. complete for finished item w | Civil | Labour | SWR33028 | 4676 | cum | 106566.04
5 | 108.3 | Coursed Rubble stone masonry 2nd sort with hard granite stones in cement mortar (1:6) for basement, including cost and conveyance of all materials, labour charges, curing, all leads and lifts, etc, complete for finished item of work. | Civil | Labour | SWR33041 | 4824 | cum | 522439.2
6 |  | RCC M20 Grade nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials labour scaffolding, centering, machine mixing, vibrating, curing all leads and lifts, in all positions of the building but excludi
| 1.09 | RCC M20 Grade Footing | Civil | Labour | SWR33098 | 9428 | cum | 10276.52
| 1.58 | RCC M20 Grade Column | Civil | Labour | SWR33100 | 13177 | cum | 20819.66
| 1.15 | RCC M20 Grade plinth beam | Civil | Labour | SWR33099 | 12299 | cum | 14143.85
7 | 0.46 | Supplying, Cutting, bending, binding, placing in position and tying reinforcement steel in all heights including cost and conveyance of steel and binding wire etc,. With all leads and lifts, labour charges, etc., complete for finished item of work. | Civil | Labour | SWR33144 | 70687 | MT | 32516.02
8 | 66.71 | Brick masonry in cement mortar (1:6) for superstructure using well burnt country made second class bricks of approved quality including cost and conveyance of all materials curing, scaffolding with all leads and lifts in all heights etc., complete for fin | Civil | Labour | SWR33068 | 8242 | cum | 549823.82
9 | 6.98 | Plain Cement concrete (1:2:4) using 20mm size well graded HBG metal for foundations, including cost, conveyance of all materials,labour all leads and lifts,consolidation and all operations, formwork as required, curing,etc. complete for finished item of work | Civil | Labour | SWR33030 | 6046 | cum | 42201.08
10 | 630.95 | Plastering with two coats, 1st coat in cm1:5 16mm thick and 2nd coat in cm 1:4 4mm thick, total 20mm thick for superstructure walls, ceiling, sunshades, Beams, etc., with sponge finishing including cost and conveyance of all materials all leads & lifts e | Civil | Labour | SWR33163 | 559 | Sqm | 352701.05
11 | 27 | Painting with two coats of ACE paint over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33356 | 210 | Sqm | 5670
12 | 781.85 | Painting with two coats of Surya Cem paint over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33329 | 85 | Sqm | 66457.25
13 | 380 | Manufacturing, Supplying and fixing of MS grill for (Gate and raillings) of approved design as per drawings, including cost and conveyance of all materials, labour charges etc.,complete for finished item of work as directed by the Engineer- in-charge. | Civil | Labour | SWR33145 | 128 | Kgs | 48640
14 | 3 | Supply and Fixng of MS Name Board including cost & conveyance of all materials,labour charges etc complete for finished item of work. | Civil | Labour | SWR33421 | 4326 | sqm | 12978
15 | 1 | Geophysical Investgation charges for water point by Geologist | Civil | Labour | SWR33608 | 5000 | EA | 5000
16 |  | Drilling of 165mm bore well with machine rig including deployment and hire charges of rig and other machinery and equipment labour charges , measuring the yeild of borewell including cost and conveyance etc complete
17 | 90 | Drill-165mm Bore Well 0 to 90 | Civil | Labour | SWR33609 | 336 | M | 30240
18 | 30 | Drill-165mm Bore Well 90M to 120M | Civil | Labour | SWR34830 | 369 | M | 11070
19 | 30 | Drill-165mm Bore Well 120M to 150M | Civil | Labour | SWR34831 | 394 | M | 11820
20 | 30 | Drill-165mm Bore Well 150M to 180M | Civil | Labour | SWR34832 | 492 | M | 14760
21 | 30 | Drill-165mm Bore Well 180M to 210M | Civil | Labour | SWR34833 | 623 | M | 18690
22 | 30 | Drill-165mm Bore Well 210M to 240M | Civil | Labour | SWR34834 | 754 | M | 22620
23 | 30 | Drill-165mm Bore Well 240M to 270M | Civil | Labour | SWR34835 | 918 | M | 27540
24 | 105 | Drill-165mm Bore Well 270M and above | Civil | Labour | SWR34836 | 1082 | M | 113610
25 | 40 | Supply and fixing of 160mm dia PVC casing of A class 6Kg point pressure including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR33611 | 883 | M | 35320
26 | 1 | Supply and erecting, ISI mark submersible 5.0 HP, Single Phase 30 stages pumpset suitable for 106/156mm dia borewell including cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33640 | 48007 | EA | 48007
27 | 312 | Supply and fixing of HDPE pipe 40mm dia of 16Kg/cm2 including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR34410 | 180 | M | 56160
28 | 1 | Supply and erecting D.O.L Starter 415V , Single phase,50Hz with SS enclouserincluding cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33645 | 7854 | EA | 7854
29 | 360 | Supply of 3 Core 2.5 Sqmm Flat Copper cable of ISI for Submersible Motors of makes Finolex / Polycab / Gold Medal / Million / Payal / Sun Light / Power Flex / Fortune Art | Civil | Labour | SWR33641 | 192 | M | 69120
30 | 6 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-28.60mm OD Pipe - SDR 11 | Civil | Labour | SWR34363 | 410 | M | 2460
31 | 1 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type - 25mm NB Size | Civil | Labour | SWR34346 | 466 | EA | 466
32 | 64.95 | Earth work excavation in all type of soils red earth, Hard gravelly soils, earth mixed with sand and sandy soils etc., in all conditions such as slushy and dry with initial leads and lifts for foundations. | Civil | Labour | SWR33015 | 486 | Cum | 31565.7
33 | 13.54 | Plain Cement concrete (1:4:8) using 40mm HBG metal for foundations and leveling course, including cost and conveyance of all materials, labour all leads and lifts, consolidation and all operations, formwork as required, curing, etc. complete for finished item w | Civil | Labour | SWR33028 | 4676 | Cum | 63313.04
34 | 26.08 | Coursed Rubble stone masonry 2nd sort with hard granite stones in cement mortar (1:6) for basement, including cost and conveyance of all materials, labour charges, curing, all leads and lifts, etc, complete for finished item of work. | Civil | Labour | SWR33041 | 4824 | Cum | 125809.92
35 | 51.88 | Supplying and filling the substation site with borrowed gravel, watering, ramming, thoroughly complying with the standard specification. | Civil | Labour | SWR33052 | 309 | Cum | 16030.92
36 |  | RCC M20 Grade nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials labour scaffolding, centering, machine mixing, vibrating, curing all leads and lifts, in all positions of the building but excludi
| 3.56 | a) RCC M20 Grade Column Footings | Civil | Labour | SWR33098 | 9428 | Cum | 33563.68
| 2.28 | b) RCC M20 Grade Columns | Civil | Labour | SWR33100 | 13177 | Cum | 30043.56
| 2.25 | c) RCC M20 Grade Plinth Beams Long wall | Civil | Labour | SWR33099 | 12299 | Cum | 27672.75
| 3.17 | D) RCC M20 Grade Roof Beams landing beam | Civil | Labour | SWR33121 | 12215 | Cum | 38721.55
| 0.58 | e) RCC M20 Grade Lintels doors | Civil | Labour | SWR33107 | 13007 | Cum | 7544.06
| 2.7 | f) RCC M20 Grade Sunshades 600mm wide and 75mm thick | Civil | Labour | SWR33114 | 1371 | Sqm | 3701.7
| 15.22 | g) RCC M20 Grade Roof Slab for Control Room | Civil | Labour | SWR33128 | 10803 | Cum | 164421.66
38 | 3 | Supplying, Cutting, bending, binding, placing in position and tying reinforcement steel in all heights including cost and conveyance of steel and binding wire etc,. With all leads and lifts, labour charges, etc., complete for finished item of work. | Civil | Labour | SWR33144 | 70687 | MT | 212061
39 | 38.36 | Brick masonry in cement mortar (1:6) for superstructure using well burnt country made second class bricks of approved quality including cost and conveyance of all materials curing, scaffolding with all leads and lifts in all heights etc., complete for fin | Civil | Labour | SWR33068 | 8242 | Cum | 316163.12
40 | 517.26 | Plastering with two coats, 1st coat in cm1:5 16mm thick and 2nd coat in cm 1:4 4mm thick, total 20mm thick for superstructure walls, ceiling, sunshades, Beams, etc., with sponge finishing including cost and conveyance of all materials all leads & lifts e | Civil | Labour | SWR33163 | 559 | Sqm | 289148.34
41 | 16.56 | Providing Design R.C. drop wall of 25mm thickness with cm 1:3 and 6mm dia MS bars at 150mm both ways and chicken mesh in two coats 20mm thick each plastering including cost and conveyance of all materials with leads and lifts, scaffolding and curing, labo | Civil | Labour | SWR33203 | 3035 | Sqm | 50259.6
42 | 12.24 | Supply and fixing of Ms ornamental safety grill of approved design including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33310 | 2990 | sqm | 36597.6
43 | 5.91 | Supply and fixing of doors with the frames of the door shall be made well seasoned mt wood of cross section 100x75mm. The shutter shall be made isi mark flushed door with decolam sheets pasted on both sides with PVC beading 40mm width all round.Frame shall be painted with two coats of synthetic enamel paint of approved color over one coat of primer over luppum with spary with 3 no 150mm brass hinges 1 no brass door stoper, 1 no 250mm brass aldrops. 2 no 300 mm aluminium tower bolts, 2 no 150mm brass fancy door handlers, 1 no keyless lockset with cp handel. The quoted rate shall include cost and conveyance of the meterials, fixig, labour carges, tools, handles,locking arrangementts and other fixtures & fittings for finished item work as directed by the Engineer - in- charge. | Civil | Labour | SWR33264 | 7314 | Sqm | 43225.74
44 | 20.25 | Raised pointing to the exposed surfaces of CRS masonry in cm 1:3 prop. including cost and conveyance of all materials, labour charges, all leads and lifts curing etc, complete for finished item of work. | Civil | Labour | SWR33184 | 124 | sqm | 2511
45 | 8.64 | Supplying and fixing Aluminium sliding windows with grill and fixed glass panels using anodised aluminium extruded sections of mat finish for frames and mullions made from approved aluminium sections 62x32x1.2mm at 0.73kg/Rm providing 5mm plain glass fix | Civil | Labour | SWR33277 | 3623 | sqm | 31302.72
46 | 16.56 | Supply and laying of Ceramic floor over of CM 1:3 20 mm thick including required materials and labour charges etc complete for item of work | Civil | Labour | SWR33224 | 914 | Sqm | 15135.84
47 | 121.92 | Flooring with double machine polished and hand cut Tandur blue stone 20mm thick of approved colour, quality and of minimum of 300x300mm size over a bed of cement mortar 1:3 20mm thick including cost of all materials, with all leads and lifts jointing and | Civil | Labour | SWR33219 | 785 | Sqm | 95707.2
48 | 6.74 | Supply and fixing of 4" high skirting of shabad stone to the walls including cost and conveyance of all materials, labour etc for finished item of work. | Civil | Labour | SWR33236 | 875 | Sqm | 5897.5
49 | 243.69 | Painting with two coats of OBD over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials labour charges etc., complete for finished item of work. | Civil | Labour | SWR33333 | 146 | Sqm | 35578.74
50 | 349.52 | Painting with two coats of ACE paint over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33356 | 210 | Sqm | 73399.2
51 | 101.17 | Providing impervious coat over RCC roof slab to requried slopes with 20mm thick in CM 1:3 mixed with approved brand of water proffing compound inclding cost and conveyance of all materials, labour charges, curing, rounding off junctions of wall and slab, all leads and lifts, etc . complete for finished item of work as directed by the Engineer - in - charge. | Civil | Labour | SWR33156 | 582 | sqm | 58880.94
52 | 60 | Supply & fixing of 25mm dia 2mm thick suSupply & fixing of 25mm dia 2mm thick surface P.V.C. pipe (ISI MARK) Concealed in wall with all required accessories including masonary work and labour charges etc.complete. | Civil | Labour | SWR33441 | 108 | M | 6480
53 | 1 | Supply & fixing TPN Distribution board w Supply & fixing TPN Distribution board with IP-42 protection (Metal Door)suitable for 3 phase ELCB/RCCB/FP Isolator as incomer and 10kA SP MCBs as out going including internal connection and labour charges for surface / flush mounting etc Complete. | Civil | Labour | SWR33526 | 11353 | EA | 11353
54 | 10 | Supply & fixing of 6A 3 pin wall plug so Supply & fixing of 6A 3 pin wall plug socket with 6A switch control on a common switch board with earth continuity including wire leads,earth connection along with all labour charges etc., complete | Civil | Labour | SWR33468 | 166 | EA | 1660
55 | 6 | Supply & fixing of 16A 3 pin and 6A 3pin Supply & fixing of 16A 3 pin and 6A 3pin plug Flush type socket with indicator lamp and 16Amps fuse unit and 16Amps switch control (5 in one )duly recessed in wall with wooden deep box of 6'' x 8'' x 2 1/2'' size covered with hylam sheet earth connection and all labour charges etc., complete on wall. | Civil | Labour | SWR33470 | 449 | EA | 2694
56 | 24 | Wiring with 2 runs of 14/0.3mm (1.0 sq.m Wiring with 2 runs of 14/0.3mm (1.0 sq.mm)Fire Retardant (FR) P.V.C. insulated flexible copper cable (ISI MARK) in existing pipe with 6A Flush type Switch,ceiling rose and 3mm thick hylam sheet covering to switch control box including all labour charges etc., complete for light points, bell , fan and exhaust fan points in Non-Residential Buildings. | Civil | Labour | SWR33457 | 676 | EA | 16224
57 | 12 | Supply & Fixing of 28W T5 fluorescent tube. | Civil | Labour | SWR33558 | 148 | EA | 1776
58 | 1 | Supply of 12" (300mm)ISI, 900 RPM Heavy duty exhaust fan with metallic blades with Mark of makes Crompton / Bajaj / Havells / Orient. | Civil | Labour | SWR33571 | 2192 | EA | 2192
59 | 180 | Supply and run of 2 of 22/0.3mm (1.5 sq.mm) (FR) P.V.C. insulated flexible copper cable in existing pipe for mains including all labour charges complete. | Civil | Labour | SWR33496 | 75 | M | 13500
60 | 180 | Supply and run of 2 of 36/0.3mm (2.5 sq.mm) FR P.V.C. insulated flexible copper cable in existing pipe for mains including all labour charges complete. | Civil | Labour | SWR33497 | 103 | M | 18540
61 | 12 | Supply & fixing of batten holder /slanting holder in lieu of ceiling rose of light point complete with all connection and all labour charges with 40W bulb (for new installation). | Civil | Labour | SWR33484 | 141 | EA | 1692
62 | 4 | Supply & fixing of 1200mm (48'') sweep 230v,A.C 50 Hz.Ceiling fan with 3 Blades and double ball bearings with all standared accessories. | Civil | Labour | SWR33563 | 2277 | EA | 9108
63 | 4 | Supply & fixing of Electronic Regulator for ceiling fans 900/1200/1400mm sweep including cost of material, Electrical charges complete for finished item of work | Civil | Labour | SWR33564 | 589 | EA | 2356
64 | 1 | Providing independent EARTHING by excavating a trench to a depth of 2.1M in all solid,as per size specified in the Data,using 40mm dia 'B' class GI pipe of 2.5 Mtrs length with necessary accessories with hume pipe ring duly providing staggered holes including filling with equal proportion of salt and Charcoal in layers and all labour charges etc., compiete for small quarters. | Civil | Labour | SWR33596 | 5345 | EA | 5345
65 | 35 | Supplying, laying, jointing and testing 101.6 mm SWG SP-1 pipes of ISI make conforming to ISI 651 & 4127 with airtight cement joints in CM 1.5:1 prop. Including excavation of trenches and socket pits in any soil (except rock requiring blasting) up to 1524 mm(5'0") depth and refilling with watering and tamping. | Civil | Labour | SWR34281 | 755 | M | 26425
66 | 3 | Constructing 904.0 mm (3#0#) dia brick masonry inspection chamber as per IS - 4111: Part-1:1986 with cement mortar (1:6) prop using 2nd Class Clay Bricks of 225 mm thick from approved source having a minimum crushing strength of 5 N/sq.mm including plastering with cement mortar 1:3 prop; ½# thick both inside and outside fitted with 20# dia RCC manhole covers and frames including excavating pits up to a depth of 904 mm (3'-0") in all sorts of soils (excluding rock) and laying cement concrete (1:4:8) 150 mm thick using 40 mm HBG Metal and P.C.C. 1:2:4 benching and channel 100 mm thick as per Standard specification and including cost and conveyance of all materials like cement, sand, bricks, water etc., to site, cost of seigniorage charges on all materials and all incidental and operational, labour charges like mixing cement mortar, constructing masonry, lift charges, curing etc., complete for finished item of work as per Standard specification. | Civil | Labour | SWR34296 | 8766 | EA | 26298
67 | 4 | Supply & fixing of 110 mm dia - Door Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34381 | 128 | EA | 512
68 | 4 | Supply & fixing of 110 mm dia - Plain Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34380 | 100 | EA | 400
69 | 12 | Supply & fixing of 110 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand | Civil | Labour | SWR34377 | 462 | M | 5544
70 | 18 | Supply & fixing of 90 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand | Civil | Labour | SWR34378 | 410 | M | 7380
71 | 3 | Supplying & fixing 150 mm x 100 mm SWG gully traps conforming to ISI 651 & 4127 with C.I Grating & Cost. Brick masonry in CM 1:6 prop. Intermediate chamber and fitted with 304.8 mm x 288.6mm (12"x9") C.I Frame and hinged cover | Civil | Labour | SWR34286 | 767 | EA | 2301
72 | 1 | Supplying and Fixing of European Water Closet of 1st Quality | Civil | Labour | SWR34314 | 2228 | EA | 2228
73 | 6 | Supply & fixing 12.7 mm NP stop cock Indian make 400 grams Seiko/ Senior/ Nice/ Senior/ Nice or equivalent | Civil | Labour | SWR34328 | 721 | EA | 4326
74 | 4 | S&F 12.7 mm N.P bib tap Indian make 400 grams Seiko/ Senior/ Nice or equivalent | Civil | Labour | SWR34329 | 296 | EA | 1184
75 | 1 | Supplying & Fixing Indian make Flat Back Wash Hand Basin (HSW/Parryware/ Neycer) 1st quality conforming to IS:2556-Part-4:1972 with waste fittings like rubber plug, chain, 32 mm nominal size C.P. Fitting with parallel pipe thread conforming to IS:2963-1979 and fitted with 15 mm nominal bore Chromium Plated Pillar Tap of 1st quality Indian make 400 grams Seiko/ Senior/ Nice/ Esso or equivalent complete with standard CI brackets including wooden block: 550 x 400 mm - Single C.P. Pillar cock | Civil | Labour | SWR34316 | 1717 | EA | 1717
76 | 2 | Supply & fixing 38.1 mm C.P waste coupling Half or Full Thread 1st Quality Indian make Parryware or equivalent | Civil | Labour | SWR34428 | 309 | EA | 618
77 | 2 | Supply & fixing of 4" (101.6 mm ) Nahany Trap ( Without Jali with inlet)UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34387 | 134 | EA | 268
78 | 1000 | Providing & Placing on Terrace (at all floor levels) polyethylene water storage tank with Double layer approved brand & manufacture with cover and suitable locking arrangement & making necessary holes for inlet & outlets and over flow pipes but with NECESSARY fittings & base support for tanks | Civil | Labour | SWR34375 | 10 | L | 10000
79 | 2 | Supply & fixing 31.75 mm dia PVC flexible waste pipe of 914.4 mm length of Ist quality | Civil | Labour | SWR34426 | 33 | EA | 66
80 | 45 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)- 15.90mm OD Pipe - SDR 11 | Civil | Labour | SWR34361 | 239 | M | 10755
81 | 40 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-22.20mm OD Pipe - SDR 11 | Civil | Labour | SWR34362 | 313 | M | 12520
82 | 65 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-28.60mm OD Pipe - SDR 11 | Civil | Labour | SWR34363 | 410 | M | 26650
83 | 4 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type - 25mm NB Size | Civil | Labour | SWR34346 | 466 | EA | 1864
84 | 4 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type -20mm NB Size | Civil | Labour | SWR34345 | 331 | EA | 1324
85 | 1 | Supply & fixing 25.4 mm dia & 609.6 mm long aluminium anodized towel rod with brackets and aluminium screws | Civil | Labour | SWR34430 | 489 | EA | 489
86 | 85.51 | Earth work excavation in all type of soils red earth, Hard gravelly soils, earth mixed with sand and sandy soils etc., in all conditions such as slushy and dry with initial leads and lifts for foundations. Ordinary Soil. | Civil | Labour | SWR33015 | 486 | cum | 41557.86
87 | 18.91 | Plain Cement concrete (1:4:8) using 40mm HBG metal for foundations and leveling course, including cost and conveyance of all materials, labour all leads and lifts, consolidation and all operations, formwork as required, curing, etc. complete for finished item w | Civil | Labour | SWR33028 | 4676 | cum | 88423.16
88 | 91.8 | Coursed Rubble stone masonry 2nd sort with hard granite stones in cement mortar (1:6) for basement, including cost and conveyance of all materials, labour charges, curing, all leads and lifts, etc, complete for finished item of work. | Civil | Labour | SWR33041 | 4824 | cum | 442843.2
89 | 36 | Plain Cement concrete (1:3:6) using 40mm HBG metal for foundations and leveling course, including cost and conveyance of all materials, labour all leads and lifts, consolidation and all operations, formwork as required, curing, etc. complete for finished item w | Civil | Labour | SWR33029 | 4966 | cum | 178776
90 | 108 | Raised pointing to the exposed surfaces of CRS masonry in cm 1:3 prop. including cost and conveyance of all materials, labour charges, all leads and lifts curing etc, complete for finished item of work. | Civil | Labour | SWR33184 | 124 | sq.mm | 13392
91 | 787.5 | Supplying and filling the substation site with borrowed gravel, watering, ramming, thoroughly complying with the standard specification. | Civil | Labour | SWR33052 | 309 | cum | 243337.5
92 | 88.8 | Plastering with two coats, 1st coat in cm1:5 16mm thick and 2nd coat in cm 1:4 4mm thick, total 20mm thick for superstructure walls, ceiling, sunshades, Beams, etc., with sponge finishing including cost and conveyance of all materials all leads & lifts e | Civil | Labour | SWR33163 | 559 | sq.mm | 49639.2
93 | 200.85 | Painting with two coats of Surya Cem paint over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33329 | 85 | sq.mm | 17072.25
94 | 120 | Supply&Fabrication and fixing of Welded wire mesh ( 2" x 2") of 3mm dia. with ISMC (75x40x4.4mm) and Pheriperal frame of ISA(35x35x3mm) incldg cost& conveyance painting with synthetic enamil paint two coats over a coat of red oxide primer etc complete for finished item of work.. | Civil | Labour | SWR33403 | 2310 | sq.mm | 277200
95 | 160 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-22.20mm OD Pipe - SDR 11 | Civil | Labour | SWR34362 | 313 | M | 50080
96 | 30 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type - 25mm NB Size | Civil | Labour | SWR34346 | 466 | EA | 13980
97 | 1 | Providing Consultancy services for arranging contour surveying with total station incuding preparation of boundary and contour levels with 2 Nos. Hard copies and soft copies complete for finished items of work | Civil | Labour | SWR33427 | 5665 | EA | 5665
98 | 425.08 | Seigniorage Charges - Sand | Civil | Labour | SWR34470 | 40 | cum | 17003.2
99 | 1434.28 | Seigniorage Charges - Metal | Civil | Labour | SWR34471 | 97.5 | cum | 139842.3
100 | 839.38 | Seigniorage Charges - Gravel | Civil | Labour | SWR34472 | 30 | cum | 25181.4
101 | 60 | Supply and fixing of RCC fencing poles of size 0.1mx0.1mx1.8m (security fencing of sub station), including cost and conveyance of all labour, materials,and hire chareges etc complete for finished item of work. | Civil | Labour | Swr33405 | 1444 | EA | 86640
102 | 1200 | Supply and fixing of galvanised barded wire (1 horizantal & 2 cross strands. including cost and conveyance of all labour, materials,and hire chareges etc complete for finished item of work. | Civil | Labour | Swr33408 | 16 | M | 19200
[5 empty] | Civil labour |  |  | 6355262.54
[5 empty] | Electrical and Civil labour |  |  | 44460639.3941