## Schedule
Schedule for the work of "Erection, testing & commissioning of new 33/11kV outdoor substation with 2x8 MVA PTRs and connected 33kV & 11kV feeders along with Construction of Control room, Compound wall and other civil works at Sy No. 152/P Jawahar nagar colony, Chandanagar (V), Serilingampally (M) in Vemana colony section of Kukatpally division in Medchal operation circle, of Master plan Sub-division 1 of WCGH Division in Rangareddy circle under T&D improvement works."
WBS No. S-1936-13-04-01-01-001 & WBS. No. S-1936-13-07-01-01-001
D.No :SAN NO. 31, D. NO. 1414/2025-26, DT: 16.10.2025
S.No | Estimate Quantity(Only Figures) | PARTICULARS | Work Type | Item Short Description | SWR No/APSS/Morth cl.No | Rate (INR) (Upto 2 Decimals) | UOM | Amount
1 | 16 | LOADING of RSJoists150 x 150 mm/RailPole | Elecy | Labour | SWR10205 | 176 | EA | 2816
2 | 5.76 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 KM and upto 20 KM | Elecy | Labour | SWR10132 | 412.08 | TO | 2373.5808
3 | 16 | UNLOADING of RSJoists150 x150 mm/RailPol | Elecy | Labour | SWR10523 | 107 | EA | 1712
4 | 16 | EXCAV. OF PIT HARD(2.6" x 2.6" x 6.0") Excavation of pits in hard rock requiring blasting. (other than SS) 9.1Mtrs PSCC Pole 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Elecy | Labour | SWR10112 | 1770 | EA | 28320
5 | 5.76 | Fabrication of struc.with power drilling Fabrication & erection of Channels Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elecy | Labour | SWR10868 | 6852 | TO | 39467.52
6 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Supply of Material for 1st coat Al. Painting. | Elecy | Labour | SMR40009 | 2181 | TO | 12562.56
7 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium. Labour for 1st coat Al. Painting. | Elecy | Labour | SWR10877 | 851 | TO | 4901.76
8 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Supply of Material for 2nd coat Al. Painting. | Elecy | Labour | SMR40010 | 1293 | TO | 7447.68
9 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | Elecy | Labour | SWR10879 | 482 | TO | 2776.32
10 | 5.76 | Fabrication & erection of Channels Alligning the Main/Aux. structures. Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication. | Elecy | Labour | SWR10867 | 1470 | TO | 8467.2
11 | 16 | Erection of RS Joist 150 x 150 mm Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation, for RS Joist, Rail poles Supply & Fabrication of bottom plate with 6mm thichness and for Box poles Supply & Fabrication of Top & Bottom plate with 6mm thichness R.S. Joists 150 x 150 mm | Elecy | Labour | SWR10348 | 1952.61 | EA | 31241.76
12 | 17.758 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement Mass concreting of supports incl. cement | Elecy | Labour | SWR10356 | 6579 | M3 | 116829.882
13 | 9.24 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | Elecy | Labour | SWR10862 | 373 | M2 | 3446.52
14 | 16 | Ptg of coping with 2cts white cmnt inclu cement Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | Elecy | Labour | SWR11089 | 48 | EA | 768
15 | 5.063 | LOADING of MS Channel,Angles,Flats&Rods | Elecy | Labour | SWR10206 | 221 | TO | 1118.923
16 | 5.063 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 KM and upto 20 KM | Elecy | Labour | SWR10132 | 412.08 | TO | 2086.361
17 | 5.063 | UNLOADING of MS Channel,Angles,Flats&Rod | Elecy | Labour | SWR10524 | 185 | TO | 936.655
18 | 5.063 | Fabrication of struc.with power drilling Fabrication & erection of Channels Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elecy | Labour | SWR10868 | 6852 | TO | 34691.676
19 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Supply of Material for 1st coat Al. Painting. | Elecy | Labour | SMR40009 | 2181 | TO | 11042.403
20 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium. Labour for 1st coat Al. Painting. | Elecy | Labour | SWR10877 | 851 | TO | 4308.613
21 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Supply of Material for 2nd coat Al. Painting. | Elecy | supply | SMR40010 | 1293 | TO | 6546.459
22 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | Elecy | Labour | SWR10879 | 482 | TO | 2440.366
23 | 5.063 | Fabrication & erection of Channels Alligning the Main/Aux. structures. Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication. | Elecy | Labour | SWR10867 | 1470 | TO | 7442.61
24 | 13 | LOADING of 33 KV AB SWCH Con 400/800 A Loading of 33KV 800 Amps AB Switch | Elecy | Labour | SWR10239 | 126 | EA | 1638
25 | 2 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Transport of Cond Drum,VCBs>10 & <20Km | Elecy | Labour | SWR11861 | 3299.7 | EA | 6599.4
26 | 13 | UNLOADING of 33 KV AB SWCH Con 400/800 A Un loading of 33KV 800 Amps AB Switch | Elecy | Labour | SWR10557 | 79 | EA | 1027
27 | 13 | Erection of 33kv ABSwitch incl earthing Erection of AB Switch and aligment complete Erection of 33 KV AB Switch including alignment and earthing | Elecy | Labour | SWR10392 | 4500 | EA | 58500
28 | 38 | Painting AB switch OP rods with PO red Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elecy | Labour | SWR10881 | 142 | EA | 5396
29 | 38 | AB Switch Coil Earthing GI No. 8 Wire Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Elecy | Labour | SWR12331 | 146.63 | EA | 5571.94
30 | 6 | LOADING of 33/11 KV CTs/ PTs | Elecy | Labour | SWR10200 | 165 | EA | 990
31 | 6 | UNLOADING of 33/11 KV CTs/ PTs | Elecy | supply | SWR10518 | 128 | EA | 768
32 | 2 | Erection of 33kv single phase PT s Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33 KV single phase PTs | Elecy | Labour | SWR10401 | 1079 | SET | 2158
33 | 12 | LOADING of 33 KV10 KA Las Station type | Elecy | supply | SWR10266 | 41 | EA | 492
34 | 12 | UNLOADING of 33 KV10 KA LAs Station type | Elecy | Labour | SWR10584 | 35 | EA | 420
35 | 4 | Erect of 33kv LA stn type incl earthing Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33 KV LAS station/Line type including earthing | Elecy | Labour | SWR10396 | 880 | SET | 3520
36 | 2 | Loading of 33 KV VCBs along with Panel boards | Elecy | supply | SWR10198 | 1024 | EA | 2048
37 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Transport of Cond Drum,VCBs>10 & <20Km | Elecy | Labour | SWR11861 | 3299.7 | EA | 3299.7
38 | 2 | Un loading of 33 KV VCBs along with Panel boards | Elecy | Labour | SWR10516 | 1044.48 | EA | 2088.96
39 | 12.58 | Excavate-Pit for 33KV VCB | Elecy | Labour | SWR23224 | 331 | M3 | 4163.98
40 | 14.52 | Cement concrete with 40MM metal VCB plin Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x 1.8 x 0.75 cum for VCB Plinth | Elecy | Labour | SWR20685 | 5160 | M3 | 74923.2
41 | 2 | Erection of 33kv VCB Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33 KV VCB with Control Panel | Elecy | Labour | SWR10460 | 12500 | EA | 25000
42 | 2 | LOADING of 8 MVA PTR Loading and unloading of PTR on constructed plinth Loading of 8MVA PTR | Elecy | Labour | SWR10613 | 5805.84 | EA | 11611.68
43 | 2 | Transport of 8MVA power transformer Transport of Power transformers (0 to 100 KM) from one place to another place in GHMC Area.(excluding of loading & unloading ) 8MVA power transformer | Elecy | Labour | SWR10854 | 21945 | EA | 43890
44 | 2 | UNLOADING of 8 MVA PTR Loading and unloading of PTR on constructed plinth Unloading of 8MVA PTR | Elecy | Labour | SWR10627 | 5805.84 | EA | 11611.68
45 | 700 | S/o rail poles 90/105lb (250x2N) | Elecy | supply | SMR22718 | 47.27 | KG | 33089
46 | 4 | Erection of Rail Pole 90Lbs Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation, for RS Joist, Rail poles Supply & Fabrication of bottom plate with 6mm thichness and for Box poles Supply & Fabrication of Top & Bottom plate with 6mm thichness Rail pole 90 lbs | Elecy | Labour | SWR10344 | 3510 | EA | 14040
47 | 2 | Erec 33/11 KV, 8 MVA PTR as per Spec Erection of PTR on constructed plinth Erection of 8 MVA PTR. | Elecy | Labour | SWR21321 | 49480.2 | EA | 98960.4
48 | 0.44 | 33KV Bay Extn: S-Zebra Conductor Extention of 33KV Bay at 132/33KV Sub-station Zebra condutor | Elecy | Labour | SMR24910 | 299369 | KM | 131722.36
49 | 30 | S-Tension HW 3Bolt 1Zebra/Pnthr 150mm Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing. | Elecy | supply | SMR11915 | 2055 | SET | 61650
50 | 30 | Supply of I-Bolts Supply of various Clamps Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367- 1961) Supply of I Bolts | Elecy | supply | SMR22473 | 294 | EA | 8820
51 | 45 | Sup T clamp LM6 Al alloy of 12 mm, 800 A Supply of various Clamps Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367- 1961) Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 " to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating . | Elecy | Labour | SMR40011 | 299 | EA | 13455
52 | 6 | Hoisting post ins&hrd wr 1panther 33kv Bus Stringing Hoisting of Insulators and hardware, stretching the conductor and stringing of 33 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 4.5mt) | Elecy | Labour | SWR21240 | 781 | EA | 4686
53 | 218.67 | Stringing of bus with panther conductor Stringing of bus with panther conductor including jumpering etc., complete to all the equipment in SS fixing to all clamps and equipment.(3 Conductors) | Elecy | supply | SWR10404 | 327.68 | M | 71653.7856
54 | 30 | Conn. of equip/bus single zebra/panther Bus Stringing Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | Elecy | Labour | SWR10884 | 224 | EA | 6720
55 | 75 | Labour for Fixing of all types of clamps | Elecy | Labour | SWR10917 | 65 | EA | 4875
56 | 29 | LOADING of RSJoists150 x 150 mm/RailPole | Elecy | Labour | SWR10205 | 176 | EA | 5104
57 | 10.12 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 KM and upto 20 KM | Elecy | Labour | SWR10132 | 412.08 | TO | 4170.2496
58 | 29 | UNLOADING of RSJoists150 x150 mm/RailPol | Elecy | Labour | SWR10523 | 107 | EA | 3103
59 | 29 | EXCAV. OF PIT HARD(2.6" x 2.6" x 6.0") Excavation of pits in hard rock requiring blasting. (other than SS) 9.1Mtrs PSCC Pole 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Elecy | Labour | SWR10112 | 1770 | EA | 51330
60 | 10.12 | Fabrication of struc.with power drilling Fabrication & erection of Channels Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elecy | supply | SWR10868 | 6852 | TO | 69342.24
61 | 10.12 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Supply of Material for 1st coat Al. Painting. | Elecy | Labour | SMR40009 | 2181 | TO | 22071.72
62 | 10.12 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium. Labour for 1st coat Al. Painting. | Elecy | Labour | SWR10877 | 851 | TO | 8612.12
63 | 10.12 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Supply of Material for 2nd coat Al. Painting. | Elecy | Labour | SMR40010 | 1293 | TO | 13085.16
64 | 10.12 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | Elecy | Labour | SWR10879 | 482 | TO | 4877.84
65 | 10.12 | Fabrication & erection of Channels Alligning the Main/Aux. structures. Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication. | Elecy | Labour | SWR10867 | 1470 | TO | 14876.4
66 | 29 | Erection of RS Joist 150 x 150 mm Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation, for RS Joist, Rail poles Supply & Fabrication of bottom plate with 6mm thichness and for Box poles Supply & Fabrication of Top & Bottom plate with 6mm thichness R.S. Joists 150 x 150 mm | Elecy | Labour | SWR10348 | 1952.61 | EA | 56625.69
67 | 32.19 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement Mass concreting of supports incl. cement | Elecy | Labour | SWR10356 | 6579 | M3 | 211778.01
68 | 16.75 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | Elecy | supply | SWR10862 | 373 | M2 | 6247.75
69 | 29 | Ptg of coping with 2cts white cmnt inclu cement Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | Elecy | Labour | SWR11089 | 48 | EA | 1392
70 | 5.588 | LOADING of MS Channel,Angles,Flats&Rods | Elecy | Labour | SWR10206 | 221 | TO | 1234.948
71 | 5.588 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 KM and upto 20 KM | Elecy | Labour | SWR10132 | 412.08 | TO | 2302.703
72 | 5.588 | UNLOADING of MS Channel,Angles,Flats&Rod | Elecy | Labour | SWR10524 | 185 | TO | 1033.78
73 | 5.588 | Fabrication of struc.with power drilling Fabrication & erection of Channels Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elecy | Labour | SWR10868 | 6852 | TO | 38288.976
74 | 5.588 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Supply of Material for 1st coat Al. Painting. | Elecy | Labour | SMR40009 | 2181 | TO | 12187.428
75 | 5.588 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium. Labour for 1st coat Al. Painting. | Elecy | Labour | SWR10877 | 851 | TO | 4755.388
76 | 5.588 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Supply of Material for 2nd coat Al. Painting. | Elecy | Labour | SMR40010 | 1293 | TO | 7225.284
77 | 5.588 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | Elecy | Labour | SWR10879 | 482 | TO | 2693.416
78 | 5.588 | Fabrication & erection of Channels Alligning the Main/Aux. structures. Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication. | Elecy | Labour | SWR10867 | 1470 | TO | 8214.36
79 | 2 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Transport of Cond Drum,VCBs>10 & <20Km | Elecy | Labour | SWR11861 | 3299.7 | EA | 6599.4
80 | 24 | UNLOADING of 11 KV AB SWCH Con 200/400 A | Elecy | Labour | SWR10556 | 80 | EA | 1920
81 | 21 | Ere 11KV 800A double throw AB Switches Erection of AB Switch and aligment complete Erection of 11KV 800A double throw AB Switches | Elecy | Labour | SWR21277 | 3500 | EA | 73500
82 | 3 | Erection of 11kv ABSwitch incl earthing Erection of AB Switch and aligment complete Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Elecy | Labour | SWR10393 | 3200 | EA | 9600
83 | 2 | LOADING of 11 KV CT - PT Sets | Elecy | Labour | SWR10201 | 190 | EA | 380
84 | 2 | UNLOADING of 11 KV CT - PT Sets | Elecy | Labour | SWR10519 | 101 | EA | 202
85 | 2 | Erection of 11kv three phase PT s Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 11 KV three phase PTs | Elecy | supply | SWR10402 | 800 | SET | 1600
86 | 30 | LOADING of 11 KV,10 KA Las Station type | Elecy | Labour | SWR10264 | 32 | EA | 960
87 | 30 | UNLOADING of 11 KV,10 KA LAs Station typ | Elecy | Labour | SWR10582 | 32 | EA | 960
88 | 2 | Erect of 11kv LA stn type incl earthing Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 11 KV LAS station type including earthing | Elecy | Labour | SWR10397 | 559 | SET | 1118
89 | 8 | Erect of 11kvLA line type incl earthing Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 11 KV LAS line type including earthing | Elecy | Labour | SWR10398 | 505 | SET | 4040
90 | 10 | Loading of 11 KV VCBs along with Panel boards | Elecy | supply | SWR10199 | 1024 | EA | 10240
91 | 5 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Transport of Cond Drum,VCBs>10 & <20Km | Elecy | Labour | SWR11861 | 3299.7 | EA | 16498.5
92 | 10 | Un loading of 11 KV VCBs along with Panel boards | Elecy | Labour | SWR10517 | 1044.48 | EA | 10444.8
93 | 52 | Excavate-Pit for 33KV VCB | Elecy | Labour | SWR23224 | 331 | M3 | 17212
94 | 60 | Cement concrete with 40MM metal VCB plin Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x 1.8 x 0.75 cum for VCB Plinth | Elecy | Labour | SWR20685 | 5160 | M3 | 309600
95 | 10 | Erection of 11kv VCB Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 11 KV VCB with Control Panel | Elecy | Labour | SWR10461 | 12000 | EA | 120000
96 | 12 | S-Tension HW 3Bolt 1Zebra/Pnthr 150mm Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing. | Elecy | supply | SMR11915 | 2055 | SET | 24660
97 | 12 | Supply of I-Bolts Supply of various Clamps Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367- 1961) Supply of I Bolts | Elecy | Labour | SMR22473 | 294 | EA | 3528
98 | 45 | Sup T clamp LM6 Al alloy of 12 mm, 800 A Supply of various Clamps Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367- 1961) Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 " to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating . | Elecy | supply | SMR40011 | 299 | EA | 13455
99 | 2 | Hoisting post ins&hrd wr 1panther 11kv Bus Stringing Hoisting of Insulators and hardware, stretching the conductor and stringing of 11 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 3.5mt) | Elecy | Labour | SWR21241 | 507 | EA | 1014
100 | 45 | Conn. of equip/bus single zebra/panther Bus Stringing Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | Elecy | supply | SWR10884 | 224 | EA | 10080
101 | 57 | Labour for Fixing of all types of clamps | Elecy | supply | SWR10917 | 65 | EA | 3705
102 | 6.27 | LOADING of MS Channel,Angles,Flats&Rods | Elecy | supply | SWR10206 | 221 | TO | 1385.67
103 | 6.27 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 KM and upto 20 KM | Elecy | supply | SWR10132 | 412.08 | TO | 2583.7416
104 | 6.27 | UNLOADING of MS Channel,Angles,Flats&Rod | Elecy | supply | SWR10524 | 185 | TO | 1159.95
105 | 696 | Laying of earth mat,excavation 75x 8mm Laying of earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication. 75x 8mm MS Flat / GI Flat. | Elecy | supply | SWR10920 | 65 | RMT | 45240
106 | 1247 | Earthing for raisers of SS Flat 50x6 mm. Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) | Elecy | supply | SWR10919 | 41 | RMT | 51127
107 | 36 | S-CI Pipe earthing 100mm dia 2.75m long Supply of earthing pipe with materials Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Elecy | supply | SMR11482 | 3486 | EA | 125496
108 | 36 | ERECT. OF LINES-Providing of earthing Providing of Earthing Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elecy | supply | SWR10357 | 1234.2 | EA | 44431.2
109 | 36 | ERECT. OF LINES-Providing of RCC collar Providing of RCC collar to earth pit. Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Elecy | supply | SWR10359 | 386 | EA | 13896
110 | 2 | SupCU Flexi jumper for Power T/F Neutral Supply of Copper Flexible jumper with 75 X 8 of length 250 mm at neutral of Power tranformer end and 50 X 6 of length 50mm two Nos at double neutral end duly brasing with flexible jumper of capacity of 5kA/3 sec for power transformer neutral. | Elecy | supply | SMR40033 | 4725 | EA | 9450
111 | 2 | Provd-Dble Erth with CuJumper incl MSChl Providing of earthing with various types of earth electrodes Providing of double earthing for neutral with flexible copper jumpers including arrangement by fixing M.S.Channel100x50mm. | Elecy | supply | SWR11892 | 1323 | EA | 2646
112 | 4 | Loading of LT AB Cable 3X16+25 Sqmm | Elecy | supply | SWR11702 | 200 | DR | 800
113 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Transport of Cond Drum,VCBs>10 & <20Km | Elecy | supply | SWR11861 | 3299.7 | EA | 3299.7
114 | 4 | Un loading of LT AB Cable 3X16+25 Sqmm | Elecy | supply | SWR11713 | 204 | DR | 816
115 | 90 | Providing of control cable trench as per DATA-XII | Elecy | supply | SWR22093 | 3148 | RMT | 283320
116 | 3312 | Lay-4C/10C 2.5Sqmm Control Cable Control Cable Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends . | Elecy | supply | SWR11879 | 27 | M | 89424
117 | 270 | L-Cable Termination to Switchgear Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per specification (including cost of ferrules, lugs and glands) | Elecy | supply | SWR12510 | 27 | EA | 7290
118 | 4 | Supply of FRP PT Marshalling Box Marshalling Box Supply of FRP PT Marshalling Box | Elecy | supply | SMR40048 | 4463 | EA | 17852
119 | 4 | Erection of Marshalling boxes Marshalling Box Erection of Marshalling boxes | Elecy | supply | SWR10940 | 374.85 | EA | 1499.4
120 | 1 | Loading 220 V Battery with Charger | Elecy | supply | SWR11166 | 1612 | SET | 1612
121 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Transport of Cond Drum,VCBs>10 & <20Km | Elecy | supply | SWR11861 | 3299.7 | EA | 3299.7
122 | 1 | Un-loading 220 V Battery with Charger | Elecy | Labour | SWR11147 | 1024 | SET | 1024
123 | 1 | Erect-220V 200Ah ConvtLead AcidBtry Batteries Erection of 220 V, 200 AH battery in complete shape fit for charging . Conventional lead acid | Elecy | Labour | SWR12350 | 7666 | EA | 7666
124 | 1 | Supply of DC Anunc.relay panel 8 feeders Control Panels Supply of DC Annunciation & relay panel for 10 feeder panel including the cost of LED Indiacation lamps, VAA auxilairy relays, Electronic Hooters complete as per specification | Elecy | Labour | SMR40044 | 42500 | EA | 42500
125 | 1 | Supply of AC Supply panel complete Control Panels Supply of AC Supply panel inluding providing of changeover switch, SFU, metering unit, 32 A three phase MCB, 16 A Single phase MCB complete as per specification. | Elecy | Labour | SMR40045 | 42000 | EA | 42000
126 | 8 | Supply 9mtrs tubular poles single way Yard lightning Supply of stepped tubular poles single way made of steel of length 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9 mm, 2.1 mtrs with outer dia 76.1 mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79 kgf as per IS 2713. | Elecy | Labour | SMR40051 | 13913 | EA | 111304
127 | 8 | S-90W LED fixture set Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE / CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA/OSRAM/SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty 90W LED Fixture set | Elecy | Labour | SMR11594 | 8200 | EA | 65600
128 | 8 | Exca Hard pit w/o blast 0.76X0.76X1.83M Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Elecy | Labour | SWR11039 | 928 | EA | 7424
129 | 8 | Errection of tubular poles Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE / CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA/OSRAM/SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty Erection of tubular poles | Elecy | Labour | SWR10955 | 1379 | EA | 11032
130 | 5.27 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement Mass concreting of supports incl. cement | Elecy | Labour | SWR10356 | 6579 | M3 | 34671.33
131 | 8 | Fixing of LED/Metal halide complete. Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE / CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA/OSRAM/SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty Fixing of Metal halide lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5 GI pipe complete. | Elecy | Labour | SWR10956 | 1268 | EA | 10144
132 | 45 | Supply & Spreading of 20mm HBG metal Supply of HBG metal Supply & spreading of 20mm machine crushed metal (HBG) including cost of conveneyance of all materials, labour charges etc complete for finished item of work and directed by the engineer incharge | Elecy | Labour | SWR10860 | 2113 | M3 | 95085
133 | 3 | LOADING of R.S. Joists 175 x 85 mm | Elecy | Labour | SWR10204 | 76 | EA | 228
134 | 0.75 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 KM and upto 20 KM | Elecy | Labour | SWR10132 | 412.08 | TO | 309.06
135 | 3 | UNLOADING of R.S. Joists 175 x 85 mm | Elecy | Labour | SWR10522 | 50 | EA | 150
136 | 2 | Ex of Hard pit w/o blast 0.75X0.9X1.95M Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Elecy | Labour | SWR11040 | 990.68 | EA | 1981.36
137 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Supply of Material for 1st coat Al. Painting. | Elecy | Labour | SMR40009 | 2181 | TO | 1635.75
138 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium. Labour for 1st coat Al. Painting. | Elecy | Labour | SWR10877 | 851 | TO | 638.25
139 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Supply of Material for 2nd coat Al. Painting. | Elecy | Labour | SMR40010 | 1293 | TO | 969.75
140 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | Elecy | Labour | SWR10879 | 482 | TO | 361.5
141 | 1 | Erect-12Meter Box pole Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation, for RS Joist, Rail poles Supply & Fabrication of bottom plate with 6mm thichness and for Box poles Supply & Fabrication of Top & Bottom plate with 6mm thichness Box pole 12 Mtr | Elecy | Labour | SWR11267 | 3901.37 | EA | 3901.37
142 | 1.732 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement Mass concreting of supports incl. cement | Elecy | Labour | SWR10356 | 6579 | M3 | 11394.828
143 | 1.16 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | Elecy | Labour | SWR10862 | 373 | M2 | 432.68
144 | 2 | Ptg of coping with 2cts white cmnt inclu cement Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | Elecy | Labour | SWR11089 | 48 | EA | 96
145 | 1 | Column type DTR Plinth topslab 4'x4'x6" Construction of DTR Plinth RCC Column type DTR Plinth of size 1'X1'X10',topslab 4'x4'x6" & beam size 4'X8'X8" upto 160KVA | Elecy | Labour | SWR21843 | 25967.57 | EA | 25967.57
146 | 1 | LOADING of 50,63,75&100kva DTR | Elecy | Labour | SWR10195 | 350 | EA | 350
147 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Transport of Cond Drum,VCBs>10 & <20Km | Elecy | Labour | SWR11861 | 3299.7 | EA | 3299.7
148 | 1 | UNLOADING of 50,63,75&100kva DTR | Elecy | Labour | SWR10513 | 280 | EA | 280
149 | 1 | E/r 3ph DTR inclu L&Un-L,T&C on plinth Erection of DTR's including loading and Unloading DTR on the Structure/Plinth etc Erection of 3 Phase DTRs 63,75 & 100 KVA | Elecy | Labour | SWR20905 | 1650 | EA | 1650
150 | 1 | LOADING of 11 KV AB SWCH T.T.200/400 A | Elecy | Labour | SWR12406 | 80 | EA | 80
151 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Transport of Cond Drum,VCBs>10 & <20Km | Elecy | Labour | SWR11861 | 3299.7 | EA | 3299.7
152 | 1 | UNLOADING of 11 KV AB SWCH T.T.200/400 A | Elecy | Labour | SWR12425 | 80 | EA | 80
153 | 1 | Erection of 11kv TT type AB switch Erection of AB Switch and aligment complete Erection of 11KV 200A TT type AB Switch including fixing of cross angles and alignment complete | Elecy | Labour | SWR20102 | 1813.49 | EA | 1813.49
154 | 1 | LOADING of 11 KV HG Fuse Sets | Elecy | Labour | SWR10231 | 18 | EA | 18
155 | 1 | UNLOADING of 11 KV HG Fuse Sets | Elecy | Labour | SWR10549 | 18 | EA | 18
156 | 1 | Erect. of 11kv HG Fuseset incl earthing Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 11 KV HG Fuse set including earthing | Elecy | Labour | SWR10395 | 740.52 | SET | 740.52
157 | 40 | Lay-SR 11KV 3x185sqmm UG Cb HG/BC/CC/BT Excavation & laying of UG Cable in Single Run Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road 11KV 3x185 Sqmm Cable | Elecy | Labour | SWR11920 | 465.46 | M | 18618.4
158 | 20 | Raise-SR 11KV 3x185sqmm UG Cb on support Excavation & laying of UG Cable in Single Run Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) 11 KV 3x185 Sqmm Cable | Elecy | Labour | SWR11956 | 126.23 | M | 2524.6
159 | 2 | OD/Idoor end termination 11kv 3x185 xlpe Making of Outdoor/Indoor End Termination Making 11 KV 3x185 Sqmm Cable Out Door/Indoor end termination | Elecy | Labour | SWR10390 | 2370.63 | EA | 4741.26
160 | 1 | Erection of LT distribution box Erection of LT distribution box including laying of LT cable from distribution box to LT OH line and DTR to distribution box including earthing of distribution box and crimping of lugs connecting of jumpers etc | Elecy | Labour | SWR10674 | 1594.67 | EA | 1594.67
161 | 85 | Lay-SR LT 3.5x95sqmm UG Cb HG/BC/CC/BT Excavation & laying of UG Cable in Single Run Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road LT 3 1/2 x 95 Sqmm Cable | Elecy | Labour | SWR11925 | 377.63 | M | 32098.55
162 | 15 | Raise-SR LT 3.5x95sqmm UG Cb on support Excavation & laying of UG Cable in Single Run Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV 1.05Mtrs & 33 KV - 1.20 mtrs. Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) LT 3 1/2 x 95 Sqmm Cable | Elecy | Labour | SWR11961 | 85.43 | M | 1281.45
163 | 2 | OD/Idoor end termination LT 3 1/2 x 185 Making of Outdoor/Indoor End Termination Supply & fixing of Oout Door/Indoor end termination LT 3 1/2 x 185 Sqmm Cable | Elecy | Labour | SWR10765 | 968.9 | EA | 1937.8
164 | 1 | Sup &fix of board ind Switchyard layout Supply and fixing of Substation board of size 3'x2.5' indicating the layout of switchyard | Elecy | Labour | SWR20032 | 1654 | EA | 1654
165 | 1 | Sup& fix safety inst/SS Op. inst board Supply and fixing of safety instructions/Substation operation instruction board | Elecy | Labour | SWR22090 | 2205 | EA | 2205
166 | 750 | Supply,fabricati of 6mm Checkerd plates Control Panels Supplying & fabrication erection of 6mm Checkerd plates as per the field conditions | Elecy | Labour | SWR10873 | 83 | KG | 62250
167 | 1 | Supply of Wall clock standard make T & P Wall clock standard make | Elecy | Labour | SMR40059 | 578 | EA | 578
168 | 1 | S-10ft Aluminium Ladder | Elecy | Labour | SMR12378 | 1654 | EA | 1654
169 | 1 | Sup Alluminium Ladder for indoor works | Elecy | Labour | SMR40062 | 4410 | EA | 4410
170 | 30 | Painting of Name Plates for any equipmen T & P Painting of Name Plates for any equipment | Elecy | Labour | SWR10963 | 122 | EA | 3660
171 | 1 | SupTaparia Tool kit complete as per Spec Supply of Taparia Tool kit of Size 20”x10”x15” with tier arrangements Tool box with locking arrangement & key containing (1) Double Ended fix Spanner sets, (Ribbed) 6 x 7, 8 x 9, 10 x 11, 12 x 13, 14 x 15, 16 x 17, 18 x19, 20 x 22, 21 x 23, 24 x 27, 25 x28, 30 x 32, (2) Double Ended Ring Spanners sets, 6 x 7 , 8 x 9, 10 x 11, 12 x 13, 14 x 15. 16 x 17 , 18 x 19, 20 x 22 , 21 x 23, 24 x 27, 25 x28, 30 x 32 mm, (3) Adjustable Spanner 305 mm length least maximum opening 35mm chrome, (4) Pipe Wrench Length 350 mm 14”, (5) Soft faced Hammer with suitable handle 2 lb, (6) Hacksaw frame with metal handle heavy duty for 12" hacksaw blade with High Speed blade, (7) Insulated Screw drivers Transparent Green Handle Set Length 6”, 8” & 12”, (8) Star Screw Driver Transparent Green Handle Length 6”, (9) Insulated Wire Cutter, (10) Insulated Cutting Plier Length 8” with cable stripper insulated with thick C. A. sleeve confirming to IS: 4378 - 1990, (11) Long Nose Plier insulated with thick C.A. sleeve generally confirming to IS:3552-1989, (12) Tester type screw driver (special with neon bulb) generally confirm to IS: 5579-1985 Grade:II handle yellow/ green colour overall length 130 mm, (13) Insulated Crimping Plier of all Taparia make. | Elecy | Labour | SMR40063 | 4925 | SET | 4925
172 | 1 | Supply of Rechargeable LED torch light. Rechargeable LED torch light of Standard make | Elecy | Labour | SMR40064 | 1733 | EA | 1733
173 | 1 | Sup Steel almarah(61/2 X 3ft) Godrej T & P Steel almarah(61/2 X 3ft) Godrej | Elecy | Labour | SMR40061 | 9818 | EA | 9818
174 | 1 | Supply of Table (3x6ft) Godrej T & P Table (3x6ft) Godrej | Elecy | Labour | SMR40057 | 6050 | EA | 6050
175 | 4 | Supply of S type chairs (Godrej) T & P S type chairs (Godrej) | Elecy | Labour | SMR40058 | 924 | EA | 3696
176 | 1 | Sup Angle racks(18x36.6inches) Godrej T & P Angle racks(18x36.6inches) Godrej | Elecy | Labour | SMR40060 | 1733 | EA | 1733
177 | 1 | Supply of Hack saw (12 inches) T & P Hack saw (12 inches) | Elecy | Labour | SMR40065 | 289 | EA | 289
178 | 4 | Supply of Earth Rods (8ft) Screw & clamp type | Elecy | Labour | SMR40066 | 578 | EA | 2312
179 | 2 | Supply of Hand Gloves | Elecy | Labour | SMR40067 | 289 | SET | 578
180 | 12 | Supply of Rubber mats( 6#x3#)size for indoorSS | Elecy | Labour | SMR40068 | 1386 | EA | 16632
181 | 1 | Supply of Stand basic cell phone with charger Biometric Time attendence System & Telecom Standard basic cell phone with charger | Elecy | Labour | SMR40069 | 1386 | EA | 1386
182 | 14 | Supply of Danger boards with clamps | Elecy | Labour | SMR40070 | 116 | EA | 1624
183 | 2 | Sup Fire Buckets Stand with Buckets Supply of Materials Fire bucket stand with 3 buckets (8 -10 ltr capacity) | Elecy | Labour | SMR40088 | 1386 | SET | 2772
184 | 2 | Supply of Fire Extinguisher for Control Room Room fire extinguisher (2 ltrs capacity) for control room | Elecy | Labour | SMR40089 | 4620 | EA | 9240
185 | 4 | Sup TrollyMounted Co2 Cylinders(IS-2878) (6.5Kgs)) | Elecy | Labour | SMR40087 | 9240 | EA | 36960
186 | 6 | Supply of Safety Helmet of standard make | Elecy | Labour | SMR40071 | 231 | EA | 1386
187 | 8 | Supply of LC Boards | Elecy | Labour | SMR40072 | 116 | EA | 928
188 | 4 | Supply of Gum Boots | Elecy | Labour | SMR40073 | 693 | EA | 2772
189 | 1 | Supply of 5000v megger | Elecy | Labour | SMR40074 | 13860 | EA | 13860
190 | 1 | Supply of Earth megger (1000v) | Elecy | Labour | SMR40075 | 8085 | EA | 8085
191 | 1 | Supply of Digital clamp meter. | Elecy | Labour | SMR40076 | 2888 | EA | 2888
192 | 1 | Sup 33/11kv S.S Permanent name board Name board of the 33/11kV Sub-Station(As per Standard Specification) | Elecy | Labour | SMR40086 | 10238 | EA | 10238
193 | 800 | S-Hot dip gal./Zinc bolts & nuts washer Supply of Hot dip galvanized/zinc coated bolts & nuts including spring washers, pack washers and flat washers etc. | Elecy | Labour | SMR12488 | 90 | KG | 72000
194 | 4 | LOADING of R.S. Joists 175 x 85 mm | Elecy | Labour | SWR10204 | 76 | EA | 304
195 | 1 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 KM and upto 20 KM | Elecy | Labour | SWR10132 | 412.08 | TO | 412.08
196 | 4 | UNLOADING of R.S. Joists 175 x 85 mm | Elecy | Labour | SWR10522 | 50 | EA | 200
197 | 4 | Exca Hard pit w/o blast 0.76X0.76X1.83M Excavation of pits in hard rock not requiring blasting. (In hard murram / rockboulders) 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Elecy | Labour | SWR11039 | 928 | EA | 3712
198 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Supply of Material for 1st coat Al. Painting. | Elecy | Labour | SMR40009 | 2181 | TO | 2181
199 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium. Labour for 1st coat Al. Painting. | Elecy | Labour | SWR10877 | 851 | TO | 851
200 | 1 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Supply of Material for 2nd coat Al. Painting. | Elecy | Labour | SMR40010 | 1293 | TO | 1293
201 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | Elecy | Labour | SWR10879 | 482 | TO | 482
202 | 3.51 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement Mass concreting of supports incl. cement | Elecy | Labour | SWR10356 | 6579 | M3 | 23092.29
203 | 2.31 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | Elecy | Labour | SWR10862 | 373 | M2 | 861.63
204 | 4 | Ptg of coping with 2cts white cmnt inclu cement Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | Elecy | Labour | SWR11089 | 48 | EA | 192
205 | 5 | Erection of RS Joist 175 x 85 mm Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation, for RS Joist, Rail poles Supply & Fabrication of bottom plate with 6mm thichness and for Box poles Supply & Fabrication of Top & Bottom plate with 6mm thichness RS Joists 150x75/175 x 85 mm | Elecy | Labour | SWR10346 | 1934 | EA | 9670
206 | 24 | LOADING of 11 KV AB SWCH Con 200/400 A | Elecy | Labour | SWR10238 | 80 | EA | 1920
207 | 3 | Supply of 33KV TC Structure as per DATA-II | Elecy | Supply | SMR40102 | 50703 | EA | 152109
208 | 5 | Supply of 33KV BD Boom as per DATA-IV | Elecy | Supply | SMR40104 | 18244 | EA | 91220
209 | 3 | Erection of 33KV TC Structure as per DATA-II | Elecy | Labour | SWR11010 | 17393.04 | EA | 52179.12
210 | 5 | Erection of 33KV BD Boom as per DATA-IV | Elecy | Labour | SWR10875 | 505 | EA | 2525
211 | 1 | Loading of 33 KV VCBs along with Panel boards | Elecy | Labour | SWR10198 | 1024 | EA | 1024
212 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Transport of Cond Drum,VCBs>10 & <20Km | Elecy | Labour | SWR11861 | 3299.7 | EA | 3299.7
213 | 1 | UNLOADING of 33 KV VCBs&Panel boards | Elecy | Labour | SWR10516 | 1044.48 | EA | 1044.48
214 | 1 | Erection of 33kv VCB Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33 KV VCB with Control Panel | Elecy | Labour | SWR10460 | 12500 | EA | 12500
215 | 0.78 | LOADING of MS Channel,Angles,Flats&Rods | Elecy | Labour | SWR10206 | 221 | TO | 172.38
216 | 0.78 | UNLOADING of MS Channel,Angles,Flats&Rod | Elecy | Labour | SWR10524 | 185 | TO | 144.3
217 | 0.78 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 KM and upto 20 KM | Elecy | Labour | SWR10132 | 412.08 | TO | 321.4224
218 | 0.38 | Fabrication & erection of Channels Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to theRSupply of Joist poles excluding cost of Mild Steel and transportcharges to substation site, including erection. Fabrication of struc.with welding. | Elecy | Labour | SWR10869 | 3426 | TO | 1301.88
219 | 0.38 | Fabrication & erection of Channels Alligning the Main/Aux. structures. Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication. | Elecy | Labour | SWR10867 | 1470 | TO | 558.6
220 | 0.38 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Supply of Material for 1st coat Al. Painting. | Elecy | Supply | SMR40009 | 2181 | TO | 828.78
221 | 0.38 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium. Labour for 1st coat Al. Painting. | Elecy | Labour | SWR10877 | 851 | TO | 323.38
222 | 0.38 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Supply of Material for 2nd coat Al. Painting. | Elecy | Supply | SMR40010 | 1293 | TO | 491.34
223 | 0.38 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | Elecy | Labour | SWR10879 | 482 | TO | 183.16
224 | 1 | Erection of 33kv CT s | Elecy | Labour | SWR10399 | 1079 | SET | 1079
225 | 1 | Supply & Erection of 33KV 1200A Isolator incl. Solid Core | Elecy | Labour | SWR12375 | 65800 | EA | 65800
226 | 2 | LOADING of 33 KV AB SWCH Con 400/800 A | Elecy | Labour | SWR10239 | 126 | EA | 252
227 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Transport of Cond Drum,VCBs>10 & <20Km | Elecy | Labour | SWR11861 | 3299.7 | EA | 3299.7
228 | 2 | UNLOADING of 33 KV AB SWCH Con 400/800 A | Elecy | Labour | SWR10557 | 79 | EA | 158
229 | 2 | Erection of 33kv ABSwitch incl earthing Erection of AB Switch and aligment complete Erection of 33 KV AB Switch including alignment and earthing | Elecy | Labour | SWR10392 | 4500 | EA | 9000
230 | 2 | Painting AB switch OP rods with PO red Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elecy | Labour | SWR10881 | 142 | EA | 284
231 | 2 | AB Switch Coil Earthing GI No. 8 Wire Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Elecy | Labour | SWR12331 | 146.63 | EA | 293.26
232 | 3 | LOADING of 33 KV10 KA Las Station type | Elecy | Labour | SWR10266 | 41 | EA | 123
233 | 3 | UNLOADING of 33 KV10 KA LAs Station type | Elecy | Labour | SWR10584 | 35 | EA | 105
234 | 1 | Erect of 33kv LA stn type incl earthing Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33 KV LAS station/Line type including earthing | Elecy | Labour | SWR10396 | 880 | SET | 880
235 | 2.52 | 33KV Bay Extn: Supply of GI Flat 100x16mm Extention of 33KV Bay at 132/33KV Sub-station GI Flat 100X16 | Elecy | Supply | SMR24915 | 63235 | TO | 159352.2
236 | 200 | Laying of MS/GI 100x16mm earth flat Laying of earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication. 100x16mm M.S./G.I earth flat | Elecy | Labour | SWR22054 | 65 | RMT | 13000
237 | 85.1 | Earthing for raisers of SS Flat 75x8 mm. Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. M.S./ G.I. Flat 75x8mm / 75 x 12 mm | Elecy | Labour | SWR10918 | 50 | RMT | 4255
238 | 6 | Providing of earthing with various types of earth electrodes Supply&Erec of CI earth Pipe as APTRANCO Excavation of earth pit, supply of cast iron pipe with flange on one end (as per ISS7181/86) of nominal dia 125mm and 2.75 meters long in side the pit including supply and fixing RCC collars 0.75 meter dia (OD), 50mm thick and 0.60meters long complete as per APTRANSCO standards | Elecy | Labour | SWR10924 | 9804 | EA | 58824
239 | 1 | Loading of 11KV 3 Way RMU/Twin feeder panel LOADING of 11KV 3 Way RMU | Elecy | Labour | SWR10615 | 907.8 | EA | 907.8
240 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Transport of Cond Drum,VCBs>10 & <20Km | Elecy | Labour | SWR11861 | 3299.7 | EA | 3299.7
241 | 1 | UNLOADING of 11KV 3 Way RMU | Elecy | Labour | SWR10629 | 907.8 | EA | 907.8
242 | 1 | Control Panels Erection of 33kV Twin feeder C&R panel. Erection of 33kV Twin feeder control & Relay panel in the control room duly mounting them on channels and grouting them with foundation bolts excluding cost of channels & foundation bolts | Elecy | Labour | SWR10934 | 1729 | EA | 1729
243 | 0.24 | Supply of Moose Conductor | Elecy | Supply | SMR23225 | 375155 | KM | 90037.2
244 | 1 | Bus Stringing Hoisting of Insl. 2 Zebra/Phanther 33kV Hoisting of Insulators and hardware, stretching the conductor and stringing of 33 kV bus comprising of three phases with Twin Moose/ Zebra/Panther conductor to a tension of 900kgs including fixing of spacer clamps.(Bus section of 4.5mt) | Elecy | Labour | SWR10882 | 1302 | EA | 1302
245 | 12 | Supply of Spacer Clamp 150mm Spacing Twin Moose | Elecy | Supply | SMR25240 | 294 | EA | 3528
246 | 18 | Supply of T-Clamp Twin to Sngle Moose 150mmSpace | Elecy | Supply | SMR25242 | 694 | EA | 12492
247 | 3 | Supply of LA clamps for single zebra / Panther Supply of Alluminum LA clamps conforming to A6 of IS 617, with hot dip galvanised bolts and nuts suitable for single zebra / Panther | Elecy | Supply | SMR40027 | 357 | EA | 1071
248 | 100 | L-Cable Termination to Switchgear Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per specification (including cost of ferrules, lugs and glands) | Elecy | Labour | SWR12510 | 27 | EA | 2700
249 | 40 | Providing of control cable trench as per DATA-XII | Elecy | Labour | SWR22093 | 3148 | RMT | 125920
250 | 1800 | Lay-4C/10C 2.5Sqmm Control Cable Control Cable Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends . | Elecy | Labour | SWR11879 | 27 | M | 48600
251 | 1 | Supply of MS Powder coated CT Marshalling Box | Elecy | Supply | SMR40047 | 3675 | EA | 3675
252 | 1 | Erection of Marshalling boxes | Elecy | Labour | SWR10940 | 374.85 | EA | 374.85
253 | 2 | Yard lightning Supply of stepped tubular poles single way made of steel of length 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9 mm, 2.1 mtrs with outer dia 76.1 mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79 kgf as per IS 2713 Supply 9mtrs tubular poles single way | Elecy | Supply | SMR40051 | 13913 | EA | 27826
254 | 2 | Exca Hard pit w/o blast 0.76X0.76X1.83M Excavation of pits in hard rock not requiring blasting. (In hard murram / rockboulders) 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Elecy | Labour | SWR11039 | 928 | EA | 1856
255 | 2 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE /CROMPTON/BAJAJ/VIN/WIPRO /JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA/OSRAM /SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing,toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control ofdistribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Polycarbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty Errection of tubular poles | Elecy | Labour | SWR10955 | 1379 | EA | 2758
256 | 2.1 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement Mass concreting of supports incl. cement | Elecy | Labour | SWR10356 | 6579 | M3 | 13815.9
257 | 2 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE /CROMPTON/BAJAJ/VIN/WIPRO /JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA/OSRAM /SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70%electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Polycarbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty Supply-90W LED fixture set | Elecy | Supply | SMR11594 | 8200 | EA | 16400
258 | 2 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE/CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA/OSRAM/SUMSANG/LG LEDs) makewith minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing,toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty. Fixing of Metal halide lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5 GI pipe complete. Fixing of LED/Metal halide complete. | Elecy | Labour | SWR10956 | 1268 | EA | 2536
259 | 24 | Labour for Fixing of all types of clamps | Elecy | Labour | SWR10917 | 65 | EA | 1560
260 | 60 | Supply & Spreading of 20mm HBG metal Supply & spreading of 20mm machine crushed metal (HBG) including cost of conveneyance of all materials, labour charges etc complete for finished item of work and directed by the engineer incharge | Elecy | Labour | SWR10860 | 2113 | M3 | 126780
261 | 2 | Sup Fire Extinguisher for Control Room Room fire extinguisher (2 ltrs capacity) for control room | Elecy | Supply | SMR40089 | 4620 | EA | 9240
262 | 12 | S&Filling with Borrowed Stone Dust Filling with stone dust in basement with 150mm thick layers incldg cost & conveyance all materials watering,consolidation etc complete for finished item of work. | Elecy | Labour | SWR33054 | 1451 | M3 | 17412
263 | 10.8 | Excavation in Ordinary Soil Earth work excavation in all type of soils red earth, Hard gravelly soils, earth mixed with sand and sandy soils etc., in all conditions such as slushy and dry with initial leads and lifts for foundations. | Elecy | Labour | SWR33015 | 513 | M3 | 5540.4
264 | 2.7 | PCC with 40mm Metal (1:4:8) PCC (1:4:8) using 40 mm metal with concrete Mixture. All work upto Plinth level including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete as directed by Engineer incharge of the work | Elecy | Labour | SWR33028 | 5556 | M3 | 15001.2
265 | 16.2 | CRS Masonary CM(1:6) 2nd Sort C.R.S Masonry in C.M(1:6) using HBG stone including cost & conveyance of all materials labour charges,curing,all leads lifts etc., complete for finished item of work. | Elecy | Labour | SWR33041 | 5829 | M3 | 94429.8
266 | 63 | Plastering 20mm (16mm+4mm)Gfloor Plastering of 20mm thick to all uneven faces of walls of superstructure in two coats with base coat in CM 1:5 of 16mm thick and top coat in CM 1:3 4mm thick with dubara sponge finish including cost and conveyance of all materials, water, all labour charges, curing for specified number of days, cutting grooves, all leads, lifts and scaffolding charges,all incidental charges etc. complete for finished item of work and as directed by the Engineer - in - charge. Ground Floor | Elecy | Labour | SWR33163 | 594 | M2 | 37422
267 | 6 | S&F-15mm Bib Tap 300gm Qtr turn Supply & Fixing 15mm bip tap Indian make 300 grams seilo/senior/nice or equivalent | Elecy | Labour | SWR34330 | 690 | EA | 4140
268 | 40 | S&F 22.20mm OD CPVC Pipe-SDR 11 Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-22.20mm OD Pipe - SDR 11 | Elecy | Labour | SWR34362 | 459 | M | 18360
269 | 12 | Painting of poles Painting of feeder name on support including cost of paint | Elecy | Labour | SWR12101 | 53 | EA | 636
270 | 100 | S-GI Bolts & Nuts,Washers etc., Supply of earthing pipe with materials Supply of GI Bolts & Nuts etc | Elecy | Supply | SMR11488 | 117.5 | KG | 11750
271 | 4.9 | Excavation in Ordinary Soil Earth work excavation in all type of soils red earth, Hard gravelly soils, earth mixed with sand and sandy soils etc., in all conditions such as slushy and dry with initial leads and lifts for foundations. | Elecy | Labour | SWR33015 | 513 | M3 | 2513.7
272 | 0.31 | PCC with 40mm Metal (1:4:8) PCC (1:4:8) using 40 mm metal with concrete Mixture. All work upto Plinth level including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete as directed by Engineer incharge of the work | Elecy | Labour | SWR33028 | 5556 | M3 | 1722.36
273 | 0.56 | RCC Footing: M20Gr, Steel Centering RCC M - 20 Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including all operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete but excluding cost of steel and its fabrication charges for finished item of work - Footing | Elecy | Labour | SWR33098 | 10503 | M3 | 5881.68
274 | 2.03 | RCC Column GF: M20Gr, Steel Centering RCC M - 20 Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including all operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete but excluding cost of steel and its fabrication charges for finished item of work - Column Ground floor | Elecy | Labour | SWR33100 | 14493 | M3 | 29420.79
275 | 0.1 | Reinforcement Steel Fe 415/500 Providing High Yield Strength Deformed (HYSD)/ Thermo Mechanically Treated (TMT) / Mild steel (MS) steel bars (Fe 415/ Fe 500 grade as per IS 1786-1979) of different diameters for RCC works , including labour charges for straightening, cutting, bending to required sizes and shapes, placing in position with cover blocks of approved materials and size and tying and lap-splicing with binding wire of 18 SWG, forming grills for reinforcement work as per approved designs and drawings, including cost and conveyance of steel bars, including all wastages such as overlaps, couplings, chairs, spacer bars including cost and conveyance of binding wire, cover blocks and all incidental, operational, labour charges such as cutting, bending, placing in position, tying excluding taxes on all materials etc., complete for finished item of work in all floors.( APSS No.126) | Elecy | Labour | SWR33144 | 79136 | TON | 7913.6
276 | 0.5 | S&F Structural Steel Angles etc. S&F of Structural steel of Angles,Channels,Beams etc including fabrication & erection, all incidental, operational, labour charges such as cutting, bending, placing in position, excluding taxes complete for finished item of work. | Elecy | Labour | SWR33145 | 129 | KG | 64.5
277 | 1.31 | Seigniorage Charges - Sand | Elecy | Labour | SWR34470 | 40 | M3 | 52.4
278 | 2.67 | Seigniorage Charges - Metal | Elecy | Labour | SWR34471 | 97.5 | M3 | 260.325
279 | 8.02 | survey line&cabl inc peg mark&tree clear | Elecy | Labour | SWR22092 | 765 | KM | 6135.3
280 | 67 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Elecy | Labour | SWR11230 | 1024 | DR | 68608
281 | 34 | Transport of Cond Drum,VCBs upto 10Km Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, Battery Chargers with Batteries, RMU, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Upto 10 Km with Lorry for each trip | Elecy | Labour | SWR11860 | 2720.34 | EA | 92491.56
282 | 67 | Un loading of 11KV/33KV XLPE UG Cable for all sizes | Elecy | Labour | SWR11231 | 1024 | DR | 68608
283 | 100 | Lay-DR 33KV 3x400sqmm UG Cb HG/BC/CC/BT Excavation & laying of UG Cable (Double Run) Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV- In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil/CC 33 KV 3x400 Sqmm Cable | Elecy | Labour | SWR11972 | 749 | M | 74900
284 | 100 | Laying of 2nd Cable in Excavated Trench | Elecy | Labour | SWR10988 | 204.1 | M | 20410
285 | 30 | Raise-DR 33KV 3x400sqmm UG Cb on support Excavation & laying of UG Cable (Double Run) Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV- Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) 33 KV 3x400 Sqmm Cable | Elecy | Labour | SWR12004 | 323.85 | M | 9715.5
286 | 4 | OD/Idoor end termination 33kv 3x400 xlpe Making of Outdoor/Indoor End Termination Making 33 KV 3x400 Sqmm Cable Out Door/Indoor end termination | Elecy | Labour | SWR10387 | 2764.76 | EA | 11059.04
287 | 2 | Straight through joint 33kv 3x400 xlpe Making of Straight through joints 33 KV 3x400 Sqmm Cable | Elecy | Labour | SWR10382 | 5700.78 | EA | 11401.56
288 | 24 | Supply of 33KV 1x630Sqmm OD Unit End Termination | Elecy | Labour | SMR12474 | 4200 | EA | 100800
289 | 24 | Install-33KV 1x630Sqmm OD Unit End Termination | Elecy | Labour | SWR12474 | 4000 | EA | 96000
290 | 2 | Supply&Erec of CI earth Pipe as APTRANCO Providing of earthing with various types of earth electrodes Excavation of earth pit, supply of cast iron pipe with flange on one end (as per ISS7181/86) of nominal dia 125mm and 2.75 meters long in side the pit including supply and fixing RCC collars 0.75 meter dia (OD), 50mm thick and 0.60meters long complete as per APTRANSCO standards | Elecy | Supply | SWR10924 | 9804 | EA | 19608
291 | 1800 | Lay-4 SC 33KV 630sqmm UG Cb HG/BC/RE/NS 33KV 1-Core Cable Laying of 4No's single core 630(Alluminium)/400(Copper) sqmm UG cable (Single Circuit with one spare cable) including excavation of trench of size 0.7 Mtrs width and 1.2 Mtrs depth from road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil | Elecy | Supply | SWR12110 | 2463.3 | M | 4433940
292 | 6120 | Lay-4 SC 33KV 630sqmm UG Cb HG/BC/RE/NS 33KV 1-Core Cable Laying of 4No's single core 630(Alluminium)/400(Copper) sqmm UG cable (Single Circuit with one spare cable) including excavation of trench of size 0.7 Mtrs width and 1.2 Mtrs depth from road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc. Along the CC / BT multi layer road requiring compressor | Elecy | Supply | SWR12111 | 2912.1 | M | 17822052
293 | 160 | Raise-SR 33KV 1x630sqmm UG Cb on Support ACSS Dog HTLS Conductor Raising of Single Run 33KV 1x630sqmm UG Cable on Support | Elecy | Labour | SWR12448 | 133 | M | 21280
294 | 720 | HDD cable with HDPE pipe in Hard rock HDD (Horizontal Directional Drilling) in normal soil Laying of 33&11KV UG cable by HDD method with casing HDPE pipe of 160mm PN4 PE 80 as per IS4984 | Elecy | Labour | SWR11001 | 6993 | M | 5034960
295 | 68 | S-33KV 1x630sqmm Ray Fit Joint ACSS Dog HTLS Conductor Supply of 33KV 1x630sqmm Ray Fit Joint | Elecy | Labour | SMR12379 | 26500 | EA | 1802000
296 | 68 | Providing of Single Core straight though Joint | Elecy | Labour | SWR12264 | 3403 | EA | 231404
297 | 20 | S-6" B Class GI pipe 5mm thck 20Kg/M Cost of Pipes and slabs Supply of 6" B class GI pipe 150 NB GI Pipe 4.85 mm thickness, 19.2 KG/Mtr | Elecy | Supply | SMR40081 | 1344 | M | 26880
298 | 1248 | S-4" BClass GI pipe 3.65mm thck 12.2Kg/M Cost of Pipes and slabs Supply of 4" B Class GI Pipe 100 NB GI Pipe 4.50 mm thickness, 12.1 KG/Mtr | Elecy | Supply | SMR40080 | 800 | M | 998400
299 | 800 | Supply of 250 mm Hume pipe of class NP3 Cost of Pipes and slabs Supply of 250 mm Hume pipe of class NP3 with compresive strength of 35N/mm2 for 28 days curing,barewall thickness of 30mm,1.25kG linear/meter and withstanding capability of 22.50KN/linear meter as per IS 458-1993. | Elecy | Labour | SMR40077 | 363 | M | 290400
300 | 1.2 | LOADING of MS Channel,Angles,Flats&Rods | Elecy | Labour | SWR10206 | 221 | TO | 265.2
301 | 1.2 | UNLOADING of MS Channel,Angles,Flats&Rod | Elecy | Labour | SWR10524 | 185 | TO | 222
302 | 16 | LOADING of R.S. Joists 175 x 85 mm | Elecy | Labour | SWR10204 | 76 | EA | 1216
303 | 5.2 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 KM and upto 20 KM | Elecy | Labour | SWR10132 | 412.08 | TO | 2142.816
304 | 16 | UNLOADING of R.S. Joists 175 x 85 mm | Elecy | Labour | SWR10522 | 50 | EA | 800
305 | 16 | Fabricate&Paint- 175x85/150x75mm RS Joist Fabrication of poles: Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable, Painting of RS Joist on inner phasing with red Oxide before Joining as box pole | Elecy | Labour | SWR10642 | 512.55 | EA | 8200.8
306 | 8 | EXCAV OF PIT HARD 0.75 Mx0.9 Mx1.95 M Excavation of pits in hard rock requiring blasting. (other than SS) 11Mtrs PSCC Pole/ Box poles 0.75 M x 0.9 M x 1.95 M | Elecy | Labour | SWR10113 | 1326 | EA | 10608
307 | 4 | Erection of 9/10/11Meter Box pole Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation, for RS Joist, Rail poles Supply & Fabrication of bottom plate with 6mm thichness and for Box poles Supply & Fabrication of Top & Bottom plate with 6mm thichness Box pole 9/10/11 Mtr | Elecy | Labour | SWR11266 | 2643.83 | EA | 10575.32
308 | 10.48 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement Mass concreting of supports incl. cement | Elecy | Labour | SWR10356 | 6579 | M3 | 68947.92
309 | 0.248 | Coping & Muffing-Iron Pole Mass Concreting for pole Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Elecy | Labour | SWR11890 | 3892.98 | M3 | 965.459
310 | 4 | S-GI pipe earthing 40mm dia 2m long Supply of earthing pipe with materials Supply of GI eath pipe with 40 mm dia,3mm thcikness with 2.0 M Length | Elecy | Labour | SMR11480 | 698 | EA | 2792
311 | 4 | S-CI Pipe earthing 80mm dia 2.75m long Supply of earthing pipe with materials Supply of CI eath pipe with 80mm dia,2.0 M Length | Elecy | Labour | SMR11483 | 2789 | EA | 11156
312 | 8 | ERECT. OF LINES-Providing of earthing Providing of Earthing Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elecy | Labour | SWR10357 | 1234.2 | EA | 9873.6
313 | 8 | ERECT. OF LINES-Providing of RCC collar Providing of RCC collar to earth pit. Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Elecy | Labour | SWR10359 | 386 | EA | 3088
314 | 8 | Painting of poles Painting of feeder name on support including cost of paint | Elecy | Labour | SWR12101 | 53 | EA | 424
315 | 100 | S-GI Bolts & Nuts,Washers etc., Supply of earthing pipe with materials Supply of GI Bolts & Nuts etc | Elecy | Labour | SMR11488 | 117.5 | KG | 11750
316 | 4.7 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Supply of Material for 1st coat Al. Painting. | Elecy | Labour | SMR40009 | 2181 | TO | 10250.7
317 | 4.7 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium. Labour for 1st coat Al. Painting. | Elecy | Labour | SWR10877 | 851 | TO | 3999.7
318 | 4.7 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Supply of Material for 2nd coat Al. Painting. | Elecy | Labour | SMR40010 | 1293 | TO | 6077.1
319 | 4.7 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | Elecy | Labour | SWR10879 | 482 | TO | 2265.4
320 | 2 | LOADING of 33 KV AB SWCH Con 400/800 A | Elecy | Labour | SWR10239 | 126 | EA | 252
321 | 2 | UNLOADING of 33 KV AB SWCH Con 400/800 A | Elecy | Labour | SWR10557 | 79 | EA | 158
322 | 2 | Erection of 33kv ABSwitch incl earthing Erection of AB Switch and aligment complete Erection of 33 KV AB Switch including alignment and earthing | Elecy | Labour | SWR10392 | 4500 | EA | 9000
323 | 208.67 | Earthing for raisers of SS Flat 50x6 mm. Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) | Elecy | Supply | SWR10919 | 41 | RMT | 8555.47
324 | 3 | LOADING of 33 KV10 KA Las Station type | Elecy | Supply | SWR10266 | 41 | EA | 123
325 | 3 | UNLOADING of 33 KV10 KA LAs Station type | Elecy | Labour | SWR10584 | 35 | EA | 105
326 | 1 | Erect of 33kv LA stn type incl earthing Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33 KV LAS station/Line type including earthing | Elecy | Labour | SWR10396 | 880 | SET | 880
327 | 2 | Painting AB switch OP rods with PO red Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elecy | Labour | SWR10881 | 142 | EA | 284
328 | 2 | AB Switch Coil Earthing GI No. 8 Wire Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Elecy | Labour | SWR12331 | 146.63 | EA | 293.26
329 | 1 | CAD Drawing per pole upto 10KM Submission of auto CAD Drawing as per pole schedule (Detailed survey and sketch) Up to 10 km | Elecy | Supply | SWR12104 | 6000 | LS | 6000
330 | 81 | Supply & Erection of Smart RFID marker | Elecy | Labour | SWR25089 | 2745 | EA | 222345
331 | 2 | Erect-33KV DP Structure with RS Joist Erection of OH Lines including AB Cable (33KV, 11KV, LT) Assembly and erection of Structure as per specification which includes fixing of top channels and cross bracings, transport of all materials from road side to the location, earthing, back filling with earth ramming etc excluding pit excavation and concreting. 33 KV DP Structure with 175x85/150x75mm RS joist |  |  | SWR11276 | 5670 | EA | 11340
332 | 480 | Lay-DR 11KV 3x300sqmm UG Cb HG/BC/CC/BT Excavation & laying of UG Cable (Double Run) Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV- In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil/CC 11 KV 3x300 Sqmm Cable | Elecy | Labour | SWR11973 | 631.06 | M | 302908.8
333 | 500 | Lay-6R 11KV 3x300sqmm UG Cb HG/BC/CC/BT Excavation & laying of UG Cable (Six Run ) Laying of XLPE UG cable Six Run including excavation of trench of size 1050mm wide to 1200mm wide as per the site conditions and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second,third or more cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil/CC 11 KV 3x300 Sqmm Cable | Elecy | Labour | SWR12066 | 1262.25 | M | 631125
334 | 2750 | Lay-SR 11KV 3x300sqmm UG Cb CC/BT Compsr Excavation & laying of UG Cable in Single Run Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. Along the CC / BT multi layer road requiring compressor 11 KV 3x300 Sqmm Cable | Elecy | Labour | SWR11928 | 1073.94 | M | 2953335
335 | 480 | Lay-TR 11KV 3x300sqmm UG Cb CC/BT Compsr Excavation & laying of UG Cable (Triple Run ) Laying of XLPE UG cable Triple or more Run including excavation of trench of size 1000mm wide to 750mm wide as per the site conditions and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second,third or more cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. Along the CC / BT multi layer road requiring compressor 11 KV 3x300 Sqmm Cable | Elecy | Labour | SWR12020 | 1578.45 | M | 757656
336 | 60 | HDD cable with HDPE pipe in Hard rock HDD (Horizontal Directional Drilling) in normal soil Laying of 33&11KV UG cable by HDD method with casing HDPE pipe of 160mm PN4 PE 80 as per IS4984 | Elecy | Labour | SWR11001 | 6993 | M | 419580
337 | 3940 | Laying of 2nd Cable in Excavated Trench | Elecy | Labour | SWR10988 | 204.1 | M | 804154
338 | 78 | OD/Idoor end termination 11kv 3x300 xlpe Making of Outdoor/Indoor End Termination Making 11 KV 3x300 Sqmm Cable Out Door/Indoor end termination | Elecy | Labour | SWR10391 | 2370.63 | EA | 184909.14
339 | 30 | Straight through joint 11kv 3x300 xlpe Making of Straight through joints 11 KV 3x300 Sqmm Cable | Elecy | Labour | SWR10386 | 3725.45 | EA | 111763.5
340 | 200 | Raise-SR 11KV 3x300sqmm UG Cb on support Excavation & laying of UG Cable in Single Run Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) 11 KV 3x300 Sqmm Cable | Elecy | Supply | SWR11955 | 144.08 | M | 28816
341 | 29 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Elecy | Supply | SWR11230 | 1024 | DR | 29696
342 | 15 | Un loading of 11KV/33KV XLPE UG Cable for all sizes | Elecy | Labour | SWR11231 | 1024 | DR | 15360
343 | 29 | Transport of Cond Drum,VCBs upto 10Km Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, Battery Chargers with Batteries, RMU, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Upto 10 Km with Lorry for each trip | Elecy | Labour | SWR11860 | 2720.34 | EA | 78889.86
344 | 8 | S-GI pipe earthing 40mm dia 2m long Supply of earthing pipe with materials Supply of GI eath pipe with 40 mm dia,3mm thcikness with 2.0 M Length | Elecy | Labour | SMR11480 | 698 | EA | 5584
345 | 18 | S-CI Pipe earthing 100mm dia 2.75m long Supply of earthing pipe with materials Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Elecy | Labour | SMR11482 | 3486 | EA | 62748
346 | 26 | ERECT. OF LINES-Providing of earthing Providing of Earthing Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elecy | Labour | SWR10357 | 1234.2 | EA | 32089.2
347 | 26 | ERECT. OF LINES-Providing of RCC collar Providing of RCC collar to earth pit. Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Elecy | Supply | SWR10359 | 386 | EA | 10036
348 | 224 | S-4" BClass GI pipe 3.65mm thck 12.2Kg/M Cost of Pipes and slabs Supply of 4" B Class GI Pipe 100 NB GI Pipe 4.50 mm thickness, 12.1 KG/Mtr | Elecy | Supply | SMR40080 | 800 | M | 179200
349 | 50 | S-GI Bolts & Nuts,Washers etc., Supply of earthing pipe with materials Supply of GI Bolts & Nuts etc | Elecy | Labour | SMR11488 | 117.5 | KG | 5875
350 | 123 | S-Earthing GI flat 25x3 mm incl material Supply of earthing pipe with materials Supply of GI Flat 25X3 mm | Elecy | Labour | SMR11485 | 105 | KG | 12915
351 | 205 | Run-GI Earth Flat 25x3mm from metallic p Running of GI eartn flat of size 25X3mm from all metallic parts of channels, AB Switch, HG fuse set, DTr neutral and LT Distribution box and inter connection of earth pits etc complete | Elecy | Labour | SWR12125 | 14.03 | M | 2876.15
352 | 32 | Labour for Fixing of all types of clamps | Elecy | Labour | SWR10917 | 65 | EA | 2080
353 | 6 | Loading of 11KV 3 Way RMU/Twin feeder panel | Elecy | Labour | SWR10615 | 907.8 | EA | 5446.8
354 | 6 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Transport of Cond Drum,VCBs>10 & <20Km | Elecy | Labour | SWR11861 | 3299.7 | EA | 19798.2
355 | 6 | Un loading of 11KV 3 Way RMU/Twin feeder panel | Elecy | Labour | SWR10629 | 907.8 | EA | 5446.8
356 | 6 | Erection of 11KV 3 Way RMU | Elecy | Labour | SWR10664 | 2051.48 | EA | 12308.88
357 | 20 | Supply & Erection of Smart RFID marker | Elecy | Supply | SWR25089 | 2745 | EA | 54900
358 | 0.315 | LOADING of MS Channel,Angles,Flats&Rods | Elecy | Labour | SWR10206 | 221.02 | TO | 69.6213
359 | 0.315 | UNLOADING of MS Channel,Angles,Flats&Rod | Elecy | Labour | SWR10524 | 185.02 | TO | 58.2813
360 | 14 | LOADING of R.S. Joists 175 x 85 mm | Elecy | Labour | SWR10204 | 76 | EA | 1064
361 | 3.815 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 KM and upto 20 KM | Elecy | Labour | SWR10132 | 412.08 | TO | 1572.0852
362 | 14 | UNLOADING of R.S. Joists 175 x 85 mm | Elecy | Labour | SWR10522 | 50 | EA | 700
363 | 14 | Fabricate&Paint- 175x85/150x75mm RS Joist Fabrication of poles: Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable, Painting of RS Joist on inner phasing with red Oxide before Joining as box pole | Elecy | Labour | SWR10642 | 512.55 | EA | 7175.7
364 | 7 | EXCAV OF PIT HARD 0.75 Mx0.9 Mx1.95 M Excavation of pits in hard rock requiring blasting. (other than SS) 11Mtrs PSCC Pole/ Box poles 0.75 M x 0.9 M x 1.95 M | Elecy | Labour | SWR10113 | 1326 | EA | 9282
365 | 7 | Erection of 9/10/11Meter Box pole Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation, for RS Joist, Rail poles Supply & Fabrication of bottom plate with 6mm thichness and for Box poles Supply & Fabrication of Top & Bottom plate with 6mm thichness Box pole 9/10/11 Mtr | Elecy | Supply | SWR11266 | 2643.83 | EA | 18506.81
366 | 9.17 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement Mass concreting of supports incl. cement | Elecy | Labour | SWR10356 | 6579 | M3 | 60329.43
367 | 0.248 | Coping & Muffing-Iron Pole Mass Concreting for pole Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Elecy | Labour | SWR11890 | 3892.98 | M3 | 965.459
368 | 7 | S-GI pipe earthing 40mm dia 2m long Supply of earthing pipe with materials Supply of GI eath pipe with 40 mm dia,3mm thcikness with 2.0 M Length | Elecy | Labour | SMR11480 | 698 | EA | 4886
369 | 7 | ERECT. OF LINES-Providing of earthing Providing of Earthing Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elecy | Labour | SWR10357 | 1234.2 | EA | 8639.4
370 | 7 | ERECT. OF LINES-Providing of RCC collar Providing of RCC collar to earth pit. Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Elecy | Labour | SWR10359 | 386 | EA | 2702
371 | 0.315 | Fabrication & erection of Channels Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to theRSupply of Joist poles excluding cost of Mild Steel and transportcharges to substation site, including erection. Fabrication of struc.with welding. | Elecy | Labour | SWR10869 | 3426 | TO | 1079.19
372 | 7 | Loading of 11 KV AB SWCH T.T.200/400 A | Elecy | Labour | SWR12406 | 80 | EA | 560
373 | 7 | UNLOADING of 11 KV AB SWCH T.T.200/400 A | Elecy | Labour | SWR12425 | 80 | EA | 560
374 | 7 | Erection of 11kv ABSwitch incl earthing Erection of AB Switch and aligment complete Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Elecy | Supply | SWR10393 | 3200 | EA | 22400
375 | 6 | Construction of plinth for 3way RMUs etc |  |  | SWR20871 | 6000 | EA | 36000
376 | 40 | Leveliing the site by cutting and levelling with the help of JCB including cost,conveyance of all materials,hire chareges etc complete for finished item of work as directed by Engineer-in-charge. | Civil | Labour | SWR34179 | 2200 | HR | 88000
377 | 68.53 | Earth Work Mass Excavation (hard rock) to a depth as directed, in soils such as hard rock requiring blasting in prohibited area and all conditions such as dry, wet, slurry etc.and in dense or hard soils, disposal and depositing of excavated soil with intial lead of 10 mt and intial lift of 2m or as directed, including cost and conveyance of all materials, ramping and lifting of materials, and labour charges, hire charges of machinery, tools & plants, bailing of water ( either sub soil water, stoMts water, rain water, surface water or of any kind) if any at any stage of work until all works below ground level is finished to the satisfaction ,and from work such as shoring, timbering, strutting with required supports etc. for the work and removal of form work after completion of work etc all complete as directed by the engineer-incharge. | Civil | Labour | SWR33018 | 876 | M3 | 60032.28
378 | 282.85 | Earth work excavation in all type of soils red earth, Hard gravelly soils, earth mixed with sand and sandy soils etc., in all conditions such as slushy and dry with initial leads and lifts for foundations. | Civil | Labour | SWR33015 | 513 | M3 | 145102.05
379 | 57.36 | Plain Cement concrete (1:4:8) using 40mm HBG metal for foundations and leveling course, including cost and conveyance of all materials, labour all leads and lifts, consolidation and all operations, formwork as required, curing, etc. complete for finished item w | Civil | Labour | SWR33028 | 5553 | M3 | 318520.08
380 | 328.12 | Coursed Rubble stone masonry 2nd sort with hard granite stones in cement mortar (1:6) for basement, including cost and conveyance of all materials, labour charges, curing, all leads and lifts, etc, complete for finished item of work. | Civil | Labour | SWR33041 | 5816 | M3 | 1908345.92
381 | 6.44 | RCC M20 Grade footing 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33098 | 10571 | M3 | 68077.24
382 | 5 | RCC M20 Grade Coloumn . 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33100 | 14561 | M3 | 72805
383 | 4.96 | RCC M20 Grade Plinth beams 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33099 | 13666 | M3 | 67783.36
384 | 5.1 | Supplying, Cutting, bending, binding, placing in position and tying reinforcement steel in all heights including cost and conveyance of steel and binding wire etc,. With all leads and lifts, labour charges, etc., complete for finished item of work. | Civil | Labour | SWR33144 | 79136 | MT | 403593.6
385 | 115.45 | Brick masonry in cement mortar (1:6) for superstructure using well burnt country made second class bricks of approved quality including cost and conveyance of all materials curing, scaffolding with all leads and lifts in all heights etc., complete for fin | Civil | Labour | SWR33068 | 8760 | M3 | 1011342
386 | 2.7 | Plain Cement concrete (1:2:4) using 20mm size well graded HBG metal for foundations, including cost, conveyance of all materials,labour all leads and lifts,consolidation and all operations, formwork as required, curing,etc. complete for finished item of work | Civil | Labour | SWR33030 | 7036 | M3 | 18997.2
387 | 1060.14 | Plastering with two coats, 1st coat in cm1:5 16mm thick and 2nd coat in cm 1:4 4mm thick, total 20mm thick for superstructure walls, ceiling, sunshades, Beams, etc., with sponge finishing including cost and conveyance of all materials all leads & lifts e | Civil | Labour | SWR33163 | 593 | M2 | 628663.02
388 | 732.01 | Painting with two coats of ACE paint over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33356 | 222 | M2 | 162506.22
389 | 410.85 | Painting with two coats of Surya Cem paint over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33329 | 88 | M2 | 36154.8
390 | 500 | Manufacturing, Supplying and fixing of MS grill for (Gate and raillings) of approved design as per drawings, including cost and conveyance of all materials, labour charges etc.,complete for finished item of work as directed by the Engineer- in-charge. | Civil | Labour | SWR33145 | 129 | KG | 64500
391 | 3 | Supply and Fixng of MS Name Board including cost & conveyance of all materials,labour charges etc complete for finished item of work. | Civil | Labour | SWR33421 | 4542 | M2 | 13626
392 | 1 | Geophysical Investgation charges for water point by Geologist | Civil | Labour | SWR33608 | 5250 | EA | 5250
393 | 90 | Drill-165mm Bore Well 0 to 90 | Civil | Labour | SWR33609 | 350 | M | 31500
394 | 30 | Drill-165mm Bore Well 90M to 120M | Civil | Labour | SWR34830 | 369 | M | 11070
395 | 30 | Drill-165mm Bore Well 120M to 150M | Civil | Labour | SWR34831 | 394 | M | 11820
396 | 30 | Drill-165mm Bore Well 150M to 180M | Civil | Labour | SWR34832 | 492 | M | 14760
397 | 30 | Drill-165mm Bore Well 180M to 210M | Civil | Labour | SWR34833 | 623 | M | 18690
398 | 30 | Drill-165mm Bore Well 210M to 240M |  |  | SWR34834 | 754 | M | 22620
399 | 30 | Drill-165mm Bore Well 240M to 270M | Civil | Labour | SWR34835 | 918 | M | 27540
400 | 80 | Drill-165mm Bore Well 270M and above | Civil | Labour | SWR34836 | 1082 | M | 86560
401 | 40 | Supply and fixing of 160mm dia PVC casing of A class 6Kg point pressure including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR33611 | 891 | M | 35640
402 | 1 | Supply and erecting, ISI mark submersible 5.0 HP, Single Phase 30 stages pumpset suitable for 106/156mm dia borewell including cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33640 | 56186 | EA | 56186
403 | 290 | Supply and fixing of HDPE pipe 40mm dia of 16Kg/cm2 including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR34410 | 175 | M | 50750
404 | 1 | Supply and erecting D.O.L Starter 415V , Single phase,50Hz with SS enclouserincluding cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33645 | 9900 | EA | 9900
405 | 305 | Supply of 3 Core 2.5 Sqmm Flat Copper cable of ISI for Submersible Motors of makes Finolex / Polycab / Gold Medal / Million / Payal / Sun Light / Power Flex / Fortune Art | Civil | Labour | SWR33641 | 211 | M | 64355
406 | 76 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-28.60mm OD Pipe - SDR 11 | Civil | Labour | SWR34363 | 556 | M | 42256
407 | 36 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type - 25mm NB Size | Civil | Labour | SWR34346 | 466 | EA | 16776
408 | 1005.56 | Supplying and filling the substation site with borrowed gravel, watering, ramming, thoroughly complying with the standard specification. | Civil | Labour | SWR33052 | 651 | M3 | 654619.56
409 | 3.56 | D) RCC M20 Grade Roof Beams landing beam 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33121 | 13625 | M3 | 48505
410 | 0.62 | e)RCC M20 Grade Lintels 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33107 | 14402 | M3 | 8929.24
411 | 2.7 | f) RCC M20 Grade Sunshades 600mm wide and 75mm thick'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33114 | 1506 | M2 | 4066.2
412 | 21.72 | g) RCC M20 Grade Roof Slab for Control Room 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33128 | 13043 | M3 | 283293.96
413 | 85.68 | Providing Structural steel tube box type 60x40x4mm thick including cost and conveyance of all materials, labour charges,curing etc. complete for finished item of work and as directed by the engineer-in-charge. | Civil | Labour | SWR33146 | 148 | KG | 12680.64
414 | 18 | Providing Roofing with Trapezoidal/Galvalume Sheet including cost and conveyance of all materials, labour charges,curing etc. complete for finished item of work and as directed by the engineer-in-charge. | Civil | Labour | SWR33402 | 604 | M2 | 10872
415 | 19.8 | Providing Design R.C. drop wall of 25mm thickness with cm 1:3 and 6mm dia MS bars at 150mm both ways and chicken mesh in two coats 20mm thick each plastering including cost and conveyance of all materials with leads and lifts, scaffolding and curing, labo | Civil | Labour | SWR33203 | 3234 | M2 | 64033.2
416 | 12.24 | Supply and fixing of Ms ornamental safety grill of approved design including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33310 | 2985 | M2 | 36536.4
417 | 9.06 | Supply and fixing of doors with the frames of the door shall be made well seasoned mt wood of cross section 100x75mm. The shutter shall be made isi mark flushed door with decolam sheets pasted on both sides with PVC beading 40mm width all round.Frame shall be painted with two coats of synthetic enamel paint of approved color over one coat of primer over luppum with spary with 3 no 150mm brass hinges 1 no brass door stoper, 1 no 250mm brass aldrops. 2 no 300 mm aluminium tower bolts, 2 no 150mm brass fancy door handlers, 1 no keyless lockset with cp handel. The quoted rate shall include cost and conveyance of the meterials, fixig, labour carges, tools, handles,locking arrangementts and other fixtures & fittings for finished item work as directed by the Engineer - in- charge. | Civil | Labour | SWR33264 | 7415 | M2 | 67179.9
418 | 128.25 | Raised pointing to the exposed surfaces of CRS masonry in cm 1:3 prop. including cost and conveyance of all materials, labour charges, all leads and lifts curing etc, complete for finished item of work. | Civil | Labour | SWR33184 | 131 | M2 | 16800.75
419 | 8.64 | Supplying and fixing Aluminium sliding windows with grill and fixed glass panels using anodised aluminium extruded sections of mat finish for frames and mullions made from approved aluminium sections 62x32x1.2mm at 0.73kg/Rm providing 5mm plain glass fix | Civil | Labour | SWR33277 | 3673 | M2 | 31734.72
420 | 39.19 | Supply and laying of Ceramic floor over of CM 1:3 20 mm thick including required materials and labour charges etc complete for item of work | Civil | Labour | SWR33224 | 950 | M2 | 37230.5
421 | 121.92 | Flooring with double machine polished and hand cut Tandur blue stone 20mm thick of approved colour, quality and of minimum of 300x300mm size over a bed of cement mortar 1:3 20mm thick including cost of all materials, with all leads and lifts jointing and | Civil | Labour | SWR33219 | 677 | M2 | 82539.84
422 | 6.74 | Supply and fixing of 4" high skirting of shabad stone to the walls including cost and conveyance of all materials, labour etc for finished item of work. | Civil | Labour | SWR33236 | 772 | M2 | 5203.28
423 | 243.69 | Painting with two coats of OBD over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials labour charges etc., complete for finished item of work. | Civil | Labour | SWR33333 | 154 | M2 | 37528.26
424 | 167.67 | Providing impervious coat over RCC roof slab to requried slopes with 20mm thick in CM 1:3 mixed with approved brand of water proffing compound inclding cost and conveyance of all materials, labour charges, curing, rounding off junctions of wall and slab, all leads and lifts, etc . complete for finished item of work as directed by the Engineer - in - charge. | Civil | Labour | SWR33156 | 616 | M2 | 103284.72
425 | 81 | Supply & Spreading 40 mm metal for WBM road including cost and convenience of labor charges etc complete finshed item of work | Civil | Labour | SWR33056 | 1741 | M3 | 141021
426 | 35 | Supply and fixing 25mm dia 1.5mm thick recessed( concealed) PVC pipe alog with reinforcement to be laid in slab including No 14 SWG GI wire for earth contunity, cost of pipe, binding wire and all labour charges etc complete | Civil | Labour | SWR33441 | 114 | M | 3990
427 | 15 | Wiring with Modular Switch LP,FP,EFP for NRBuildPVC insulated flexiable copper cable in the existing metalic/Non metalic conduit pipe with 6A mini modular SP switch, mounted on metalic box covereds with appropriate front plate modules etc ceiling rose including cot and conveyance of all mateials, labour charges complete for light points, bell points and fan points in non residential builsing except circuit moving finished in all types masonary as directed by department. | Civil | Labour | SWR33457 | 703 | EA | 10545
428 | 31 | Supply and fixing 32mm dia 2mm thick ( concealed) PVC pipe in the wall including No 14 SWG GI wire for earth contunity, cost of pipe, binding wire and all labour charges etc complete for finished item of work. | Civil | Labour | SWR33442 | 105 | M | 3255
429 | 22 | Supply and fixing of 6A 3/2 pin flush type plug socket with 6A flush type marked switch control on a common board with earth continuity including wire leads earth connections along with all labour charges etc. complete | Civil | Labour | SWR33462 | 333 | EA | 7326
430 | 12 | Supply and fixing of 16A 3pin flush type plug socket and 16A flush type fuse unit and 16A switch control. | Civil | Labour | SWR33464 | 532 | EA | 6384
431 | 8 | Supply and fixing of Batten holders with 100W bulb with all connections and labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Civil | Labour | SWR33484 | 146 | EA | 1168
432 | 12 | Supply and fixing of patty type tube light fitting with 4' 0" - 40W tube light,40W copper choke,starter,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Civil | Labour | SWR33543 | 780 | EA | 9360
433 | 120 | Supply and run of 2 of 22/0.3 (1.5sqmm) pvc insulated flexible copper cable in the existing metalic/non-metalic conduit pipe. | Civil | Labour | SWR33496 | 78 | M | 9360
434 | 180 | Supply and run of 2 of 36/0.3 (2.5sqmm) pvc insulated flexible copper cable in the existing metalic/non-metalic conduit pipe. | Civil | Labour | SWR33497 | 108 | M | 19440
435 | 1 | Providing independent earthing for main switches,IC cutouts and motors using 40mm. Dia. B-class G.I.Pipe of 2.5' length duly providing 12mm. Dia. 6No. Holes and required bolts,nuts and washers,including filling with equal preparation of salt and charcoal in layers and labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Civil | Labour | SWR33596 | 5407 | EA | 5407
436 | 3 | Supply and Fixing of 48" ceiling fan of bajaj make(or equivalent make) including cost material,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Civil | Labour | SWR33563 | 2290 | EA | 6870
437 | 1 | S&F Orissa Pan WC 580mmx440mm of Parry, Neycer or Hindhusthan, make with 'P' or 'S' trap etc complete for finished item of work and as directed by the engineer-in-charge. | Civil | Labour | swr34311 | 2428 | EA | 2428
438 | 1 | Supply and fixing of European Water Closet of first quality conforming IS2556-part-21973 of Parry, Neycer or Hindhusthan, make with 'P' or 'S' trap etc,white glazed complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | swr34314 | 2257 | EA | 2257
439 | 1 | PVC low level system parry ware , slim line with internal components & short ben 10 liters capacity dual flush including cost and conveyance of all materials and labour charges for finished item of work | Civil | Labour | swr34376 | 2048.4 | EA | 2048.4
440 | 2 | Supply and Fixing 4" PVC floor trap including labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Civil | Labour | SWR34386 | 269 | EA | 538
441 | 5 | Supply,fixing 4" dia. PVC Plain Bend including cost etc. complete for finished item of work and as directed by the engineer-in-charge. | Civil | Labour | SWR34380 | 100 | EA | 500
442 | 5 | Supply,fixing 4" dia. PVC Door Bend including cost etc. complete for finished item of work and as directed by the engineer-in-charge. | Civil | Labour | SWR34381 | 128 | EA | 640
443 | 1 | S&Fixing 150mm x 100mm SWG gully traps Ist class grating & constg brick masonry in CM (1:6) prop inter mediate chamber and fitted with CI frame etc complete. | Civil | Labour | SWR34286 | 768.2 | EA | 768.2
444 | 10 | Supply and Fixing 4" dia 3M Single socket PVC pipe including labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Civil | Labour | SWR34377 | 470 | M | 4700
445 | 10 | Supply and Fixing 90mm dia 3M Single socket PVC pipe including labour charges etc. complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR34378 | 418.33 | M | 4183.3
446 | 3 | Supply,laying and jointing 152.4 mm SWG pipe including excavation of trenches etc. complete for finished item of work and as directed by the engineer-in-charge. | Civil | Labour | SWR34284 | 918 | M | 2754
447 | 1 | Constructing 3'x 3' Brick in CM(1:6) prop Masonry inspection chamber and fitted with light weight CI frame and cover etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR34297 | 4610 | EA | 4610
448 | 50 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)- 15.90mm OD Pipe - SDR 11 | Civil | Labour | SWR34361 | 385 | M | 19250
449 | 340 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-22.20mm OD Pipe - SDR 11 | Civil | Labour | SWR34362 | 459 | M | 156060
450 | 50 | Supply and fixing of 15mm dia. GM Ball valve including labour charges complete for finished item of work and as directed by the engineer-in-charge. | Civil | Labour | SWR34344 | 230 | EA | 11500
451 | 5 | Supply and fixing of 20mm dia. GM Ball valve including labour charges complete for finished item of work and as directed by the engineer-in-charge. | Civil | Labour | SWR34345 | 331 | EA | 1655
452 | 5 | Supply and fixing of 12.7mm bib tap Indian make including labour charges complete for finished item of work and as directed by the engineer-in-charge. | Civil | Labour | SWR34329 | 304 | EA | 1520
453 | 10 | Supply and fixing of 12.7mm dia. concealed stop cock including labour charges complete for finished item of work and as directed by the engineer-in-charge. | Civil | Labour | SWR34328 | 730 | EA | 7300
454 | 1000 | Providing and placing on Terrace polyetheylene water storage tank with double layer approved brand and manufacture with cover complete for finished item of work and as directed by the engineer-in-charge. | Civil | Labour | SWR34375 | 10 | L | 10000
455 | 3 | Supply and fixing of Glow sign board of size 10' x 3' including lettering,labour charges,fitting charges complete for finished item of work and as directed by the engineer-in-charge. | Civil | Labour | SWR33422 | 3730 | M2 | 11190
456 | 1 | Providing supply of electricity to the site premises through customer service centre duly applying for new connection including application fee and other missalaneous charges prescribed by APCPDCL complete for the finished item of work. | Civil | Labour | SWR33425 | 5678 | EA | 5678
457 | 2400 | Provd 2Sets of Structural Drawings | Civil | Labour | SWR33426 | 5 | FT2 | 12000
458 | 2 | Providing consultancy services for arranging contour surveying with total station including preparation of boundary and contour levels with 2 No.s hard copies and soft copies complete for finished items of work. | Civil | Labour | SWR33427 | 5850 | EA | 11700
459 | 1 | Supplying & Fixing Indian make Flat Back Wash Hand Basin (HSW/Parryware/ Neycer) 1st quality conforming to IS:2556-Part-4:1972 with waste fittings like rubber plug, chain, 32 mm nominal size C.P. Fitting with parallel pipe thread conforming to IS:2963-1979 and fitted with 15 mm nominal bore Chromium Plated Pillar Tap of 1st quality Indian make 400 grams Seiko/ Senior/ Nice/ Esso or equivalent complete with standard CI brackets including wooden block: 550 x 400 mm - Single C.P. Pillar cock | Civil | Labour | SWR34316 | 1765 | EA | 1765
460 | 6 | Supply & fixing 38.1 mm C.P waste coupling Half or Full Thread 1st Quality Indian make Parryware or equivalent | Civil | Labour | SWR34428 | 318 | EA | 1908
461 | 2 | Supply & fixing of 4" (101.6 mm ) Nahany Trap ( Without Jali with inlet)UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34387 | 134 | EA | 268
462 | 2 | S&F 76.2mm Nahany Trap with Jali | Civil | Labour | SWR34388 | 122 | EA | 244
463 | 1 | SBC Test will be done by OU/JNTU 3Samples including mobilization and Demobilization of drill equipment, lab testing of bore hole samples, preperation of technical report etc., | Civil | Labour | SWR34099 | 46000 | EA | 46000
464 | 1 | Supply & fixing 8wySPNDB IP-42,10kA-6-32A SPMCB 6Nos. MCBs as out going including internal connection and labour charges for surface / flush mounting etc Complete. | Civil | Labour | SWR33523 | 6518 | EA | 6518
465 | 36 | Plain Cement concrete (1:3:6) using 40mm HBG metal for foundations and leveling course, including cost and conveyance of all materials, labour all leads and lifts, consolidation and all operations, formwork as required, curing, etc. complete for finished item w | Civil | Labour | SWR33029 | 5848 | M3 | 210528
466 | 144 | Supply&Fabrication and fixing of Welded wire mesh ( 2" x 2") of 3mm dia. with ISMC (75x40x4.4mm) and Pheriperal frame of ISA(35x35x3mm) incldg cost& conveyance painting with synthetic enamil paint two coats over a coat of red oxide primer etc complete for finished item of work.. | Civil | Labour | SWR33403 | 2451 | M2 | 352944
467 | 591.17 | Seigniorage Charges - Sand | Civil | Labour | SWR34470 | 40 | M3 | 23646.8
468 | 1465.96 | Seigniorage Charges - Metal | Civil | Labour | SWR34471 | 97.5 | M3 | 142931.1
469 | 218.06 | Seigniorage Charges - Gravel | Civil | Labour | SWR34472 | 30 | M3 | 6541.8
|  | Total (Excl.GST.) | [5 empty] | 52162346.306
|  | GST 18% Rs. | [5 empty] | 9389222.3351
Total (Incl.GST) | [7 empty] | 61551568.641

## Sheet1
Schedule for the work of "Erection, testing & commissioning of new 33/11kV outdoor substation with 2x8 MVA PTRs and connected 33kV & 11kV feeders along with Construction of Control room, Compound wall and other civil works at Sy No. 152/P Jawahar nagar colony, Chandanagar (V), Serilingampally (M) in Vemana colony section of Kukatpally division in Medchal operation circle, of Master plan Sub-division 1 of WCGH Division in Rangareddy circle under T&D improvement works."
WBS No. S-1936-13-04-01-01-001
D.No :SAN NO. 31, D. NO. 1414/2025-26, DT: 16.10.2025
S.No | Estimate Quantity(Only Figures) | PARTICULARS | Work Type | Item Short Description | SWR No/APSS/Morth cl.No | Rate (INR) (Upto 2 Decimals) | UOM | Amount
SS labour
1 | 16 | LOADING of RSJoists150 x 150 mm/RailPole | Elecy | Labour | SWR10205 | 176 | EA | 2816
2 | 5.76 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 KM and upto 20 KM | Elecy | Labour | SWR10132 | 412.08 | TO | 2373.5808
3 | 16 | UNLOADING of RSJoists150 x150 mm/RailPol | Elecy | Labour | SWR10523 | 107 | EA | 1712
4 | 16 | EXCAV. OF PIT HARD(2.6" x 2.6" x 6.0") Excavation of pits in hard rock requiring blasting. (other than SS) 9.1Mtrs PSCC Pole 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Elecy | Labour | SWR10112 | 1770 | EA | 28320
5 | 5.76 | Fabrication of struc.with power drilling Fabrication & erection of Channels Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elecy | Labour | SWR10868 | 6852 | TO | 39467.52
6 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Supply of Material for 1st coat Al. Painting. | Elecy | Labour | SMR40009 | 2181 | TO | 12562.56
7 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium. Labour for 1st coat Al. Painting. | Elecy | Labour | SWR10877 | 851 | TO | 4901.76
8 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Supply of Material for 2nd coat Al. Painting. | Elecy | Labour | SMR40010 | 1293 | TO | 7447.68
9 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | Elecy | Labour | SWR10879 | 482 | TO | 2776.32
10 | 5.76 | Fabrication & erection of Channels Alligning the Main/Aux. structures. Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication. | Elecy | Labour | SWR10867 | 1470 | TO | 8467.2
11 | 16 | Erection of RS Joist 150 x 150 mm Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation, for RS Joist, Rail poles Supply & Fabrication of bottom plate with 6mm thichness and for Box poles Supply & Fabrication of Top & Bottom plate with 6mm thichness R.S. Joists 150 x 150 mm | Elecy | Labour | SWR10348 | 1952.61 | EA | 31241.76
12 | 17.758 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement Mass concreting of supports incl. cement | Elecy | Labour | SWR10356 | 6579 | M3 | 116829.882
13 | 9.24 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | Elecy | Labour | SWR10862 | 373 | M2 | 3446.52
14 | 16 | Ptg of coping with 2cts white cmnt inclu cement Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | Elecy | Labour | SWR11089 | 48 | EA | 768
15 | 5.063 | LOADING of MS Channel,Angles,Flats&Rods | Elecy | Labour | SWR10206 | 221 | TO | 1118.923
16 | 5.063 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 KM and upto 20 KM | Elecy | Labour | SWR10132 | 412.08 | TO | 2086.361
17 | 5.063 | UNLOADING of MS Channel,Angles,Flats&Rod | Elecy | Labour | SWR10524 | 185 | TO | 936.655
18 | 5.063 | Fabrication of struc.with power drilling Fabrication & erection of Channels Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elecy | Labour | SWR10868 | 6852 | TO | 34691.676
19 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Supply of Material for 1st coat Al. Painting. | Elecy | Labour | SMR40009 | 2181 | TO | 11042.403
20 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium. Labour for 1st coat Al. Painting. | Elecy | Labour | SWR10877 | 851 | TO | 4308.613
21 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Supply of Material for 2nd coat Al. Painting. | Elecy | supply | SMR40010 | 1293 | TO | 6546.459
22 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | Elecy | Labour | SWR10879 | 482 | TO | 2440.366
23 | 5.063 | Fabrication & erection of Channels Alligning the Main/Aux. structures. Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication. | Elecy | Labour | SWR10867 | 1470 | TO | 7442.61
24 | 13 | LOADING of 33 KV AB SWCH Con 400/800 A Loading of 33KV 800 Amps AB Switch | Elecy | Labour | SWR10239 | 126 | EA | 1638
25 | 2 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Transport of Cond Drum,VCBs>10 & <20Km | Elecy | Labour | SWR11861 | 3299.7 | EA | 6599.4
26 | 13 | UNLOADING of 33 KV AB SWCH Con 400/800 A Un loading of 33KV 800 Amps AB Switch | Elecy | Labour | SWR10557 | 79 | EA | 1027
27 | 13 | Erection of 33kv ABSwitch incl earthing Erection of AB Switch and aligment complete Erection of 33 KV AB Switch including alignment and earthing | Elecy | Labour | SWR10392 | 4500 | EA | 58500
28 | 38 | Painting AB switch OP rods with PO red Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elecy | Labour | SWR10881 | 142 | EA | 5396
29 | 38 | AB Switch Coil Earthing GI No. 8 Wire Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Elecy | Labour | SWR12331 | 146.63 | EA | 5571.94
30 | 6 | LOADING of 33/11 KV CTs/ PTs | Elecy | Labour | SWR10200 | 165 | EA | 990
31 | 6 | UNLOADING of 33/11 KV CTs/ PTs | Elecy | supply | SWR10518 | 128 | EA | 768
32 | 2 | Erection of 33kv single phase PT s Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33 KV single phase PTs | Elecy | Labour | SWR10401 | 1079 | SET | 2158
33 | 12 | LOADING of 33 KV10 KA Las Station type | Elecy | supply | SWR10266 | 41 | EA | 492
34 | 12 | UNLOADING of 33 KV10 KA LAs Station type | Elecy | Labour | SWR10584 | 35 | EA | 420
35 | 4 | Erect of 33kv LA stn type incl earthing Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33 KV LAS station/Line type including earthing | Elecy | Labour | SWR10396 | 880 | SET | 3520
36 | 2 | Loading of 33 KV VCBs along with Panel boards | Elecy | supply | SWR10198 | 1024 | EA | 2048
37 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Transport of Cond Drum,VCBs>10 & <20Km | Elecy | Labour | SWR11861 | 3299.7 | EA | 3299.7
38 | 2 | Un loading of 33 KV VCBs along with Panel boards | Elecy | Labour | SWR10516 | 1044.48 | EA | 2088.96
39 | 12.58 | Excavate-Pit for 33KV VCB | Elecy | Labour | SWR23224 | 331 | M3 | 4163.98
40 | 14.52 | Cement concrete with 40MM metal VCB plin Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x 1.8 x 0.75 cum for VCB Plinth | Elecy | Labour | SWR20685 | 5160 | M3 | 74923.2
41 | 2 | Erection of 33kv VCB Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33 KV VCB with Control Panel | Elecy | Labour | SWR10460 | 12500 | EA | 25000
42 | 2 | LOADING of 8 MVA PTR Loading and unloading of PTR on constructed plinth Loading of 8MVA PTR | Elecy | Labour | SWR10613 | 5805.84 | EA | 11611.68
43 | 2 | Transport of 8MVA power transformer Transport of Power transformers (0 to 100 KM) from one place to another place in GHMC Area.(excluding of loading & unloading ) 8MVA power transformer | Elecy | Labour | SWR10854 | 21945 | EA | 43890
44 | 2 | UNLOADING of 8 MVA PTR Loading and unloading of PTR on constructed plinth Unloading of 8MVA PTR | Elecy | Labour | SWR10627 | 5805.84 | EA | 11611.68
45 | 700 | S/o rail poles 90/105lb (250x2N) | Elecy | supply | SMR22718 | 47.27 | KG | 33089
46 | 4 | Erection of Rail Pole 90Lbs Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation, for RS Joist, Rail poles Supply & Fabrication of bottom plate with 6mm thichness and for Box poles Supply & Fabrication of Top & Bottom plate with 6mm thichness Rail pole 90 lbs | Elecy | Labour | SWR10344 | 3510 | EA | 14040
47 | 2 | Erec 33/11 KV, 8 MVA PTR as per Spec Erection of PTR on constructed plinth Erection of 8 MVA PTR. | Elecy | Labour | SWR21321 | 49480.2 | EA | 98960.4
48 | 0.44 | 33KV Bay Extn: S-Zebra Conductor Extention of 33KV Bay at 132/33KV Sub-station Zebra condutor | Elecy | Labour | SMR24910 | 299369 | KM | 131722.36
49 | 30 | S-Tension HW 3Bolt 1Zebra/Pnthr 150mm Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing. | Elecy | supply | SMR11915 | 2055 | SET | 61650
50 | 30 | Supply of I-Bolts Supply of various Clamps Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367- 1961) Supply of I Bolts | Elecy | supply | SMR22473 | 294 | EA | 8820
51 | 45 | Sup T clamp LM6 Al alloy of 12 mm, 800 A Supply of various Clamps Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367- 1961) Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 " to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating . | Elecy | Labour | SMR40011 | 299 | EA | 13455
52 | 6 | Hoisting post ins&hrd wr 1panther 33kv Bus Stringing Hoisting of Insulators and hardware, stretching the conductor and stringing of 33 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 4.5mt) | Elecy | Labour | SWR21240 | 781 | EA | 4686
53 | 218.67 | Stringing of bus with panther conductor Stringing of bus with panther conductor including jumpering etc., complete to all the equipment in SS fixing to all clamps and equipment.(3 Conductors) | Elecy | supply | SWR10404 | 327.68 | M | 71653.7856
54 | 30 | Conn. of equip/bus single zebra/panther Bus Stringing Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | Elecy | Labour | SWR10884 | 224 | EA | 6720
55 | 75 | Labour for Fixing of all types of clamps | Elecy | Labour | SWR10917 | 65 | EA | 4875
56 | 29 | LOADING of RSJoists150 x 150 mm/RailPole | Elecy | Labour | SWR10205 | 176 | EA | 5104
57 | 10.12 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 KM and upto 20 KM | Elecy | Labour | SWR10132 | 412.08 | TO | 4170.2496
58 | 29 | UNLOADING of RSJoists150 x150 mm/RailPol | Elecy | Labour | SWR10523 | 107 | EA | 3103
59 | 29 | EXCAV. OF PIT HARD(2.6" x 2.6" x 6.0") Excavation of pits in hard rock requiring blasting. (other than SS) 9.1Mtrs PSCC Pole 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Elecy | Labour | SWR10112 | 1770 | EA | 51330
60 | 10.12 | Fabrication of struc.with power drilling Fabrication & erection of Channels Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elecy | supply | SWR10868 | 6852 | TO | 69342.24
61 | 10.12 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Supply of Material for 1st coat Al. Painting. | Elecy | Labour | SMR40009 | 2181 | TO | 22071.72
62 | 10.12 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium. Labour for 1st coat Al. Painting. | Elecy | Labour | SWR10877 | 851 | TO | 8612.12
63 | 10.12 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Supply of Material for 2nd coat Al. Painting. | Elecy | Labour | SMR40010 | 1293 | TO | 13085.16
64 | 10.12 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | Elecy | Labour | SWR10879 | 482 | TO | 4877.84
65 | 10.12 | Fabrication & erection of Channels Alligning the Main/Aux. structures. Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication. | Elecy | Labour | SWR10867 | 1470 | TO | 14876.4
66 | 29 | Erection of RS Joist 150 x 150 mm Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation, for RS Joist, Rail poles Supply & Fabrication of bottom plate with 6mm thichness and for Box poles Supply & Fabrication of Top & Bottom plate with 6mm thichness R.S. Joists 150 x 150 mm | Elecy | Labour | SWR10348 | 1952.61 | EA | 56625.69
67 | 32.19 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement Mass concreting of supports incl. cement | Elecy | Labour | SWR10356 | 6579 | M3 | 211778.01
68 | 16.75 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | Elecy | supply | SWR10862 | 373 | M2 | 6247.75
69 | 29 | Ptg of coping with 2cts white cmnt inclu cement Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | Elecy | Labour | SWR11089 | 48 | EA | 1392
70 | 5.588 | LOADING of MS Channel,Angles,Flats&Rods | Elecy | Labour | SWR10206 | 221 | TO | 1234.948
71 | 5.588 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 KM and upto 20 KM | Elecy | Labour | SWR10132 | 412.08 | TO | 2302.703
72 | 5.588 | UNLOADING of MS Channel,Angles,Flats&Rod | Elecy | Labour | SWR10524 | 185 | TO | 1033.78
73 | 5.588 | Fabrication of struc.with power drilling Fabrication & erection of Channels Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elecy | Labour | SWR10868 | 6852 | TO | 38288.976
74 | 5.588 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Supply of Material for 1st coat Al. Painting. | Elecy | Labour | SMR40009 | 2181 | TO | 12187.428
75 | 5.588 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium. Labour for 1st coat Al. Painting. | Elecy | Labour | SWR10877 | 851 | TO | 4755.388
76 | 5.588 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Supply of Material for 2nd coat Al. Painting. | Elecy | Labour | SMR40010 | 1293 | TO | 7225.284
77 | 5.588 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | Elecy | Labour | SWR10879 | 482 | TO | 2693.416
78 | 5.588 | Fabrication & erection of Channels Alligning the Main/Aux. structures. Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication. | Elecy | Labour | SWR10867 | 1470 | TO | 8214.36
79 | 2 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Transport of Cond Drum,VCBs>10 & <20Km | Elecy | Labour | SWR11861 | 3299.7 | EA | 6599.4
80 | 24 | UNLOADING of 11 KV AB SWCH Con 200/400 A | Elecy | Labour | SWR10556 | 80 | EA | 1920
81 | 21 | Ere 11KV 800A double throw AB Switches Erection of AB Switch and aligment complete Erection of 11KV 800A double throw AB Switches | Elecy | Labour | SWR21277 | 3500 | EA | 73500
82 | 3 | Erection of 11kv ABSwitch incl earthing Erection of AB Switch and aligment complete Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Elecy | Labour | SWR10393 | 3200 | EA | 9600
83 | 2 | LOADING of 11 KV CT - PT Sets | Elecy | Labour | SWR10201 | 190 | EA | 380
84 | 2 | UNLOADING of 11 KV CT - PT Sets | Elecy | Labour | SWR10519 | 101 | EA | 202
85 | 2 | Erection of 11kv three phase PT s Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 11 KV three phase PTs | Elecy | supply | SWR10402 | 800 | SET | 1600
86 | 30 | LOADING of 11 KV,10 KA Las Station type | Elecy | Labour | SWR10264 | 32 | EA | 960
87 | 30 | UNLOADING of 11 KV,10 KA LAs Station typ | Elecy | Labour | SWR10582 | 32 | EA | 960
88 | 2 | Erect of 11kv LA stn type incl earthing Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 11 KV LAS station type including earthing | Elecy | Labour | SWR10397 | 559 | SET | 1118
89 | 8 | Erect of 11kvLA line type incl earthing Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 11 KV LAS line type including earthing | Elecy | Labour | SWR10398 | 505 | SET | 4040
90 | 10 | Loading of 11 KV VCBs along with Panel boards | Elecy | supply | SWR10199 | 1024 | EA | 10240
91 | 5 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Transport of Cond Drum,VCBs>10 & <20Km | Elecy | Labour | SWR11861 | 3299.7 | EA | 16498.5
92 | 10 | Un loading of 11 KV VCBs along with Panel boards | Elecy | Labour | SWR10517 | 1044.48 | EA | 10444.8
93 | 52 | Excavate-Pit for 33KV VCB | Elecy | Labour | SWR23224 | 331 | M3 | 17212
94 | 60 | Cement concrete with 40MM metal VCB plin Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x 1.8 x 0.75 cum for VCB Plinth | Elecy | Labour | SWR20685 | 5160 | M3 | 309600
95 | 10 | Erection of 11kv VCB Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 11 KV VCB with Control Panel | Elecy | Labour | SWR10461 | 12000 | EA | 120000
96 | 12 | S-Tension HW 3Bolt 1Zebra/Pnthr 150mm Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing. | Elecy | supply | SMR11915 | 2055 | SET | 24660
97 | 12 | Supply of I-Bolts Supply of various Clamps Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367- 1961) Supply of I Bolts | Elecy | Labour | SMR22473 | 294 | EA | 3528
98 | 45 | Sup T clamp LM6 Al alloy of 12 mm, 800 A Supply of various Clamps Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367- 1961) Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 " to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating . | Elecy | supply | SMR40011 | 299 | EA | 13455
99 | 2 | Hoisting post ins&hrd wr 1panther 11kv Bus Stringing Hoisting of Insulators and hardware, stretching the conductor and stringing of 11 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 3.5mt) | Elecy | Labour | SWR21241 | 507 | EA | 1014
100 | 45 | Conn. of equip/bus single zebra/panther Bus Stringing Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | Elecy | supply | SWR10884 | 224 | EA | 10080
101 | 57 | Labour for Fixing of all types of clamps | Elecy | supply | SWR10917 | 65 | EA | 3705
102 | 6.27 | LOADING of MS Channel,Angles,Flats&Rods | Elecy | supply | SWR10206 | 221 | TO | 1385.67
103 | 6.27 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 KM and upto 20 KM | Elecy | supply | SWR10132 | 412.08 | TO | 2583.7416
104 | 6.27 | UNLOADING of MS Channel,Angles,Flats&Rod | Elecy | supply | SWR10524 | 185 | TO | 1159.95
105 | 696 | Laying of earth mat,excavation 75x 8mm Laying of earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication. 75x 8mm MS Flat / GI Flat. | Elecy | supply | SWR10920 | 65 | RMT | 45240
106 | 1247 | Earthing for raisers of SS Flat 50x6 mm. Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) | Elecy | supply | SWR10919 | 41 | RMT | 51127
107 | 36 | S-CI Pipe earthing 100mm dia 2.75m long Supply of earthing pipe with materials Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Elecy | supply | SMR11482 | 3486 | EA | 125496
108 | 36 | ERECT. OF LINES-Providing of earthing Providing of Earthing Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elecy | supply | SWR10357 | 1234.2 | EA | 44431.2
109 | 36 | ERECT. OF LINES-Providing of RCC collar Providing of RCC collar to earth pit. Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Elecy | supply | SWR10359 | 386 | EA | 13896
110 | 2 | SupCU Flexi jumper for Power T/F Neutral Supply of Copper Flexible jumper with 75 X 8 of length 250 mm at neutral of Power tranformer end and 50 X 6 of length 50mm two Nos at double neutral end duly brasing with flexible jumper of capacity of 5kA/3 sec for power transformer neutral. | Elecy | supply | SMR40033 | 4725 | EA | 9450
111 | 2 | Provd-Dble Erth with CuJumper incl MSChl Providing of earthing with various types of earth electrodes Providing of double earthing for neutral with flexible copper jumpers including arrangement by fixing M.S.Channel100x50mm. | Elecy | supply | SWR11892 | 1323 | EA | 2646
112 | 4 | Loading of LT AB Cable 3X16+25 Sqmm | Elecy | supply | SWR11702 | 200 | DR | 800
113 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Transport of Cond Drum,VCBs>10 & <20Km | Elecy | supply | SWR11861 | 3299.7 | EA | 3299.7
114 | 4 | Un loading of LT AB Cable 3X16+25 Sqmm | Elecy | supply | SWR11713 | 204 | DR | 816
115 | 90 | Providing of control cable trench as per DATA-XII | Elecy | supply | SWR22093 | 3148 | RMT | 283320
116 | 3312 | Lay-4C/10C 2.5Sqmm Control Cable Control Cable Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends . | Elecy | supply | SWR11879 | 27 | M | 89424
117 | 270 | L-Cable Termination to Switchgear Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per specification (including cost of ferrules, lugs and glands) | Elecy | supply | SWR12510 | 27 | EA | 7290
118 | 4 | Supply of FRP PT Marshalling Box Marshalling Box Supply of FRP PT Marshalling Box | Elecy | supply | SMR40048 | 4463 | EA | 17852
119 | 4 | Erection of Marshalling boxes Marshalling Box Erection of Marshalling boxes | Elecy | supply | SWR10940 | 374.85 | EA | 1499.4
120 | 1 | Loading 220 V Battery with Charger | Elecy | supply | SWR11166 | 1612 | SET | 1612
121 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Transport of Cond Drum,VCBs>10 & <20Km | Elecy | supply | SWR11861 | 3299.7 | EA | 3299.7
122 | 1 | Un-loading 220 V Battery with Charger | Elecy | Labour | SWR11147 | 1024 | SET | 1024
123 | 1 | Erect-220V 200Ah ConvtLead AcidBtry Batteries Erection of 220 V, 200 AH battery in complete shape fit for charging . Conventional lead acid | Elecy | Labour | SWR12350 | 7666 | EA | 7666
124 | 1 | Supply of DC Anunc.relay panel 8 feeders Control Panels Supply of DC Annunciation & relay panel for 10 feeder panel including the cost of LED Indiacation lamps, VAA auxilairy relays, Electronic Hooters complete as per specification | Elecy | Labour | SMR40044 | 42500 | EA | 42500
125 | 1 | Supply of AC Supply panel complete Control Panels Supply of AC Supply panel inluding providing of changeover switch, SFU, metering unit, 32 A three phase MCB, 16 A Single phase MCB complete as per specification. | Elecy | Labour | SMR40045 | 42000 | EA | 42000
126 | 8 | Supply 9mtrs tubular poles single way Yard lightning Supply of stepped tubular poles single way made of steel of length 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9 mm, 2.1 mtrs with outer dia 76.1 mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79 kgf as per IS 2713. | Elecy | Labour | SMR40051 | 13913 | EA | 111304
127 | 8 | S-90W LED fixture set Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE / CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA/OSRAM/SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty 90W LED Fixture set | Elecy | Labour | SMR11594 | 8200 | EA | 65600
128 | 8 | Exca Hard pit w/o blast 0.76X0.76X1.83M Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Elecy | Labour | SWR11039 | 928 | EA | 7424
129 | 8 | Errection of tubular poles Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE / CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA/OSRAM/SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty Erection of tubular poles | Elecy | Labour | SWR10955 | 1379 | EA | 11032
130 | 5.27 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement Mass concreting of supports incl. cement | Elecy | Labour | SWR10356 | 6579 | M3 | 34671.33
131 | 8 | Fixing of LED/Metal halide complete. Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE / CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA/OSRAM/SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty Fixing of Metal halide lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5 GI pipe complete. | Elecy | Labour | SWR10956 | 1268 | EA | 10144
132 | 45 | Supply & Spreading of 20mm HBG metal Supply of HBG metal Supply & spreading of 20mm machine crushed metal (HBG) including cost of conveneyance of all materials, labour charges etc complete for finished item of work and directed by the engineer incharge | Elecy | Labour | SWR10860 | 2113 | M3 | 95085
133 | 3 | LOADING of R.S. Joists 175 x 85 mm | Elecy | Labour | SWR10204 | 76 | EA | 228
134 | 0.75 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 KM and upto 20 KM | Elecy | Labour | SWR10132 | 412.08 | TO | 309.06
135 | 3 | UNLOADING of R.S. Joists 175 x 85 mm | Elecy | Labour | SWR10522 | 50 | EA | 150
136 | 2 | Ex of Hard pit w/o blast 0.75X0.9X1.95M Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Elecy | Labour | SWR11040 | 990.68 | EA | 1981.36
137 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Supply of Material for 1st coat Al. Painting. | Elecy | Labour | SMR40009 | 2181 | TO | 1635.75
138 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium. Labour for 1st coat Al. Painting. | Elecy | Labour | SWR10877 | 851 | TO | 638.25
139 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Supply of Material for 2nd coat Al. Painting. | Elecy | Labour | SMR40010 | 1293 | TO | 969.75
140 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | Elecy | Labour | SWR10879 | 482 | TO | 361.5
141 | 1 | Erect-12Meter Box pole Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation, for RS Joist, Rail poles Supply & Fabrication of bottom plate with 6mm thichness and for Box poles Supply & Fabrication of Top & Bottom plate with 6mm thichness Box pole 12 Mtr | Elecy | Labour | SWR11267 | 3901.37 | EA | 3901.37
142 | 1.732 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement Mass concreting of supports incl. cement | Elecy | Labour | SWR10356 | 6579 | M3 | 11394.828
143 | 1.16 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | Elecy | Labour | SWR10862 | 373 | M2 | 432.68
144 | 2 | Ptg of coping with 2cts white cmnt inclu cement Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | Elecy | Labour | SWR11089 | 48 | EA | 96
145 | 1 | Column type DTR Plinth topslab 4'x4'x6" Construction of DTR Plinth RCC Column type DTR Plinth of size 1'X1'X10',topslab 4'x4'x6" & beam size 4'X8'X8" upto 160KVA | Elecy | Labour | SWR21843 | 25967.57 | EA | 25967.57
146 | 1 | LOADING of 50,63,75&100kva DTR | Elecy | Labour | SWR10195 | 350 | EA | 350
147 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Transport of Cond Drum,VCBs>10 & <20Km | Elecy | Labour | SWR11861 | 3299.7 | EA | 3299.7
148 | 1 | UNLOADING of 50,63,75&100kva DTR | Elecy | Labour | SWR10513 | 280 | EA | 280
149 | 1 | E/r 3ph DTR inclu L&Un-L,T&C on plinth Erection of DTR's including loading and Unloading DTR on the Structure/Plinth etc Erection of 3 Phase DTRs 63,75 & 100 KVA | Elecy | Labour | SWR20905 | 1650 | EA | 1650
150 | 1 | LOADING of 11 KV AB SWCH T.T.200/400 A | Elecy | Labour | SWR12406 | 80 | EA | 80
151 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Transport of Cond Drum,VCBs>10 & <20Km | Elecy | Labour | SWR11861 | 3299.7 | EA | 3299.7
152 | 1 | UNLOADING of 11 KV AB SWCH T.T.200/400 A | Elecy | Labour | SWR12425 | 80 | EA | 80
153 | 1 | Erection of 11kv TT type AB switch Erection of AB Switch and aligment complete Erection of 11KV 200A TT type AB Switch including fixing of cross angles and alignment complete | Elecy | Labour | SWR20102 | 1813.49 | EA | 1813.49
154 | 1 | LOADING of 11 KV HG Fuse Sets | Elecy | Labour | SWR10231 | 18 | EA | 18
155 | 1 | UNLOADING of 11 KV HG Fuse Sets | Elecy | Labour | SWR10549 | 18 | EA | 18
156 | 1 | Erect. of 11kv HG Fuseset incl earthing Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 11 KV HG Fuse set including earthing | Elecy | Labour | SWR10395 | 740.52 | SET | 740.52
157 | 40 | Lay-SR 11KV 3x185sqmm UG Cb HG/BC/CC/BT Excavation & laying of UG Cable in Single Run Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road 11KV 3x185 Sqmm Cable | Elecy | Labour | SWR11920 | 465.46 | M | 18618.4
158 | 20 | Raise-SR 11KV 3x185sqmm UG Cb on support Excavation & laying of UG Cable in Single Run Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) 11 KV 3x185 Sqmm Cable | Elecy | Labour | SWR11956 | 126.23 | M | 2524.6
159 | 2 | OD/Idoor end termination 11kv 3x185 xlpe Making of Outdoor/Indoor End Termination Making 11 KV 3x185 Sqmm Cable Out Door/Indoor end termination | Elecy | Labour | SWR10390 | 2370.63 | EA | 4741.26
160 | 1 | Erection of LT distribution box Erection of LT distribution box including laying of LT cable from distribution box to LT OH line and DTR to distribution box including earthing of distribution box and crimping of lugs connecting of jumpers etc | Elecy | Labour | SWR10674 | 1594.67 | EA | 1594.67
161 | 85 | Lay-SR LT 3.5x95sqmm UG Cb HG/BC/CC/BT Excavation & laying of UG Cable in Single Run Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road LT 3 1/2 x 95 Sqmm Cable | Elecy | Labour | SWR11925 | 377.63 | M | 32098.55
162 | 15 | Raise-SR LT 3.5x95sqmm UG Cb on support Excavation & laying of UG Cable in Single Run Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV 1.05Mtrs & 33 KV - 1.20 mtrs. Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) LT 3 1/2 x 95 Sqmm Cable | Elecy | Labour | SWR11961 | 85.43 | M | 1281.45
163 | 2 | OD/Idoor end termination LT 3 1/2 x 185 Making of Outdoor/Indoor End Termination Supply & fixing of Oout Door/Indoor end termination LT 3 1/2 x 185 Sqmm Cable | Elecy | Labour | SWR10765 | 968.9 | EA | 1937.8
164 | 1 | Sup &fix of board ind Switchyard layout Supply and fixing of Substation board of size 3'x2.5' indicating the layout of switchyard | Elecy | Labour | SWR20032 | 1654 | EA | 1654
165 | 1 | Sup& fix safety inst/SS Op. inst board Supply and fixing of safety instructions/Substation operation instruction board | Elecy | Labour | SWR22090 | 2205 | EA | 2205
166 | 750 | Supply,fabricati of 6mm Checkerd plates Control Panels Supplying & fabrication erection of 6mm Checkerd plates as per the field conditions | Elecy | Labour | SWR10873 | 83 | KG | 62250
167 | 1 | Supply of Wall clock standard make T & P Wall clock standard make | Elecy | Labour | SMR40059 | 578 | EA | 578
168 | 1 | S-10ft Aluminium Ladder | Elecy | Labour | SMR12378 | 1654 | EA | 1654
169 | 1 | Sup Alluminium Ladder for indoor works | Elecy | Labour | SMR40062 | 4410 | EA | 4410
170 | 30 | Painting of Name Plates for any equipmen T & P Painting of Name Plates for any equipment | Elecy | Labour | SWR10963 | 122 | EA | 3660
171 | 1 | SupTaparia Tool kit complete as per Spec Supply of Taparia Tool kit of Size 20”x10”x15” with tier arrangements Tool box with locking arrangement & key containing (1) Double Ended fix Spanner sets, (Ribbed) 6 x 7, 8 x 9, 10 x 11, 12 x 13, 14 x 15, 16 x 17, 18 x19, 20 x 22, 21 x 23, 24 x 27, 25 x28, 30 x 32, (2) Double Ended Ring Spanners sets, 6 x 7 , 8 x 9, 10 x 11, 12 x 13, 14 x 15. 16 x 17 , 18 x 19, 20 x 22 , 21 x 23, 24 x 27, 25 x28, 30 x 32 mm, (3) Adjustable Spanner 305 mm length least maximum opening 35mm chrome, (4) Pipe Wrench Length 350 mm 14”, (5) Soft faced Hammer with suitable handle 2 lb, (6) Hacksaw frame with metal handle heavy duty for 12" hacksaw blade with High Speed blade, (7) Insulated Screw drivers Transparent Green Handle Set Length 6”, 8” & 12”, (8) Star Screw Driver Transparent Green Handle Length 6”, (9) Insulated Wire Cutter, (10) Insulated Cutting Plier Length 8” with cable stripper insulated with thick C. A. sleeve confirming to IS: 4378 - 1990, (11) Long Nose Plier insulated with thick C.A. sleeve generally confirming to IS:3552-1989, (12) Tester type screw driver (special with neon bulb) generally confirm to IS: 5579-1985 Grade:II handle yellow/ green colour overall length 130 mm, (13) Insulated Crimping Plier of all Taparia make. | Elecy | Labour | SMR40063 | 4925 | SET | 4925
172 | 1 | Supply of Rechargeable LED torch light. Rechargeable LED torch light of Standard make | Elecy | Labour | SMR40064 | 1733 | EA | 1733
173 | 1 | Sup Steel almarah(61/2 X 3ft) Godrej T & P Steel almarah(61/2 X 3ft) Godrej | Elecy | Labour | SMR40061 | 9818 | EA | 9818
174 | 1 | Supply of Table (3x6ft) Godrej T & P Table (3x6ft) Godrej | Elecy | Labour | SMR40057 | 6050 | EA | 6050
175 | 4 | Supply of S type chairs (Godrej) T & P S type chairs (Godrej) | Elecy | Labour | SMR40058 | 924 | EA | 3696
176 | 1 | Sup Angle racks(18x36.6inches) Godrej T & P Angle racks(18x36.6inches) Godrej | Elecy | Labour | SMR40060 | 1733 | EA | 1733
177 | 1 | Supply of Hack saw (12 inches) T & P Hack saw (12 inches) | Elecy | Labour | SMR40065 | 289 | EA | 289
178 | 4 | Supply of Earth Rods (8ft) Screw & clamp type | Elecy | Labour | SMR40066 | 578 | EA | 2312
179 | 2 | Supply of Hand Gloves | Elecy | Labour | SMR40067 | 289 | SET | 578
180 | 12 | Supply of Rubber mats( 6#x3#)size for indoorSS | Elecy | Labour | SMR40068 | 1386 | EA | 16632
181 | 1 | Supply of Stand basic cell phone with charger Biometric Time attendence System & Telecom Standard basic cell phone with charger | Elecy | Labour | SMR40069 | 1386 | EA | 1386
182 | 14 | Supply of Danger boards with clamps | Elecy | Labour | SMR40070 | 116 | EA | 1624
183 | 2 | Sup Fire Buckets Stand with Buckets Supply of Materials Fire bucket stand with 3 buckets (8 -10 ltr capacity) | Elecy | Labour | SMR40088 | 1386 | SET | 2772
184 | 2 | Supply of Fire Extinguisher for Control Room Room fire extinguisher (2 ltrs capacity) for control room | Elecy | Labour | SMR40089 | 4620 | EA | 9240
185 | 4 | Sup TrollyMounted Co2 Cylinders(IS-2878) (6.5Kgs)) | Elecy | Labour | SMR40087 | 9240 | EA | 36960
186 | 6 | Supply of Safety Helmet of standard make | Elecy | Labour | SMR40071 | 231 | EA | 1386
187 | 8 | Supply of LC Boards | Elecy | Labour | SMR40072 | 116 | EA | 928
188 | 4 | Supply of Gum Boots | Elecy | Labour | SMR40073 | 693 | EA | 2772
189 | 1 | Supply of 5000v megger | Elecy | Labour | SMR40074 | 13860 | EA | 13860
190 | 1 | Supply of Earth megger (1000v) | Elecy | Labour | SMR40075 | 8085 | EA | 8085
191 | 1 | Supply of Digital clamp meter. | Elecy | Labour | SMR40076 | 2888 | EA | 2888
192 | 1 | Sup 33/11kv S.S Permanent name board Name board of the 33/11kV Sub-Station(As per Standard Specification) | Elecy | Labour | SMR40086 | 10238 | EA | 10238
193 | 800 | S-Hot dip gal./Zinc bolts & nuts washer Supply of Hot dip galvanized/zinc coated bolts & nuts including spring washers, pack washers and flat washers etc. | Elecy | Labour | SMR12488 | 90 | KG | 72000
194 | 4 | LOADING of R.S. Joists 175 x 85 mm | Elecy | Labour | SWR10204 | 76 | EA | 304
195 | 1 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 KM and upto 20 KM | Elecy | Labour | SWR10132 | 412.08 | TO | 412.08
196 | 4 | UNLOADING of R.S. Joists 175 x 85 mm | Elecy | Labour | SWR10522 | 50 | EA | 200
197 | 4 | Exca Hard pit w/o blast 0.76X0.76X1.83M Excavation of pits in hard rock not requiring blasting. (In hard murram / rockboulders) 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Elecy | Labour | SWR11039 | 928 | EA | 3712
198 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Supply of Material for 1st coat Al. Painting. | Elecy | Labour | SMR40009 | 2181 | TO | 2181
199 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium. Labour for 1st coat Al. Painting. | Elecy | Labour | SWR10877 | 851 | TO | 851
200 | 1 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Supply of Material for 2nd coat Al. Painting. | Elecy | Labour | SMR40010 | 1293 | TO | 1293
201 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | Elecy | Labour | SWR10879 | 482 | TO | 482
202 | 3.51 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement Mass concreting of supports incl. cement | Elecy | Labour | SWR10356 | 6579 | M3 | 23092.29
203 | 2.31 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | Elecy | Labour | SWR10862 | 373 | M2 | 861.63
204 | 4 | Ptg of coping with 2cts white cmnt inclu cement Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | Elecy | Labour | SWR11089 | 48 | EA | 192
205 | 5 | Erection of RS Joist 175 x 85 mm Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation, for RS Joist, Rail poles Supply & Fabrication of bottom plate with 6mm thichness and for Box poles Supply & Fabrication of Top & Bottom plate with 6mm thichness RS Joists 150x75/175 x 85 mm | Elecy | Labour | SWR10346 | 1934 | EA | 9670
206 | 24 | LOADING of 11 KV AB SWCH Con 200/400 A | Elecy | Labour | SWR10238 | 80 | EA | 1920
[7 empty] | sub Total | 3832061.0467
Bay extension
207 | 3 | Supply of 33KV TC Structure as per DATA-II | Elecy | Supply | SMR40102 | 50703 | EA | 152109
208 | 5 | Supply of 33KV BD Boom as per DATA-IV | Elecy | Supply | SMR40104 | 18244 | EA | 91220
209 | 3 | Erection of 33KV TC Structure as per DATA-II | Elecy | Labour | SWR11010 | 17393.04 | EA | 52179.12
210 | 5 | Erection of 33KV BD Boom as per DATA-IV | Elecy | Labour | SWR10875 | 505 | EA | 2525
211 | 1 | Loading of 33 KV VCBs along with Panel boards | Elecy | Labour | SWR10198 | 1024 | EA | 1024
212 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Transport of Cond Drum,VCBs>10 & <20Km | Elecy | Labour | SWR11861 | 3299.7 | EA | 3299.7
213 | 1 | UNLOADING of 33 KV VCBs&Panel boards | Elecy | Labour | SWR10516 | 1044.48 | EA | 1044.48
214 | 1 | Erection of 33kv VCB Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33 KV VCB with Control Panel | Elecy | Labour | SWR10460 | 12500 | EA | 12500
215 | 0.78 | LOADING of MS Channel,Angles,Flats&Rods | Elecy | Labour | SWR10206 | 221 | TO | 172.38
216 | 0.78 | UNLOADING of MS Channel,Angles,Flats&Rod | Elecy | Labour | SWR10524 | 185 | TO | 144.3
217 | 0.78 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 KM and upto 20 KM | Elecy | Labour | SWR10132 | 412.08 | TO | 321.4224
218 | 0.38 | Fabrication & erection of Channels Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to theRSupply of Joist poles excluding cost of Mild Steel and transportcharges to substation site, including erection. Fabrication of struc.with welding. | Elecy | Labour | SWR10869 | 3426 | TO | 1301.88
219 | 0.38 | Fabrication & erection of Channels Alligning the Main/Aux. structures. Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication. | Elecy | Labour | SWR10867 | 1470 | TO | 558.6
220 | 0.38 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Supply of Material for 1st coat Al. Painting. | Elecy | Supply | SMR40009 | 2181 | TO | 828.78
221 | 0.38 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium. Labour for 1st coat Al. Painting. | Elecy | Labour | SWR10877 | 851 | TO | 323.38
222 | 0.38 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Supply of Material for 2nd coat Al. Painting. | Elecy | Supply | SMR40010 | 1293 | TO | 491.34
223 | 0.38 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | Elecy | Labour | SWR10879 | 482 | TO | 183.16
224 | 1 | Erection of 33kv CT s | Elecy | Labour | SWR10399 | 1079 | SET | 1079
225 | 1 | Supply & Erection of 33KV 1200A Isolator incl. Solid Core | Elecy | Labour | SWR12375 | 65800 | EA | 65800
226 | 2 | LOADING of 33 KV AB SWCH Con 400/800 A | Elecy | Labour | SWR10239 | 126 | EA | 252
227 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Transport of Cond Drum,VCBs>10 & <20Km | Elecy | Labour | SWR11861 | 3299.7 | EA | 3299.7
228 | 2 | UNLOADING of 33 KV AB SWCH Con 400/800 A | Elecy | Labour | SWR10557 | 79 | EA | 158
229 | 2 | Erection of 33kv ABSwitch incl earthing Erection of AB Switch and aligment complete Erection of 33 KV AB Switch including alignment and earthing | Elecy | Labour | SWR10392 | 4500 | EA | 9000
230 | 2 | Painting AB switch OP rods with PO red Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elecy | Labour | SWR10881 | 142 | EA | 284
231 | 2 | AB Switch Coil Earthing GI No. 8 Wire Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Elecy | Labour | SWR12331 | 146.63 | EA | 293.26
232 | 3 | LOADING of 33 KV10 KA Las Station type | Elecy | Labour | SWR10266 | 41 | EA | 123
233 | 3 | UNLOADING of 33 KV10 KA LAs Station type | Elecy | Labour | SWR10584 | 35 | EA | 105
234 | 1 | Erect of 33kv LA stn type incl earthing Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33 KV LAS station/Line type including earthing | Elecy | Labour | SWR10396 | 880 | SET | 880
235 | 2.52 | 33KV Bay Extn: Supply of GI Flat 100x16mm Extention of 33KV Bay at 132/33KV Sub-station GI Flat 100X16 | Elecy | Supply | SMR24915 | 63235 | TO | 159352.2
236 | 200 | Laying of MS/GI 100x16mm earth flat Laying of earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication. 100x16mm M.S./G.I earth flat | Elecy | Labour | SWR22054 | 65 | RMT | 13000
237 | 85.1 | Earthing for raisers of SS Flat 75x8 mm. Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. M.S./ G.I. Flat 75x8mm / 75 x 12 mm | Elecy | Labour | SWR10918 | 50 | RMT | 4255
238 | 6 | Providing of earthing with various types of earth electrodes Supply&Erec of CI earth Pipe as APTRANCO Excavation of earth pit, supply of cast iron pipe with flange on one end (as per ISS7181/86) of nominal dia 125mm and 2.75 meters long in side the pit including supply and fixing RCC collars 0.75 meter dia (OD), 50mm thick and 0.60meters long complete as per APTRANSCO standards | Elecy | Labour | SWR10924 | 9804 | EA | 58824
239 | 1 | Loading of 11KV 3 Way RMU/Twin feeder panel LOADING of 11KV 3 Way RMU | Elecy | Labour | SWR10615 | 907.8 | EA | 907.8
240 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Transport of Cond Drum,VCBs>10 & <20Km | Elecy | Labour | SWR11861 | 3299.7 | EA | 3299.7
241 | 1 | UNLOADING of 11KV 3 Way RMU | Elecy | Labour | SWR10629 | 907.8 | EA | 907.8
242 | 1 | Control Panels Erection of 33kV Twin feeder C&R panel. Erection of 33kV Twin feeder control & Relay panel in the control room duly mounting them on channels and grouting them with foundation bolts excluding cost of channels & foundation bolts | Elecy | Labour | SWR10934 | 1729 | EA | 1729
243 | 0.24 | Supply of Moose Conductor | Elecy | Supply | SMR23225 | 375155 | KM | 90037.2
244 | 1 | Bus Stringing Hoisting of Insl. 2 Zebra/Phanther 33kV Hoisting of Insulators and hardware, stretching the conductor and stringing of 33 kV bus comprising of three phases with Twin Moose/ Zebra/Panther conductor to a tension of 900kgs including fixing of spacer clamps.(Bus section of 4.5mt) | Elecy | Labour | SWR10882 | 1302 | EA | 1302
245 | 12 | Supply of Spacer Clamp 150mm Spacing Twin Moose | Elecy | Supply | SMR25240 | 294 | EA | 3528
246 | 18 | Supply of T-Clamp Twin to Sngle Moose 150mmSpace | Elecy | Supply | SMR25242 | 694 | EA | 12492
247 | 3 | Supply of LA clamps for single zebra / Panther Supply of Alluminum LA clamps conforming to A6 of IS 617, with hot dip galvanised bolts and nuts suitable for single zebra / Panther | Elecy | Supply | SMR40027 | 357 | EA | 1071
248 | 100 | L-Cable Termination to Switchgear Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per specification (including cost of ferrules, lugs and glands) | Elecy | Labour | SWR12510 | 27 | EA | 2700
249 | 40 | Providing of control cable trench as per DATA-XII | Elecy | Labour | SWR22093 | 3148 | RMT | 125920
250 | 1800 | Lay-4C/10C 2.5Sqmm Control Cable Control Cable Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends . | Elecy | Labour | SWR11879 | 27 | M | 48600
251 | 1 | Supply of MS Powder coated CT Marshalling Box | Elecy | Supply | SMR40047 | 3675 | EA | 3675
252 | 1 | Erection of Marshalling boxes | Elecy | Labour | SWR10940 | 374.85 | EA | 374.85
253 | 2 | Yard lightning Supply of stepped tubular poles single way made of steel of length 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9 mm, 2.1 mtrs with outer dia 76.1 mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79 kgf as per IS 2713 Supply 9mtrs tubular poles single way | Elecy | Supply | SMR40051 | 13913 | EA | 27826
254 | 2 | Exca Hard pit w/o blast 0.76X0.76X1.83M Excavation of pits in hard rock not requiring blasting. (In hard murram / rockboulders) 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Elecy | Labour | SWR11039 | 928 | EA | 1856
255 | 2 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE /CROMPTON/BAJAJ/VIN/WIPRO /JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA/OSRAM /SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing,toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control ofdistribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Polycarbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty Errection of tubular poles | Elecy | Labour | SWR10955 | 1379 | EA | 2758
256 | 2.1 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement Mass concreting of supports incl. cement | Elecy | Labour | SWR10356 | 6579 | M3 | 13815.9
257 | 2 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE /CROMPTON/BAJAJ/VIN/WIPRO /JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA/OSRAM /SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70%electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Polycarbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty Supply-90W LED fixture set | Elecy | Supply | SMR11594 | 8200 | EA | 16400
258 | 2 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE/CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA/OSRAM/SUMSANG/LG LEDs) makewith minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing,toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty. Fixing of Metal halide lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5 GI pipe complete. Fixing of LED/Metal halide complete. | Elecy | Labour | SWR10956 | 1268 | EA | 2536
259 | 24 | Labour for Fixing of all types of clamps | Elecy | Labour | SWR10917 | 65 | EA | 1560
260 | 60 | Supply & Spreading of 20mm HBG metal Supply & spreading of 20mm machine crushed metal (HBG) including cost of conveneyance of all materials, labour charges etc complete for finished item of work and directed by the engineer incharge | Elecy | Labour | SWR10860 | 2113 | M3 | 126780
261 | 2 | Sup Fire Extinguisher for Control Room Room fire extinguisher (2 ltrs capacity) for control room | Elecy | Supply | SMR40089 | 4620 | EA | 9240
262 | 12 | S&Filling with Borrowed Stone Dust Filling with stone dust in basement with 150mm thick layers incldg cost & conveyance all materials watering,consolidation etc complete for finished item of work. | Elecy | Labour | SWR33054 | 1451 | M3 | 17412
263 | 10.8 | Excavation in Ordinary Soil Earth work excavation in all type of soils red earth, Hard gravelly soils, earth mixed with sand and sandy soils etc., in all conditions such as slushy and dry with initial leads and lifts for foundations. | Elecy | Labour | SWR33015 | 513 | M3 | 5540.4
264 | 2.7 | PCC with 40mm Metal (1:4:8) PCC (1:4:8) using 40 mm metal with concrete Mixture. All work upto Plinth level including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete as directed by Engineer incharge of the work | Elecy | Labour | SWR33028 | 5556 | M3 | 15001.2
265 | 16.2 | CRS Masonary CM(1:6) 2nd Sort C.R.S Masonry in C.M(1:6) using HBG stone including cost & conveyance of all materials labour charges,curing,all leads lifts etc., complete for finished item of work. | Elecy | Labour | SWR33041 | 5829 | M3 | 94429.8
266 | 63 | Plastering 20mm (16mm+4mm)Gfloor Plastering of 20mm thick to all uneven faces of walls of superstructure in two coats with base coat in CM 1:5 of 16mm thick and top coat in CM 1:3 4mm thick with dubara sponge finish including cost and conveyance of all materials, water, all labour charges, curing for specified number of days, cutting grooves, all leads, lifts and scaffolding charges,all incidental charges etc. complete for finished item of work and as directed by the Engineer - in - charge. Ground Floor | Elecy | Labour | SWR33163 | 594 | M2 | 37422
267 | 6 | S&F-15mm Bib Tap 300gm Qtr turn Supply & Fixing 15mm bip tap Indian make 300 grams seilo/senior/nice or equivalent | Elecy | Labour | SWR34330 | 690 | EA | 4140
268 | 40 | S&F 22.20mm OD CPVC Pipe-SDR 11 Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-22.20mm OD Pipe - SDR 11 | Elecy | Labour | SWR34362 | 459 | M | 18360
269 | 12 | Painting of poles Painting of feeder name on support including cost of paint | Elecy | Labour | SWR12101 | 53 | EA | 636
270 | 100 | S-GI Bolts & Nuts,Washers etc., Supply of earthing pipe with materials Supply of GI Bolts & Nuts etc | Elecy | Supply | SMR11488 | 117.5 | KG | 11750
271 | 4.9 | Excavation in Ordinary Soil Earth work excavation in all type of soils red earth, Hard gravelly soils, earth mixed with sand and sandy soils etc., in all conditions such as slushy and dry with initial leads and lifts for foundations. | Elecy | Labour | SWR33015 | 513 | M3 | 2513.7
272 | 0.31 | PCC with 40mm Metal (1:4:8) PCC (1:4:8) using 40 mm metal with concrete Mixture. All work upto Plinth level including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete as directed by Engineer incharge of the work | Elecy | Labour | SWR33028 | 5556 | M3 | 1722.36
273 | 0.56 | RCC Footing: M20Gr, Steel Centering RCC M - 20 Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including all operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete but excluding cost of steel and its fabrication charges for finished item of work - Footing | Elecy | Labour | SWR33098 | 10503 | M3 | 5881.68
274 | 2.03 | RCC Column GF: M20Gr, Steel Centering RCC M - 20 Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including all operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete but excluding cost of steel and its fabrication charges for finished item of work - Column Ground floor | Elecy | Labour | SWR33100 | 14493 | M3 | 29420.79
275 | 0.1 | Reinforcement Steel Fe 415/500 Providing High Yield Strength Deformed (HYSD)/ Thermo Mechanically Treated (TMT) / Mild steel (MS) steel bars (Fe 415/ Fe 500 grade as per IS 1786-1979) of different diameters for RCC works , including labour charges for straightening, cutting, bending to required sizes and shapes, placing in position with cover blocks of approved materials and size and tying and lap-splicing with binding wire of 18 SWG, forming grills for reinforcement work as per approved designs and drawings, including cost and conveyance of steel bars, including all wastages such as overlaps, couplings, chairs, spacer bars including cost and conveyance of binding wire, cover blocks and all incidental, operational, labour charges such as cutting, bending, placing in position, tying excluding taxes on all materials etc., complete for finished item of work in all floors.( APSS No.126) | Elecy | Labour | SWR33144 | 79136 | TON | 7913.6
276 | 0.5 | S&F Structural Steel Angles etc. S&F of Structural steel of Angles,Channels,Beams etc including fabrication & erection, all incidental, operational, labour charges such as cutting, bending, placing in position, excluding taxes complete for finished item of work. | Elecy | Labour | SWR33145 | 129 | KG | 64.5
277 | 1.31 | Seigniorage Charges - Sand | Elecy | Labour | SWR34470 | 40 | M3 | 52.4
278 | 2.67 | Seigniorage Charges - Metal | Elecy | Labour | SWR34471 | 97.5 | M3 | 260.325
[7 empty] | sub Total | 1388768.7074
33kV line labour
279 | 8.02 | survey line&cabl inc peg mark&tree clear | Elecy | Labour | SWR22092 | 765 | KM | 6135.3
280 | 67 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Elecy | Labour | SWR11230 | 1024 | DR | 68608
281 | 34 | Transport of Cond Drum,VCBs upto 10Km Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, Battery Chargers with Batteries, RMU, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Upto 10 Km with Lorry for each trip | Elecy | Labour | SWR11860 | 2720.34 | EA | 92491.56
282 | 67 | Un loading of 11KV/33KV XLPE UG Cable for all sizes | Elecy | Labour | SWR11231 | 1024 | DR | 68608
283 | 100 | Lay-DR 33KV 3x400sqmm UG Cb HG/BC/CC/BT Excavation & laying of UG Cable (Double Run) Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV- In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil/CC 33 KV 3x400 Sqmm Cable | Elecy | Labour | SWR11972 | 749 | M | 74900
284 | 100 | Laying of 2nd Cable in Excavated Trench | Elecy | Labour | SWR10988 | 204.1 | M | 20410
285 | 30 | Raise-DR 33KV 3x400sqmm UG Cb on support Excavation & laying of UG Cable (Double Run) Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV- Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) 33 KV 3x400 Sqmm Cable | Elecy | Labour | SWR12004 | 323.85 | M | 9715.5
286 | 4 | OD/Idoor end termination 33kv 3x400 xlpe Making of Outdoor/Indoor End Termination Making 33 KV 3x400 Sqmm Cable Out Door/Indoor end termination | Elecy | Labour | SWR10387 | 2764.76 | EA | 11059.04
287 | 2 | Straight through joint 33kv 3x400 xlpe Making of Straight through joints 33 KV 3x400 Sqmm Cable | Elecy | Labour | SWR10382 | 5700.78 | EA | 11401.56
288 | 24 | Supply of 33KV 1x630Sqmm OD Unit End Termination | Elecy | Labour | SMR12474 | 4200 | EA | 100800
289 | 24 | Install-33KV 1x630Sqmm OD Unit End Termination | Elecy | Labour | SWR12474 | 4000 | EA | 96000
290 | 2 | Supply&Erec of CI earth Pipe as APTRANCO Providing of earthing with various types of earth electrodes Excavation of earth pit, supply of cast iron pipe with flange on one end (as per ISS7181/86) of nominal dia 125mm and 2.75 meters long in side the pit including supply and fixing RCC collars 0.75 meter dia (OD), 50mm thick and 0.60meters long complete as per APTRANSCO standards | Elecy | Supply | SWR10924 | 9804 | EA | 19608
291 | 1800 | Lay-4 SC 33KV 630sqmm UG Cb HG/BC/RE/NS 33KV 1-Core Cable Laying of 4No's single core 630(Alluminium)/400(Copper) sqmm UG cable (Single Circuit with one spare cable) including excavation of trench of size 0.7 Mtrs width and 1.2 Mtrs depth from road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil | Elecy | Supply | SWR12110 | 2463.3 | M | 4433940
292 | 6120 | Lay-4 SC 33KV 630sqmm UG Cb HG/BC/RE/NS 33KV 1-Core Cable Laying of 4No's single core 630(Alluminium)/400(Copper) sqmm UG cable (Single Circuit with one spare cable) including excavation of trench of size 0.7 Mtrs width and 1.2 Mtrs depth from road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc. Along the CC / BT multi layer road requiring compressor | Elecy | Supply | SWR12111 | 2912.1 | M | 17822052
293 | 160 | Raise-SR 33KV 1x630sqmm UG Cb on Support ACSS Dog HTLS Conductor Raising of Single Run 33KV 1x630sqmm UG Cable on Support | Elecy | Labour | SWR12448 | 133 | M | 21280
294 | 720 | HDD cable with HDPE pipe in Hard rock HDD (Horizontal Directional Drilling) in normal soil Laying of 33&11KV UG cable by HDD method with casing HDPE pipe of 160mm PN4 PE 80 as per IS4984 | Elecy | Labour | SWR11001 | 6993 | M | 5034960
295 | 68 | S-33KV 1x630sqmm Ray Fit Joint ACSS Dog HTLS Conductor Supply of 33KV 1x630sqmm Ray Fit Joint | Elecy | Labour | SMR12379 | 26500 | EA | 1802000
296 | 68 | Providing of Single Core straight though Joint | Elecy | Labour | SWR12264 | 3403 | EA | 231404
297 | 20 | S-6" B Class GI pipe 5mm thck 20Kg/M Cost of Pipes and slabs Supply of 6" B class GI pipe 150 NB GI Pipe 4.85 mm thickness, 19.2 KG/Mtr | Elecy | Supply | SMR40081 | 1344 | M | 26880
298 | 1248 | S-4" BClass GI pipe 3.65mm thck 12.2Kg/M Cost of Pipes and slabs Supply of 4" B Class GI Pipe 100 NB GI Pipe 4.50 mm thickness, 12.1 KG/Mtr | Elecy | Supply | SMR40080 | 800 | M | 998400
299 | 800 | Supply of 250 mm Hume pipe of class NP3 Cost of Pipes and slabs Supply of 250 mm Hume pipe of class NP3 with compresive strength of 35N/mm2 for 28 days curing,barewall thickness of 30mm,1.25kG linear/meter and withstanding capability of 22.50KN/linear meter as per IS 458-1993. | Elecy | Labour | SMR40077 | 363 | M | 290400
300 | 1.2 | LOADING of MS Channel,Angles,Flats&Rods | Elecy | Labour | SWR10206 | 221 | TO | 265.2
301 | 1.2 | UNLOADING of MS Channel,Angles,Flats&Rod | Elecy | Labour | SWR10524 | 185 | TO | 222
302 | 16 | LOADING of R.S. Joists 175 x 85 mm | Elecy | Labour | SWR10204 | 76 | EA | 1216
303 | 5.2 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 KM and upto 20 KM | Elecy | Labour | SWR10132 | 412.08 | TO | 2142.816
304 | 16 | UNLOADING of R.S. Joists 175 x 85 mm | Elecy | Labour | SWR10522 | 50 | EA | 800
305 | 16 | Fabricate&Paint- 175x85/150x75mm RS Joist Fabrication of poles: Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable, Painting of RS Joist on inner phasing with red Oxide before Joining as box pole | Elecy | Labour | SWR10642 | 512.55 | EA | 8200.8
306 | 8 | EXCAV OF PIT HARD 0.75 Mx0.9 Mx1.95 M Excavation of pits in hard rock requiring blasting. (other than SS) 11Mtrs PSCC Pole/ Box poles 0.75 M x 0.9 M x 1.95 M | Elecy | Labour | SWR10113 | 1326 | EA | 10608
307 | 4 | Erection of 9/10/11Meter Box pole Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation, for RS Joist, Rail poles Supply & Fabrication of bottom plate with 6mm thichness and for Box poles Supply & Fabrication of Top & Bottom plate with 6mm thichness Box pole 9/10/11 Mtr | Elecy | Labour | SWR11266 | 2643.83 | EA | 10575.32
308 | 10.48 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement Mass concreting of supports incl. cement | Elecy | Labour | SWR10356 | 6579 | M3 | 68947.92
309 | 0.248 | Coping & Muffing-Iron Pole Mass Concreting for pole Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Elecy | Labour | SWR11890 | 3892.98 | M3 | 965.459
310 | 4 | S-GI pipe earthing 40mm dia 2m long Supply of earthing pipe with materials Supply of GI eath pipe with 40 mm dia,3mm thcikness with 2.0 M Length | Elecy | Labour | SMR11480 | 698 | EA | 2792
311 | 4 | S-CI Pipe earthing 80mm dia 2.75m long Supply of earthing pipe with materials Supply of CI eath pipe with 80mm dia,2.0 M Length | Elecy | Labour | SMR11483 | 2789 | EA | 11156
312 | 8 | ERECT. OF LINES-Providing of earthing Providing of Earthing Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elecy | Labour | SWR10357 | 1234.2 | EA | 9873.6
313 | 8 | ERECT. OF LINES-Providing of RCC collar Providing of RCC collar to earth pit. Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Elecy | Labour | SWR10359 | 386 | EA | 3088
314 | 8 | Painting of poles Painting of feeder name on support including cost of paint | Elecy | Labour | SWR12101 | 53 | EA | 424
315 | 100 | S-GI Bolts & Nuts,Washers etc., Supply of earthing pipe with materials Supply of GI Bolts & Nuts etc | Elecy | Labour | SMR11488 | 117.5 | KG | 11750
316 | 4.7 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Supply of Material for 1st coat Al. Painting. | Elecy | Labour | SMR40009 | 2181 | TO | 10250.7
317 | 4.7 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium. Labour for 1st coat Al. Painting. | Elecy | Labour | SWR10877 | 851 | TO | 3999.7
318 | 4.7 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Supply of Material for 2nd coat Al. Painting. | Elecy | Labour | SMR40010 | 1293 | TO | 6077.1
319 | 4.7 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | Elecy | Labour | SWR10879 | 482 | TO | 2265.4
320 | 2 | LOADING of 33 KV AB SWCH Con 400/800 A | Elecy | Labour | SWR10239 | 126 | EA | 252
321 | 2 | UNLOADING of 33 KV AB SWCH Con 400/800 A | Elecy | Labour | SWR10557 | 79 | EA | 158
322 | 2 | Erection of 33kv ABSwitch incl earthing Erection of AB Switch and aligment complete Erection of 33 KV AB Switch including alignment and earthing | Elecy | Labour | SWR10392 | 4500 | EA | 9000
323 | 208.67 | Earthing for raisers of SS Flat 50x6 mm. Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) | Elecy | Supply | SWR10919 | 41 | RMT | 8555.47
324 | 3 | LOADING of 33 KV10 KA Las Station type | Elecy | Supply | SWR10266 | 41 | EA | 123
325 | 3 | UNLOADING of 33 KV10 KA LAs Station type | Elecy | Labour | SWR10584 | 35 | EA | 105
326 | 1 | Erect of 33kv LA stn type incl earthing Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33 KV LAS station/Line type including earthing | Elecy | Labour | SWR10396 | 880 | SET | 880
327 | 2 | Painting AB switch OP rods with PO red Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elecy | Labour | SWR10881 | 142 | EA | 284
328 | 2 | AB Switch Coil Earthing GI No. 8 Wire Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Elecy | Labour | SWR12331 | 146.63 | EA | 293.26
329 | 1 | CAD Drawing per pole upto 10KM Submission of auto CAD Drawing as per pole schedule (Detailed survey and sketch) Up to 10 km | Elecy | Supply | SWR12104 | 6000 | LS | 6000
330 | 81 | Supply & Erection of Smart RFID marker | Elecy | Labour | SWR25089 | 2745 | EA | 222345
331 | 2 | Erect-33KV DP Structure with RS Joist Erection of OH Lines including AB Cable (33KV, 11KV, LT) Assembly and erection of Structure as per specification which includes fixing of top channels and cross bracings, transport of all materials from road side to the location, earthing, back filling with earth ramming etc excluding pit excavation and concreting. 33 KV DP Structure with 175x85/150x75mm RS joist |  |  | SWR11276 | 5670 | EA | 11340
| sub Total | [6 empty] | 31666008.705
11kV Labour
332 | 480 | Lay-DR 11KV 3x300sqmm UG Cb HG/BC/CC/BT Excavation & laying of UG Cable (Double Run) Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV- In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil/CC 11 KV 3x300 Sqmm Cable | Elecy | Labour | SWR11973 | 631.06 | M | 302908.8
333 | 500 | Lay-6R 11KV 3x300sqmm UG Cb HG/BC/CC/BT Excavation & laying of UG Cable (Six Run ) Laying of XLPE UG cable Six Run including excavation of trench of size 1050mm wide to 1200mm wide as per the site conditions and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second,third or more cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil/CC 11 KV 3x300 Sqmm Cable | Elecy | Labour | SWR12066 | 1262.25 | M | 631125
334 | 2750 | Lay-SR 11KV 3x300sqmm UG Cb CC/BT Compsr Excavation & laying of UG Cable in Single Run Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. Along the CC / BT multi layer road requiring compressor 11 KV 3x300 Sqmm Cable | Elecy | Labour | SWR11928 | 1073.94 | M | 2953335
335 | 480 | Lay-TR 11KV 3x300sqmm UG Cb CC/BT Compsr Excavation & laying of UG Cable (Triple Run ) Laying of XLPE UG cable Triple or more Run including excavation of trench of size 1000mm wide to 750mm wide as per the site conditions and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second,third or more cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. Along the CC / BT multi layer road requiring compressor 11 KV 3x300 Sqmm Cable | Elecy | Labour | SWR12020 | 1578.45 | M | 757656
336 | 60 | HDD cable with HDPE pipe in Hard rock HDD (Horizontal Directional Drilling) in normal soil Laying of 33&11KV UG cable by HDD method with casing HDPE pipe of 160mm PN4 PE 80 as per IS4984 | Elecy | Labour | SWR11001 | 6993 | M | 419580
337 | 3940 | Laying of 2nd Cable in Excavated Trench | Elecy | Labour | SWR10988 | 204.1 | M | 804154
338 | 78 | OD/Idoor end termination 11kv 3x300 xlpe Making of Outdoor/Indoor End Termination Making 11 KV 3x300 Sqmm Cable Out Door/Indoor end termination | Elecy | Labour | SWR10391 | 2370.63 | EA | 184909.14
339 | 30 | Straight through joint 11kv 3x300 xlpe Making of Straight through joints 11 KV 3x300 Sqmm Cable | Elecy | Labour | SWR10386 | 3725.45 | EA | 111763.5
340 | 200 | Raise-SR 11KV 3x300sqmm UG Cb on support Excavation & laying of UG Cable in Single Run Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) 11 KV 3x300 Sqmm Cable | Elecy | Supply | SWR11955 | 144.08 | M | 28816
341 | 29 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Elecy | Supply | SWR11230 | 1024 | DR | 29696
342 | 15 | Un loading of 11KV/33KV XLPE UG Cable for all sizes | Elecy | Labour | SWR11231 | 1024 | DR | 15360
343 | 29 | Transport of Cond Drum,VCBs upto 10Km Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, Battery Chargers with Batteries, RMU, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Upto 10 Km with Lorry for each trip | Elecy | Labour | SWR11860 | 2720.34 | EA | 78889.86
344 | 8 | S-GI pipe earthing 40mm dia 2m long Supply of earthing pipe with materials Supply of GI eath pipe with 40 mm dia,3mm thcikness with 2.0 M Length | Elecy | Labour | SMR11480 | 698 | EA | 5584
345 | 18 | S-CI Pipe earthing 100mm dia 2.75m long Supply of earthing pipe with materials Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Elecy | Labour | SMR11482 | 3486 | EA | 62748
346 | 26 | ERECT. OF LINES-Providing of earthing Providing of Earthing Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elecy | Labour | SWR10357 | 1234.2 | EA | 32089.2
347 | 26 | ERECT. OF LINES-Providing of RCC collar Providing of RCC collar to earth pit. Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Elecy | Supply | SWR10359 | 386 | EA | 10036
348 | 224 | S-4" BClass GI pipe 3.65mm thck 12.2Kg/M Cost of Pipes and slabs Supply of 4" B Class GI Pipe 100 NB GI Pipe 4.50 mm thickness, 12.1 KG/Mtr | Elecy | Supply | SMR40080 | 800 | M | 179200
349 | 50 | S-GI Bolts & Nuts,Washers etc., Supply of earthing pipe with materials Supply of GI Bolts & Nuts etc | Elecy | Labour | SMR11488 | 117.5 | KG | 5875
350 | 123 | S-Earthing GI flat 25x3 mm incl material Supply of earthing pipe with materials Supply of GI Flat 25X3 mm | Elecy | Labour | SMR11485 | 105 | KG | 12915
351 | 205 | Run-GI Earth Flat 25x3mm from metallic p Running of GI eartn flat of size 25X3mm from all metallic parts of channels, AB Switch, HG fuse set, DTr neutral and LT Distribution box and inter connection of earth pits etc complete | Elecy | Labour | SWR12125 | 14.03 | M | 2876.15
352 | 32 | Labour for Fixing of all types of clamps | Elecy | Labour | SWR10917 | 65 | EA | 2080
353 | 6 | Loading of 11KV 3 Way RMU/Twin feeder panel | Elecy | Labour | SWR10615 | 907.8 | EA | 5446.8
354 | 6 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Transport of Cond Drum,VCBs>10 & <20Km | Elecy | Labour | SWR11861 | 3299.7 | EA | 19798.2
355 | 6 | Un loading of 11KV 3 Way RMU/Twin feeder panel | Elecy | Labour | SWR10629 | 907.8 | EA | 5446.8
356 | 6 | Erection of 11KV 3 Way RMU | Elecy | Labour | SWR10664 | 2051.48 | EA | 12308.88
357 | 20 | Supply & Erection of Smart RFID marker | Elecy | Supply | SWR25089 | 2745 | EA | 54900
358 | 0.315 | LOADING of MS Channel,Angles,Flats&Rods | Elecy | Labour | SWR10206 | 221.02 | TO | 69.6213
359 | 0.315 | UNLOADING of MS Channel,Angles,Flats&Rod | Elecy | Labour | SWR10524 | 185.02 | TO | 58.2813
360 | 14 | LOADING of R.S. Joists 175 x 85 mm | Elecy | Labour | SWR10204 | 76 | EA | 1064
361 | 3.815 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 KM and upto 20 KM | Elecy | Labour | SWR10132 | 412.08 | TO | 1572.0852
362 | 14 | UNLOADING of R.S. Joists 175 x 85 mm | Elecy | Labour | SWR10522 | 50 | EA | 700
363 | 14 | Fabricate&Paint- 175x85/150x75mm RS Joist Fabrication of poles: Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable, Painting of RS Joist on inner phasing with red Oxide before Joining as box pole | Elecy | Labour | SWR10642 | 512.55 | EA | 7175.7
364 | 7 | EXCAV OF PIT HARD 0.75 Mx0.9 Mx1.95 M Excavation of pits in hard rock requiring blasting. (other than SS) 11Mtrs PSCC Pole/ Box poles 0.75 M x 0.9 M x 1.95 M | Elecy | Labour | SWR10113 | 1326 | EA | 9282
365 | 7 | Erection of 9/10/11Meter Box pole Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation, for RS Joist, Rail poles Supply & Fabrication of bottom plate with 6mm thichness and for Box poles Supply & Fabrication of Top & Bottom plate with 6mm thichness Box pole 9/10/11 Mtr | Elecy | Supply | SWR11266 | 2643.83 | EA | 18506.81
366 | 9.17 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement Mass concreting of supports incl. cement | Elecy | Labour | SWR10356 | 6579 | M3 | 60329.43
367 | 0.248 | Coping & Muffing-Iron Pole Mass Concreting for pole Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Elecy | Labour | SWR11890 | 3892.98 | M3 | 965.459
368 | 7 | S-GI pipe earthing 40mm dia 2m long Supply of earthing pipe with materials Supply of GI eath pipe with 40 mm dia,3mm thcikness with 2.0 M Length | Elecy | Labour | SMR11480 | 698 | EA | 4886
369 | 7 | ERECT. OF LINES-Providing of earthing Providing of Earthing Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elecy | Labour | SWR10357 | 1234.2 | EA | 8639.4
370 | 7 | ERECT. OF LINES-Providing of RCC collar Providing of RCC collar to earth pit. Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Elecy | Labour | SWR10359 | 386 | EA | 2702
371 | 0.315 | Fabrication & erection of Channels Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to theRSupply of Joist poles excluding cost of Mild Steel and transportcharges to substation site, including erection. Fabrication of struc.with welding. | Elecy | Labour | SWR10869 | 3426 | TO | 1079.19
372 | 7 | Loading of 11 KV AB SWCH T.T.200/400 A | Elecy | Labour | SWR12406 | 80 | EA | 560
373 | 7 | UNLOADING of 11 KV AB SWCH T.T.200/400 A | Elecy | Labour | SWR12425 | 80 | EA | 560
374 | 7 | Erection of 11kv ABSwitch incl earthing Erection of AB Switch and aligment complete Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Elecy | Supply | SWR10393 | 3200 | EA | 22400
375 | 6 | Construction of plinth for 3way RMUs etc |  |  | SWR20871 | 6000 | EA | 36000
[7 empty] | sub Total | 6906047.3068
Total Amount | [7 empty] | 43792885.766
GST 18% | [7 empty] | 7882719.4379
Electrical total Amount | [7 empty] | 51675605.2038
WBS. No. S-1936-13-07-01-01-001
| Estimate Quantity (only Figures) | Item Detailed Specification Description | Work Type eg. Earth Work, Electrical works. etc (upto 200 Characters) | Item Short Description (upto 100 Characters) | APSS / Morth Cl. Number (upto 200 Characters) | Rate (INR) (Upto 2 Decimals ) | UOM (upto 50 Characters) | Amount
1 | 40 | Leveliing the site by cutting and levelling with the help of JCB including cost,conveyance of all materials,hire chareges etc complete for finished item of work as directed by Engineer-in-charge. | Civil | Labour | SWR34179 | 2200 | HR | 88000
2 | 68.53 | Earth Work Mass Excavation (hard rock) to a depth as directed, in soils such as hard rock requiring blasting in prohibited area and all conditions such as dry, wet, slurry etc.and in dense or hard soils, disposal and depositing of excavated soil with intial lead of 10 mt and intial lift of 2m or as directed, including cost and conveyance of all materials, ramping and lifting of materials, and labour charges, hire charges of machinery, tools & plants, bailing of water ( either sub soil water, stoMts water, rain water, surface water or of any kind) if any at any stage of work until all works below ground level is finished to the satisfaction ,and from work such as shoring, timbering, strutting with required supports etc. for the work and removal of form work after completion of work etc all complete as directed by the engineer-incharge. | Civil | Labour | SWR33018 | 876 | M3 | 60032.28
3 | 282.85 | Earth work excavation in all type of soils red earth, Hard gravelly soils, earth mixed with sand and sandy soils etc., in all conditions such as slushy and dry with initial leads and lifts for foundations. | Civil | Labour | SWR33015 | 513 | M3 | 145102.05
4 | 57.36 | Plain Cement concrete (1:4:8) using 40mm HBG metal for foundations and leveling course, including cost and conveyance of all materials, labour all leads and lifts, consolidation and all operations, formwork as required, curing, etc. complete for finished item w | Civil | Labour | SWR33028 | 5553 | M3 | 318520.08
5 | 328.12 | Coursed Rubble stone masonry 2nd sort with hard granite stones in cement mortar (1:6) for basement, including cost and conveyance of all materials, labour charges, curing, all leads and lifts, etc, complete for finished item of work. | Civil | Labour | SWR33041 | 5816 | M3 | 1908345.92
6 | 6.44 | RCC M20 Grade footing 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33098 | 10571 | M3 | 68077.24
7 | 5 | RCC M20 Grade Coloumn . 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33100 | 14561 | M3 | 72805
8 | 4.96 | RCC M20 Grade Plinth beams 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33099 | 13666 | M3 | 67783.36
9 | 5.1 | Supplying, Cutting, bending, binding, placing in position and tying reinforcement steel in all heights including cost and conveyance of steel and binding wire etc,. With all leads and lifts, labour charges, etc., complete for finished item of work. | Civil | Labour | SWR33144 | 79136 | MT | 403593.6
10 | 115.45 | Brick masonry in cement mortar (1:6) for superstructure using well burnt country made second class bricks of approved quality including cost and conveyance of all materials curing, scaffolding with all leads and lifts in all heights etc., complete for fin | Civil | Labour | SWR33068 | 8760 | M3 | 1011342
11 | 2.7 | Plain Cement concrete (1:2:4) using 20mm size well graded HBG metal for foundations, including cost, conveyance of all materials,labour all leads and lifts,consolidation and all operations, formwork as required, curing,etc. complete for finished item of work | Civil | Labour | SWR33030 | 7036 | M3 | 18997.2
12 | 1060.14 | Plastering with two coats, 1st coat in cm1:5 16mm thick and 2nd coat in cm 1:4 4mm thick, total 20mm thick for superstructure walls, ceiling, sunshades, Beams, etc., with sponge finishing including cost and conveyance of all materials all leads & lifts e | Civil | Labour | SWR33163 | 593 | M2 | 628663.02
13 | 732.01 | Painting with two coats of ACE paint over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33356 | 222 | M2 | 162506.22
14 | 410.85 | Painting with two coats of Surya Cem paint over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33329 | 88 | M2 | 36154.8
15 | 500 | Manufacturing, Supplying and fixing of MS grill for (Gate and raillings) of approved design as per drawings, including cost and conveyance of all materials, labour charges etc.,complete for finished item of work as directed by the Engineer- in-charge. | Civil | Labour | SWR33145 | 129 | KG | 64500
16 | 3 | Supply and Fixng of MS Name Board including cost & conveyance of all materials,labour charges etc complete for finished item of work. | Civil | Labour | SWR33421 | 4542 | M2 | 13626
17 | 1 | Geophysical Investgation charges for water point by Geologist | Civil | Labour | SWR33608 | 5250 | EA | 5250
18 | 90 | Drill-165mm Bore Well 0 to 90 | Civil | Labour | SWR33609 | 350 | M | 31500
19 | 30 | Drill-165mm Bore Well 90M to 120M | Civil | Labour | SWR34830 | 369 | M | 11070
20 | 30 | Drill-165mm Bore Well 120M to 150M | Civil | Labour | SWR34831 | 394 | M | 11820
21 | 30 | Drill-165mm Bore Well 150M to 180M | Civil | Labour | SWR34832 | 492 | M | 14760
22 | 30 | Drill-165mm Bore Well 180M to 210M | Civil | Labour | SWR34833 | 623 | M | 18690
23 | 30 | Drill-165mm Bore Well 210M to 240M |  |  | SWR34834 | 754 | M | 22620
24 | 30 | Drill-165mm Bore Well 240M to 270M | Civil | Labour | SWR34835 | 918 | M | 27540
25 | 80 | Drill-165mm Bore Well 270M and above | Civil | Labour | SWR34836 | 1082 | M | 86560
26 | 40 | Supply and fixing of 160mm dia PVC casing of A class 6Kg point pressure including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR33611 | 891 | M | 35640
27 | 1 | Supply and erecting, ISI mark submersible 5.0 HP, Single Phase 30 stages pumpset suitable for 106/156mm dia borewell including cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33640 | 56186 | EA | 56186
28 | 290 | Supply and fixing of HDPE pipe 40mm dia of 16Kg/cm2 including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR34410 | 175 | M | 50750
29 | 1 | Supply and erecting D.O.L Starter 415V , Single phase,50Hz with SS enclouserincluding cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33645 | 9900 | EA | 9900
30 | 305 | Supply of 3 Core 2.5 Sqmm Flat Copper cable of ISI for Submersible Motors of makes Finolex / Polycab / Gold Medal / Million / Payal / Sun Light / Power Flex / Fortune Art | Civil | Labour | SWR33641 | 211 | M | 64355
31 | 76 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-28.60mm OD Pipe - SDR 11 | Civil | Labour | SWR34363 | 556 | M | 42256
32 | 36 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type - 25mm NB Size | Civil | Labour | SWR34346 | 466 | EA | 16776
33 | 1005.56 | Supplying and filling the substation site with borrowed gravel, watering, ramming, thoroughly complying with the standard specification. | Civil | Labour | SWR33052 | 651 | M3 | 654619.56
34 | 3.56 | D) RCC M20 Grade Roof Beams landing beam 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33121 | 13625 | M3 | 48505
35 | 0.62 | e)RCC M20 Grade Lintels 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33107 | 14402 | M3 | 8929.24
36 | 2.7 | f) RCC M20 Grade Sunshades 600mm wide and 75mm thick'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33114 | 1506 | M2 | 4066.2
37 | 21.72 | g) RCC M20 Grade Roof Slab for Control Room 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33128 | 13043 | M3 | 283293.96
38 | 85.68 | Providing Structural steel tube box type 60x40x4mm thick including cost and conveyance of all materials, labour charges,curing etc. complete for finished item of work and as directed by the engineer-in-charge. | Civil | Labour | SWR33146 | 148 | KG | 12680.64
39 | 18 | Providing Roofing with Trapezoidal/Galvalume Sheet including cost and conveyance of all materials, labour charges,curing etc. complete for finished item of work and as directed by the engineer-in-charge. | Civil | Labour | SWR33402 | 604 | M2 | 10872
40 | 19.8 | Providing Design R.C. drop wall of 25mm thickness with cm 1:3 and 6mm dia MS bars at 150mm both ways and chicken mesh in two coats 20mm thick each plastering including cost and conveyance of all materials with leads and lifts, scaffolding and curing, labo | Civil | Labour | SWR33203 | 3234 | M2 | 64033.2
41 | 12.24 | Supply and fixing of Ms ornamental safety grill of approved design including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33310 | 2985 | M2 | 36536.4
42 | 9.06 | Supply and fixing of doors with the frames of the door shall be made well seasoned mt wood of cross section 100x75mm. The shutter shall be made isi mark flushed door with decolam sheets pasted on both sides with PVC beading 40mm width all round.Frame shall be painted with two coats of synthetic enamel paint of approved color over one coat of primer over luppum with spary with 3 no 150mm brass hinges 1 no brass door stoper, 1 no 250mm brass aldrops. 2 no 300 mm aluminium tower bolts, 2 no 150mm brass fancy door handlers, 1 no keyless lockset with cp handel. The quoted rate shall include cost and conveyance of the meterials, fixig, labour carges, tools, handles,locking arrangementts and other fixtures & fittings for finished item work as directed by the Engineer - in- charge. | Civil | Labour | SWR33264 | 7415 | M2 | 67179.9
43 | 128.25 | Raised pointing to the exposed surfaces of CRS masonry in cm 1:3 prop. including cost and conveyance of all materials, labour charges, all leads and lifts curing etc, complete for finished item of work. | Civil | Labour | SWR33184 | 131 | M2 | 16800.75
44 | 8.64 | Supplying and fixing Aluminium sliding windows with grill and fixed glass panels using anodised aluminium extruded sections of mat finish for frames and mullions made from approved aluminium sections 62x32x1.2mm at 0.73kg/Rm providing 5mm plain glass fix | Civil | Labour | SWR33277 | 3673 | M2 | 31734.72
45 | 39.19 | Supply and laying of Ceramic floor over of CM 1:3 20 mm thick including required materials and labour charges etc complete for item of work | Civil | Labour | SWR33224 | 950 | M2 | 37230.5
46 | 121.92 | Flooring with double machine polished and hand cut Tandur blue stone 20mm thick of approved colour, quality and of minimum of 300x300mm size over a bed of cement mortar 1:3 20mm thick including cost of all materials, with all leads and lifts jointing and | Civil | Labour | SWR33219 | 677 | M2 | 82539.84
47 | 6.74 | Supply and fixing of 4" high skirting of shabad stone to the walls including cost and conveyance of all materials, labour etc for finished item of work. | Civil | Labour | SWR33236 | 772 | M2 | 5203.28
48 | 243.69 | Painting with two coats of OBD over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials labour charges etc., complete for finished item of work. | Civil | Labour | SWR33333 | 154 | M2 | 37528.26
49 | 167.67 | Providing impervious coat over RCC roof slab to requried slopes with 20mm thick in CM 1:3 mixed with approved brand of water proffing compound inclding cost and conveyance of all materials, labour charges, curing, rounding off junctions of wall and slab, all leads and lifts, etc . complete for finished item of work as directed by the Engineer - in - charge. | Civil | Labour | SWR33156 | 616 | M2 | 103284.72
50 | 81 | Supply & Spreading 40 mm metal for WBM road including cost and convenience of labor charges etc complete finshed item of work | Civil | Labour | SWR33056 | 1741 | M3 | 141021
51 | 35 | Supply and fixing 25mm dia 1.5mm thick recessed( concealed) PVC pipe alog with reinforcement to be laid in slab including No 14 SWG GI wire for earth contunity, cost of pipe, binding wire and all labour charges etc complete | Civil | Labour | SWR33441 | 114 | M | 3990
52 | 15 | Wiring with Modular Switch LP,FP,EFP for NRBuildPVC insulated flexiable copper cable in the existing metalic/Non metalic conduit pipe with 6A mini modular SP switch, mounted on metalic box covereds with appropriate front plate modules etc ceiling rose including cot and conveyance of all mateials, labour charges complete for light points, bell points and fan points in non residential builsing except circuit moving finished in all types masonary as directed by department. | Civil | Labour | SWR33457 | 703 | EA | 10545
53 | 31 | Supply and fixing 32mm dia 2mm thick ( concealed) PVC pipe in the wall including No 14 SWG GI wire for earth contunity, cost of pipe, binding wire and all labour charges etc complete for finished item of work. | Civil | Labour | SWR33442 | 105 | M | 3255
54 | 22 | Supply and fixing of 6A 3/2 pin flush type plug socket with 6A flush type marked switch control on a common board with earth continuity including wire leads earth connections along with all labour charges etc. complete | Civil | Labour | SWR33462 | 333 | EA | 7326
55 | 12 | Supply and fixing of 16A 3pin flush type plug socket and 16A flush type fuse unit and 16A switch control. | Civil | Labour | SWR33464 | 532 | EA | 6384
56 | 8 | Supply and fixing of Batten holders with 100W bulb with all connections and labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Civil | Labour | SWR33484 | 146 | EA | 1168
57 | 12 | Supply and fixing of patty type tube light fitting with 4' 0" - 40W tube light,40W copper choke,starter,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Civil | Labour | SWR33543 | 780 | EA | 9360
58 | 120 | Supply and run of 2 of 22/0.3 (1.5sqmm) pvc insulated flexible copper cable in the existing metalic/non-metalic conduit pipe. | Civil | Labour | SWR33496 | 78 | M | 9360
59 | 180 | Supply and run of 2 of 36/0.3 (2.5sqmm) pvc insulated flexible copper cable in the existing metalic/non-metalic conduit pipe. | Civil | Labour | SWR33497 | 108 | M | 19440
60 | 1 | Providing independent earthing for main switches,IC cutouts and motors using 40mm. Dia. B-class G.I.Pipe of 2.5' length duly providing 12mm. Dia. 6No. Holes and required bolts,nuts and washers,including filling with equal preparation of salt and charcoal in layers and labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Civil | Labour | SWR33596 | 5407 | EA | 5407
61 | 3 | Supply and Fixing of 48" ceiling fan of bajaj make(or equivalent make) including cost material,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Civil | Labour | SWR33563 | 2290 | EA | 6870
62 | 1 | S&F Orissa Pan WC 580mmx440mm of Parry, Neycer or Hindhusthan, make with 'P' or 'S' trap etc complete for finished item of work and as directed by the engineer-in-charge. | Civil | Labour | swr34311 | 2428 | EA | 2428
63 | 1 | Supply and fixing of European Water Closet of first quality conforming IS2556-part-21973 of Parry, Neycer or Hindhusthan, make with 'P' or 'S' trap etc,white glazed complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | swr34314 | 2257 | EA | 2257
64 | 1 | PVC low level system parry ware , slim line with internal components & short ben 10 liters capacity dual flush including cost and conveyance of all materials and labour charges for finished item of work | Civil | Labour | swr34376 | 2048.4 | EA | 2048.4
65 | 2 | Supply and Fixing 4" PVC floor trap including labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Civil | Labour | SWR34386 | 269 | EA | 538
66 | 5 | Supply,fixing 4" dia. PVC Plain Bend including cost etc. complete for finished item of work and as directed by the engineer-in-charge. | Civil | Labour | SWR34380 | 100 | EA | 500
67 | 5 | Supply,fixing 4" dia. PVC Door Bend including cost etc. complete for finished item of work and as directed by the engineer-in-charge. | Civil | Labour | SWR34381 | 128 | EA | 640
68 | 1 | S&Fixing 150mm x 100mm SWG gully traps Ist class grating & constg brick masonry in CM (1:6) prop inter mediate chamber and fitted with CI frame etc complete. | Civil | Labour | SWR34286 | 768.2 | EA | 768.2
69 | 10 | Supply and Fixing 4" dia 3M Single socket PVC pipe including labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Civil | Labour | SWR34377 | 470 | M | 4700
70 | 10 | Supply and Fixing 90mm dia 3M Single socket PVC pipe including labour charges etc. complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR34378 | 418.33 | M | 4183.3
71 | 3 | Supply,laying and jointing 152.4 mm SWG pipe including excavation of trenches etc. complete for finished item of work and as directed by the engineer-in-charge. | Civil | Labour | SWR34284 | 918 | M | 2754
72 | 1 | Constructing 3'x 3' Brick in CM(1:6) prop Masonry inspection chamber and fitted with light weight CI frame and cover etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR34297 | 4610 | EA | 4610
73 | 50 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)- 15.90mm OD Pipe - SDR 11 | Civil | Labour | SWR34361 | 385 | M | 19250
74 | 340 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-22.20mm OD Pipe - SDR 11 | Civil | Labour | SWR34362 | 459 | M | 156060
75 | 50 | Supply and fixing of 15mm dia. GM Ball valve including labour charges complete for finished item of work and as directed by the engineer-in-charge. | Civil | Labour | SWR34344 | 230 | EA | 11500
76 | 5 | Supply and fixing of 20mm dia. GM Ball valve including labour charges complete for finished item of work and as directed by the engineer-in-charge. | Civil | Labour | SWR34345 | 331 | EA | 1655
77 | 5 | Supply and fixing of 12.7mm bib tap Indian make including labour charges complete for finished item of work and as directed by the engineer-in-charge. | Civil | Labour | SWR34329 | 304 | EA | 1520
78 | 10 | Supply and fixing of 12.7mm dia. concealed stop cock including labour charges complete for finished item of work and as directed by the engineer-in-charge. | Civil | Labour | SWR34328 | 730 | EA | 7300
79 | 1000 | Providing and placing on Terrace polyetheylene water storage tank with double layer approved brand and manufacture with cover complete for finished item of work and as directed by the engineer-in-charge. | Civil | Labour | SWR34375 | 10 | L | 10000
80 | 3 | Supply and fixing of Glow sign board of size 10' x 3' including lettering,labour charges,fitting charges complete for finished item of work and as directed by the engineer-in-charge. | Civil | Labour | SWR33422 | 3730 | M2 | 11190
81 | 1 | Providing supply of electricity to the site premises through customer service centre duly applying for new connection including application fee and other missalaneous charges prescribed by APCPDCL complete for the finished item of work. | Civil | Labour | SWR33425 | 5678 | EA | 5678
82 | 2400 | Provd 2Sets of Structural Drawings | Civil | Labour | SWR33426 | 5 | FT2 | 12000
83 | 2 | Providing consultancy services for arranging contour surveying with total station including preparation of boundary and contour levels with 2 No.s hard copies and soft copies complete for finished items of work. | Civil | Labour | SWR33427 | 5850 | EA | 11700
84 | 1 | Supplying & Fixing Indian make Flat Back Wash Hand Basin (HSW/Parryware/ Neycer) 1st quality conforming to IS:2556-Part-4:1972 with waste fittings like rubber plug, chain, 32 mm nominal size C.P. Fitting with parallel pipe thread conforming to IS:2963-1979 and fitted with 15 mm nominal bore Chromium Plated Pillar Tap of 1st quality Indian make 400 grams Seiko/ Senior/ Nice/ Esso or equivalent complete with standard CI brackets including wooden block: 550 x 400 mm - Single C.P. Pillar cock | Civil | Labour | SWR34316 | 1765 | EA | 1765
85 | 6 | Supply & fixing 38.1 mm C.P waste coupling Half or Full Thread 1st Quality Indian make Parryware or equivalent | Civil | Labour | SWR34428 | 318 | EA | 1908
86 | 2 | Supply & fixing of 4" (101.6 mm ) Nahany Trap ( Without Jali with inlet)UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34387 | 134 | EA | 268
87 | 2 | S&F 76.2mm Nahany Trap with Jali | Civil | Labour | SWR34388 | 122 | EA | 244
88 | 1 | SBC Test will be done by OU/JNTU 3Samples including mobilization and Demobilization of drill equipment, lab testing of bore hole samples, preperation of technical report etc., | Civil | Labour | SWR34099 | 46000 | EA | 46000
89 | 1 | Supply & fixing 8wySPNDB IP-42,10kA-6-32A SPMCB 6Nos. MCBs as out going including internal connection and labour charges for surface / flush mounting etc Complete. | Civil | Labour | SWR33523 | 6518 | EA | 6518
90 | 36 | Plain Cement concrete (1:3:6) using 40mm HBG metal for foundations and leveling course, including cost and conveyance of all materials, labour all leads and lifts, consolidation and all operations, formwork as required, curing, etc. complete for finished item w | Civil | Labour | SWR33029 | 5848 | M3 | 210528
91 | 144 | Supply&Fabrication and fixing of Welded wire mesh ( 2" x 2") of 3mm dia. with ISMC (75x40x4.4mm) and Pheriperal frame of ISA(35x35x3mm) incldg cost& conveyance painting with synthetic enamil paint two coats over a coat of red oxide primer etc complete for finished item of work.. | Civil | Labour | SWR33403 | 2451 | M2 | 352944
92 | 591.17 | Seigniorage Charges - Sand | Civil | Labour | SWR34470 | 40 | M3 | 23646.8
93 | 1465.96 | Seigniorage Charges - Metal | Civil | Labour | SWR34471 | 97.5 | M3 | 142931.1
94 | 218.06 | Seigniorage Charges - Gravel | Civil | Labour | SWR34472 | 30 | M3 | 6541.8
|  | Total Rs. | [5 empty] | 8369460.54
|  | GST 18% Rs. | [5 empty] | 1506502.8972
|  | Grand Total Rs. | [5 empty] | 9875963.4372
[5 empty] | Total Civil + Electrical without GST |  |  | 52162346.306
[5 empty] | Total Civil + Electrical with GST |  |  | 61551568.641

## Sheet2
3 | 3
5 | 5
3 | 3
0.78 | 0.78
1 | 1
1 | 1
1 | 1
1 | 1
0.78 | 0.78
0.78 | 0.78
0.78 | 0.78
0.38 | 0.38
0.38 | 0.38
0.38 | 0.38
0.38 | 0.38
0.38 | 0.38
0.38 | 0.38
1 | 1
1 | 1
2 | 2
1 | 1
2 | 2
2 | 2
2 | 2
2 | 2
3 | 3
3 | 3
1 | 1
2.52 | 2.52
200 | 200
85.1 | 85.1
6 | 6
1 | 1
1 | 1
1 | 1
1 | 1
0.24 | 0.24
1 | 1
12 | 12
18 | 18
3 | 3
100 | 100
40 | 40
1800 | 1800
1 | 1
1 | 1
2 | 2
2 | 2
2 | 2
2.1 | 2.1
2 | 2
2 | 2
24 | 24
60 | 60
2 | 2
12 | 12
10.8 | 10.8
2.7 | 2.7
16.2 | 16.2
63 | 63
6 | 6
40 | 40
12 | 12
100 | 100
4.9 | 4.9
0.31 | 0.31
0.56 | 0.56
2.03 | 2.03
0.1 | 0.1
0.5 | 0.5
1.31 | 1.31
2.67 | 2.67
5 | 5

## Sheet3
9875963.44
205799764.11
215675727.55