## O.H to UG at Syed Nagar
SCHEDULE
Name of the work: “Conversion of 33KV O.H line to UG cable for 33KV Jubilee Hills-Asifnagr Ckt-I & II DCOH line which is passing over the consumers houses from Syed nagar-2 to Ahmed Nagar ” under T& D Improvement works in Subdivision-VI of Master Plan-I Division
WBS Element No:T-2580-12-01-03-01-002
Electrical Portion
SNo | S No. | Estimate Quantity (only FigurEs) | Item Detailed Specification Description | Work Type | Item Short Descripti | Service Code | Rate | UOM | Amount
| 1 | 0.56 | survey line&cabl inc peg mark&tree clear | Electrical | Labour | SWR22092 | 765 | KM | 428.4
| 2 | 4 | Loading of 11KV/33KV XLPE UG Cable Drum for all sizes | Electrical | Labour | SWR11230 | 1024 | DR | 4096
| 3 | 3 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Upto 10 Km with Lorry for each trip | Electrical | Labour | SWR11860 | 2720.34 | EA | 8161.02
| 4 | 4 | Un loading of 11KV/33KV XLPE UG Cable Drum for all sizes | Electrical | Labour | SWR11231 | 1024 | DR | 4096
| 5 | 444 | Laying of XLPE UG cable Double including excavation of trench of size 600mm wide to 1200mm wide as per the site conditions and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second,third or more cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. Along the CC / BT multi layer road requiring compressor 33 KV 3x400 Sqmm Cable | Electrical | Labour | SWR11980 | 1388.84 | M | 616644.96
| 6 | 120 | Laying of XLPE UG cable Double including excavation of trench of size 600mm wide to 1200mm wide as per the site conditions and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second,third or more cable laying cost notIncluded) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. Across the CC/ BT road crossing multi layer road requiring compressor (excluding the cost of Hume pipe) 33 KV 3x400 Sqmm Cable | Electrical | Labour | SWR11988 | 1587 | M | 190440
| 7 | 564 | Laying of 2nd cable in excavated trench | Electrical | Labour | SWR10988 | 204 | M | 115056
| 8 | 72 | Raising of Single run 33KV 3x400sqmm UG cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Electrical | Labour | SWR11954 | 135.66 | M | 9767.52
| 9 | 7 | Supply & Erecton of Smart RFID marker | Electrical | Labour | SWR25089 | 2745 | EA | 19215
| 10 | 6 | Making of 33KV 3X400Sq.mm XLPE UG Cable Straight through joints | Electrical | Labour | SWR10382 | 5700.78 | EA | 34204.68
| 11 | 80 | Supply of 6" B Class GI pipe 5mm thck 20Kg/M | Electrical | Supply | SMR40081 | 1344 | M | 107520
| 12 | 50 | supply of 6" DWC pipe | Electrical | Supply | SMR11610 | 1012 | M | 50600
| 13 | 100 | Supply of Hume Pipe Size 9" size | Electrical | Supply | SMR40001 | 125 | M | 12500
| 14 | 4 | Making of 33KV 3X400Sq.mm XLPE UG Cable Outdoor/Indoor End Termination | Electrical | Labour | SWR10387 | 2764.76 | EA | 11059.04
| 15 | 564 | Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours. | Electrical | Labour | SWR21903 | 30 | M | 16920
| 16 | 1 | Submission of auto CAD Drawing as per pole schedule (Detailed survey and sketch) Up to 10 km | Electrical | Labour | SWR12104 | 6000 | LS | 6000
| 17 | 7 | Supply of Pre-cast cable Joint markersSupply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters , CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | Electrical | Supply | SMR40085 | 484 | EA | 3388
| 18 | 4 | Painting of feeder name on support including cost of paint | Electrical | Labour | SWR12101 | 53 | KG | 212
| 19 | 1 | Supply of M+3 Tower (Galvanized) | Electrical | Supply | SMR11683 | 140674 | EA | 140674
| 20 | 1 | Erection of M+3 Tower (Galvanized) | Electrical | Labour | SWR11850 | 64576 | EA | 64576
| 21 | 1 | Excavation of pits in hard rock requiring blasting. (other than SS) M-Type Tower (1.2M x 1.2M x 3.3M ) 4.752cum | Electrical | Labour | SWR12093 | 4810.58 | EA | 4810.58
| 22 | 6 | Dismantling of Damaged Poles, not required and available in the middle of roads, transporting to stock point etc.Dismantle-RS Joists 175 x 75mm | Electrical | Labour | SWR11325 | 1116 | EA | 6696
| 23 | 0.45 | Dismantling of Line-Dismantling of 100 Sqmm Conductor DC | Electrical | Labour | SWR22064 | 11816.71 | KM | 5317.5195
| 24 | 0.438 | LOADING of ACSR conductor scrap | Electrical | Labour | SWR10257 | 491.01 | TO | 215.0624
| 25 | 0.438 | UNLOADING of ACSR conductor scrap | Electrical | Labour | SWR10575 | 491 | TO | 215.058
| 26 | 0.576 | LOADING of MS Scrap | Electrical | Labour | SWR10258 | 578 | TO | 332.928
| 27 | 0.576 | UNLOADING of MS Scrap | Electrical | Labour | SWR10576 | 578 | TO | 332.928
| 28 | 1.014 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel,iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) -Above 10 KM and upto 20 KM | Electrical | Labour | SWR10132 | 412.08 | TO | 417.8491
|  |  | Total | [5 empty] | 1433896.545 | 1433896.545
|  |  | 18% GST | [5 empty] | 258101.3781
| Total Cost (With 18 % GST)=Electrical | [7 empty] | 1691997.9231

## SD6 SS Schedule (hidden)
SCHEDULE
Name of the work: Erection, testing and commissioning of 33/11KV Indoor Sub Station with 2x 8MVA PTRs at Road No.10,Zaheera Nagar , BanjaraHills Operation Division, Kairathabad Constituency in SD-IV, Div-1,Masterplan, Hyderabad Circle under T&D Improvement works.
WBS No: S-1750-12-01-01-01-001 (Electrical)
Electrical Portion
SNo | S No. | Estimate Quantity (only FigurEs) | Item Detailed Specification Description | Work Type | Item Short Descripti | Service Code | Rate | UOM | Amount
| 1 | 2 | Loading of 8MVA PTR | Electrical | Labour | SWR10613 | 5805.84 | EA | 11611.68 | SS LABOUR |  | 1
| 2 | 2 | Transport of Power transformers (0 to 100 KM) from one place to another place in GHMC Area.(excluding of loading & unloading )-8MVA power transformer | Electrical | Labour | SWR10854 | 21945 | EA | 43890 |  |  | 2
| 3 | 2 | Unloading of 8MVA PTR | Electrical | Labour | SWR10627 | 5805.84 | EA | 11611.68 |  |  | 3
| 4 | 2 | Erection of PTR on constructed plinth-Erection of 8 MVA PTR. | Electrical | Labour | SWR21321 | 49480.2 | EA | 98960.4 |  |  | 4
| 5 | 1 | Loading of 50,63, 75 & 100 KVA DTR | Electrical | Labour | SWR10195 | 350 | EA | 350 |  |  | 5
| 6 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | Electrical | Labour | SWR11861 | 3299.7 | EA | 3299.7 |  |  | 6
| 7 | 1 | Un loading of 50,63, 75 & 100 KVA DTR | Electrical | Labour | SWR10513 | 280 | EA | 280 |  |  | 7
| 8 | 1 | Construction of DTR Plinth- RCC Column type DTR Plinth of size 1'X1'X10',topslab 4'x4'x6" & beam size 4'X8'X8" upto 160KVA | Electrical | Labour | SWR21843 | 25967.57 | EA | 25967.57 |  |  | 8
| 9 | 1 | Erection of 3 Phase DTRs 63,75 & 100 KVA including loading and Unloading DTR on the Structure/Plinth etc | Electrical | Labour | SWR20905 | 1650 | EA | 1650 |  |  | 9
| 10 | 16 | Loading of 11 KV VCBs along with Panel boards | Electrical | Labour | SWR10199 | 1024 | EA | 16384 |  |  | 10
| 11 | 8 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | Electrical | Labour | SWR11861 | 3299.7 | EA | 26397.6 |  |  | 11
| 12 | 16 | Un loading of 11 KV VCBs along with Panel boards | Electrical | Labour | SWR10517 | 1044.48 | EA | 16711.68 |  |  | 12
| 13 | 16 | Erection of 11KV indoor switch gear panel/indoor PT panel /Bus section panel / Bus raiser panel/Capacitor panel/Switch fuse panel for DTR. | Electrical | Labour | SWR10931 | 8894 | EA | 142304 |  |  | 13
| 14 | 10 | Loading of 33 KV VCBs along with Panel boards | Electrical | Labour | SWR10198 | 1024 | EA | 10240 |  |  | 14
| 15 | 5 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | Electrical | Labour | SWR11861 | 3299.7 | EA | 16498.5 |  |  | 15
| 16 | 10 | Un loading of 33 KV VCBs along with Panel boards | Electrical | Labour | SWR10516 | 1044.48 | EA | 10444.8 |  |  | 16
| 17 | 10 | Erection of 33KV indoor switch gear panel/33KV indoor PT panel / Bus section panel / Bus raiser panel | Electrical | Labour | SWR10930 | 9847 | EA | 98470 |  |  | 17
| 18 | 1 | Loading of 220 V Batterry with charger | Electrical | Labour | SWR11166 | 1612 | SET | 1612 |  |  | 18
| 19 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | Electrical | Labour | SWR11861 | 3299.7 | EA | 3299.7 |  |  | 19
| 20 | 1 | Un loading of 220 V Batterry with charger | Electrical | Labour | SWR11147 | 1024 | SET | 1024 |  |  | 20
| 21 | 1 | Erection of 220 V, 80 AH battery in complete shape fit for charging . Conventional lead acid | Electrical | Labour | SWR12295 | 7666 | EA | 7666 |  |  | 21
| 22 | 1 | Supply of AC Supply panel inluding providing of changeover switch, SFU, metering unit, 32 A three phase MCB, 16 A Single phase MCB complete as per specification. | Electrical | Supply | SMR40045 | 42000 | EA | 42000 |  |  | 22
| 23 | 1 | Erection of control/Relay panels, AC Panels, announciationpanels etc in the control room duly mounting them on channels and grouting them with foundation bolts excluding cost of channels & foundation bolts | Electrical | Labour | SWR11893 | 2122 | EA | 2122 |  |  | 23
| 24 | 8 | LOADING of RSJoists150 x 150 mm/RailPole | Electrical | Labour | SWR10205 | 176 | EA | 1408 |  |  | 24
| 25 | 8 | UNLOADING of RSJoists150 x150 mm/RailPol | Electrical | Labour | SWR10523 | 107 | EA | 856 |  |  | 25
| 26 | 0.83 | LOADING of MS Channel,Angles,Flats&Rods | Electrical | Labour | SWR10206 | 221 | TO | 183.43 |  |  | 26
| 27 | 0.83 | UNLOADING of MS Channel,Angles,Flats&Rod | Electrical | Labour | SWR10524 | 185 | TO | 153.55 |  |  | 27
| 28 | 3.83 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 Km and upto 20 Km | Electrical | Labour | SWR10132 | 412.08 | TO | 1578.2664 |  |  | 28
| 29 | 44 | Cutting Charges for RS joist 150x150mm | Electrical | Labour | SWR10297 | 48 | EA | 2112 |  |  | 29
| 30 | 0.83 | Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Electrical | Labour | SWR10869 | 3426 | TO | 2843.58 |  |  | 30
| 31 | 3.83 | Alligning the Main and Auxiliary structures such as RS joist,M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication. | Electrical | Labour | SWR10867 | 1470 | TO | 5630.1 |  |  | 31
| 32 | 3.83 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes,labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Electrical | Supply | SMR40009 | 2181 | TO | 8353.23 |  |  | 32
| 33 | 3.83 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters ofthinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes,labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Electrical | Labour | SWR10877 | 851 | TO | 3259.33 |  |  | 33
| 34 | 3.83 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc | Electrical | Supply | SMR40010 | 1293 | TO | 4952.19 |  |  | 34
| 35 | 3.83 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium | Electrical | Labour | SWR10879 | 482 | TO | 1846.06 |  |  | 35
| 36 | 43 | Painting of Name Plates for any equipment | Electrical | Labour | SWR10963 | 122 | EA | 5246 |  |  | 36
| 37 | 36 | Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness10mm with flange as per specication | Electrical | Supply | SMR11482 | 3486 | EA | 125496 |  |  | 37
| 38 | 36 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Electrical | Labour | SWR10357 | 1234.2 | EA | 44431.2 |  |  | 38
| 39 | 36 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50M height | Electrical | Labour | SWR10359 | 386 | EA | 13896 |  |  | 39
| 40 | 3.4 | LOADING of MS Channel,Angles,Flats&Rods | Electrical | Labour | SWR10206 | 221 | TO | 751.4 |  |  | 40
| 41 | 3.4 | UNLOADING of MS Channel,Angles,Flats&Rod | Electrical | Labour | SWR10524 | 185 | TO | 629 |  |  | 41
| 42 | 3.4 | TRANSPORT OF STEEL 10 TO 20KM | Electrical | Labour | SWR10132 | 412.08 | TO | 1401.072 |  |  | 42
| 43 | 531.9 | Laying of MS Flats /GI Flats 75x 8mm earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment andconnecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes including fabrication | Electrical | Labour | SWR10920 | 65 | RMT | 34573.5 |  |  | 43
| 44 | 210 | Fabrication and connecting of M.S./ G.I. Flat 50x6mm to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. | Electrical | Labour | SWR10919 | 41 | RMT | 8610 |  |  | 44
| 45 | 50 | Supply of GI Bolts & Nuts | Electrical | Supply | SMR11488 | 117.5 | KG | 5875 |  |  | 45
| 46 | 314 | Paint-Black to all Earth Flat incl. Pain | Electrical | Labour | SWR12217 | 55 | M | 17270 |  |  | 46
| 47 | 2 | Supply of Copper Flexible jumper with 75 X 8 of length 250 mm at neutral of Power tranformer end and 50 X 6 of length 50mm two Nos at double neutral end duly brasing with flexible jumper of capacity of 5kA/3 sec for power transformer neutral | Electrical | Supply | SMR40033 | 4725 | EA | 9450 |  |  | 47
| 48 | 2 | Providing of double earthing for neutral with flexible copper jumpers including arrangement by fixing M.S.Channel 100x50mm | Electrical | Labour | SWR11892 | 1323 | EA | 2646 |  |  | 48
| 49 | 106 | Laying of 4No's single core 630 sqmm UG cable (Single Circuit with one spare cable) including excavation of trench of size 0.7 Mtrs width and 1.2 Mtrs depth from road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.Lay-4 SC 33KV 630sqmm UG Cb HG/BC/RE/NS | Electrical | Labour | SWR12110 | 2463.3 | M | 261109.8 |  |  | 49
| 50 | 56 | Raise-SR 33KV 1x630sqmm UG Cb on Support | Electrical | Labour | SWR12448 | 133 | M | 7448 |  |  | 50
| 51 | 106 | Laying of second cable 33KV UG Cb in Existing Duct | Electrical | Labour | SWR12452 | 200 | M | 21200 |  |  | 51
| 52 | 14 | Raising of single run 33kV 3x400 Sqmm Cu cable on already erected support with wooden / MS clamps and connecting it to over head line withcable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Electrical | Labour | SWR11954 | 135.66 | M | 1899.24 |  |  | 52
| 53 | 8 | Supply of 33KV 1x630Sqmm GIS ID Unit EndTermtn | Electrical | Supply | SMR12473 | 2500 | EA | 20000 |  |  | 53
| 54 | 8 | Supply of33KV 1x630Sqmm OD Unit EndTermtn | Electrical | Supply | SMR12474 | 4200 | EA | 33600 |  |  | 54
| 55 | 8 | Installation of 33KV 1x630Sqmm GIS ID EndTermtn | Electrical | Labour | SWR12473 | 17600 | EA | 140800 |  |  | 55
| 56 | 8 | Installation of 33KV 1x630Sqmm OD Unit EndTermtn | Electrical | Labour | SWR12474 | 4000 | EA | 32000 |  |  | 56
| 57 | 4 | Making of Outdoor/Indoor 33 KV 3x400 Sqmm End Termination | Electrical | Labour | SWR10387 | 2764.76 | EA | 11059.04 |  |  | 57
| 58 | 85 | Laying of XLPE UG cable Single Run including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the siteinluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders/Normal soil / CC/BT Road 11KV 3x185 Sqmm Cable | Electrical | Labour | SWR11920 | 465.46 | M | 39564.1 |  |  | 58
| 59 | 15 | Raising of Single Run 11 KV 3x185 Sqmm Cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Electrical | Labour | SWR11956 | 126.23 | M | 1893.45 |  |  | 59
| 60 | 2 | Making of Outdoor/Indoor 11 KV 3x185 Sqmm Cable End Termination | Electrical | Labour | SWR10390 | 2370.63 | EA | 4741.26 |  |  | 60
| 61 | 90 | Laying of XLPE UG cable Single Run including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders/Normal soil / CC/BT Road LT 3 1/2 x 185 Sqmm Cable | Electrical | Labour | SWR11923 | 377.63 | M | 33986.7 |  |  | 61
| 62 | 10 | Raising of Single Run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-LT 3 1/2 x 185 Sqmm Cable | Electrical | Labour | SWR11959 | 85.43 | M | 854.3 |  |  | 62
| 63 | 2 | Fixing of Oout Door/Indoor end termination LT 3 1/2 x185 Sqmm Cable | Electrical | Labour | SWR10765 | 968.9 | EA | 1937.8 |  |  | 63
| 64 | 2200 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends . | Electrical | Labour | SWR11879 | 27 | M | 59400 |  |  | 64
| 65 | 500 | Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per specification (including cost of ferrules, lugs and glands) | Electrical | Labour | SWR12510 | 27 | EA | 13500 |  |  | 65
| 66 | 6 | Loading of R.S. Joists 175 x 85 mm | Electrical | Labour | SWR10204 | 76 | EA | 456 |  |  | 66
| 67 | 1.6 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 KM and upto 20 KM | Electrical | Labour | SWR10132 | 412.08 | TO | 659.328 |  |  | 67
| 68 | 6 | UNLOADING of R.S. Joists 175 x 85 mm | Electrical | Labour | SWR10522 | 50 | EA | 300 |  |  | 68
| 69 | 1.6 | Fabrication of Main and Auxiliary structures with welding using raw steel such as RS joist, M.S.Angles, Plates, Channels, including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Electrical | Labour | SWR10869 | 3426 | TO | 5481.6 |  |  | 69
| 70 | 1.6 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Electrical | Supply | SMR40009 | 2181 | TO | 3489.6 |  |  | 70
| 71 | 1.6 | Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Electrical | Labour | SWR10877 | 851 | TO | 1361.6 |  |  | 71
| 72 | 1.6 | Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. | Electrical | Supply | SMR40010 | 1293 | TO | 2068.8 |  |  | 72
| 73 | 1.6 | Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . | Electrical | Labour | SWR10879 | 482 | TO | 771.2 |  |  | 73
| 74 | 5 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Electrical | Labour | SWR11040 | 990.68 | EA | 4953.4 |  |  | 74
| 75 | 5 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Box pole 9/10/11 Mtr | Electrical | Labour | SWR11266 | 2643.83 | EA | 13219.15 |  |  | 75
| 76 | 4.7 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.-Including the cost of cement | Electrical | Labour | SWR10356 | 6579 | M3 | 30921.3 |  |  | 76
| 77 | 0.155 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Electrical | Labour | SWR11890 | 3893.03 | M3 | 603.4197 |  |  | 77
| 78 | 5 | Paint of coping with 2 coats of white cement incl cost of paints etc. | Electrical | Labour | SWR11089 | 48 | EA | 240 |  |  | 78
| 79 | 1 | Loading of 11 KV HG Fuse Sets | Electrical | Labour | SWR10231 | 18 | EA | 18 |  |  | 79
| 80 | 1 | Un loading of 11 KV HG Fuse Sets | Electrical | Labour | SWR10549 | 18 | EA | 18 |  |  | 80
| 81 | 1 | Erection of 11 KV HG Fuse set including earthing | Electrical | Labour | SWR10395 | 740.52 | SET | 740.52 |  |  | 81
| 82 | 1 | Loading of 11 KV AB SWCH T.T.200/400 A | Electrical | Labour | SWR12406 | 80 | EA | 80 |  |  | 82
| 83 | 1 | Un loading of 11 KV AB SWCH T.T.200/400 A | Electrical | Labour | SWR12425 | 80 | EA | 80 |  |  | 83
| 84 | 1 | Erection of 11KV 200A TT type AB Switch including fixing of cross angles and alignment complete | Electrical | Labour | SWR20102 | 1813.49 | EA | 1813.49 |  |  | 84
| 85 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.-Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Electrical | Labour | SWR10881 | 142 | EA | 142 |  |  | 85
| 86 | 1 | Erection of LT distribution box including laying of LT cable from distribution box to LT OH line and DTR to distribution box including earthing of distribution box and crimping of lugs connecting of jumpers etc | Electrical | Labour | SWR10674 | 1594.67 | EA | 1594.67 |  |  | 86
| 87 | 18 | Supply of earthing pipe with materials GI Flat 25X3 mm | Electrical | Supply | SMR11485 | 105 | KG | 1890 |  |  | 87
| 88 | 30 | Running of GI eartn flat of size 25X3mm from all metallic parts of channels, AB Switch, HG fuse set, DTr neutral and LT Distribution box and inter connection of earth pits etc complete. | Electrical | Labour | SWR12125 | 14.03 | M | 420.9 |  |  | 88
| 89 | 2 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Electrical | Labour | SWR11230 | 1024 | DR | 2048 |  |  | 89
| 90 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | Electrical | Labour | SWR11861 | 3299.7 | EA | 3299.7 |  |  | 90
| 91 | 2 | Un loading of 11KV/33KV XLPE UG Cable for all sizes | Electrical | Labour | SWR11231 | 1024 | DR | 2048 |  |  | 91
| 92 | 8 | Supply of stepped tubular poles single way made of steel of length 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9 mm, 2.1 mtrs with outer dia 76.1 mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79 kgf as per IS 2713. | Electrical | Supply | SMR40051 | 13913 | EA | 111304 |  |  | 92
| 93 | 8 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Electrical | Labour | SWR11039 | 928 | EA | 7424 |  |  | 93
| 94 | 8 | Erection of tubular poles | Electrical | Labour | SWR10955 | 1379 | EA | 11032 |  |  | 94
| 95 | 6.1 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.-Including the cost of cement | Electrical | Labour | SWR10356 | 6579 | M3 | 40131.9 |  |  | 95
| 96 | 0.248 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Electrical | Labour | SWR11890 | 3892.98 | M3 | 965.459 |  |  | 96
| 97 | 8 | Paint of coping with 2 coats of white cement incl cost of paints etc. | Electrical | Labour | SWR11089 | 48 | EA | 384 |  |  | 97
| 98 | 8 | Supply of Metal Handle Lamp 150W | Electrical | Supply | SMR24635 | 6450 | EA | 51600 |  |  | 98
| 99 | 50 | Supply of GI Bolts & Nuts,washers etc. | Electrical | Supply | SMR11488 | 117.5 | KG | 5875 |  |  | 99
| 100 | 8 | Fixing of Metal halide lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5 GI pipe complete. | Electrical | Labour | SWR10956 | 1268 | EA | 10144 |  |  | 100
| 101 | 1 | Supply of Steel almarah(61/2 X 3ft) Godrej | Electrical | Supply | SMR40061 | 9818 | EA | 9818 |  |  | 101
| 102 | 750 | Supplying & fabrication erection of 6mm Checkerd plates as per the field conditions | Electrical | Labour | SWR10873 | 83 | KG | 62250 |  |  | 102
| 103 | 12 | Supply of Rubber mats ( 6’x3’) size for indoor SS | Electrical | Supply | SMR40068 | 1386 | EA | 16632 |  |  | 103
| 104 | 1 | Supply of Alluminium Ladder for indoor works | Electrical | Supply | SMR40062 | 4410 | EA | 4410 |  |  | 104
| 105 | 2 | Supply of Trolley mounted CO2 (6.5Kgs)(IS-2878) | Electrical | Supply | SMR40087 | 9240 | EA | 18480 |  |  | 105
| 106 | 2 | Supply of Fire Buckets Stand with Buckets | Electrical | Supply | SMR40088 | 1386 | SET | 2772 |  |  | 106
| 107 | 6 | Supply of Fire Extinguisher for Control Room | Electrical | Supply | SMR40089 | 4620 | EA | 27720 |  |  | 107
| 108 | 4 | Supply of Safety Helmet of standard make | Electrical | Supply | SMR40071 | 231 | EA | 924 |  |  | 108
| 109 | 4 | Supply of Earth Rods (8ft) Screw & clamp type | Electrical | Supply | SMR40066 | 578 | EA | 2312 |  |  | 109
| 110 | 4 | Supply of Hand Gloves | Electrical | Supply | SMR40067 | 289 | SET | 1156 |  |  | 110
| 111 | 1 | Supply of Stand basic cell phone with charger | Electrical | Supply | SMR40069 | 1386 | EA | 1386 |  |  | 111
| 112 | 1 | Supply of Table (3x6ft) Godrej | Electrical | Supply | SMR40057 | 6050 | EA | 6050 |  |  | 112
| 113 | 4 | Supply of S type chairs (Godrej) | Electrical | Supply | SMR40058 | 924 | EA | 3696 |  |  | 113
| 114 | 1 | Supply of Angle racks(18x36.6inches) Godrej | Electrical | Supply | SMR40060 | 1733 | EA | 1733 |  |  | 114
| 115 | 10 | Supply of Danger boards with clamps | Electrical | Supply | SMR40070 | 116 | EA | 1160 |  |  | 115
| 116 | 1 | Supply of 33/11kv S.S Permanent name board | Electrical | Supply | SMR40086 | 10238 | EA | 10238 |  |  | 116
| 117 | 1 | Supply of Wall clock standard make | Electrical | Supply | SMR40059 | 578 | EA | 578 |  |  | 117
| 118 | 1 | Supply of Taparia Tool kit complete as per Spec | Electrical | Supply | SMR40063 | 4925 | SET | 4925 |  |  | 118
| 119 | 1 | Supply of Rechargeable LED torch light. | Electrical | Supply | SMR40064 | 1733 | EA | 1733 |  |  | 119
| 120 | 1 | Supply of Hack saw (12 inches) | Electrical | Supply | SMR40065 | 289 | EA | 289 |  |  | 120
| 121 | 8 | Supply of LC Boards | Electrical | Supply | SMR40072 | 116 | EA | 928 |  |  | 121
| 122 | 2 | Supply of Gum Boots | Electrical | Supply | SMR40073 | 693 | EA | 1386 |  |  | 122
| 123 | 1 | Supply of Digital clamp meter. | Electrical | Supply | SMR40076 | 2888 | EA | 2888 |  |  | 123
| 124 | 1 | Supply of 5000v megger | Electrical | Supply | SMR40074 | 13860 | EA | 13860 |  |  | 124
| 125 | 1 | Supply &fixing of board ind Switchyard layout | Electrical | Labour | SWR20032 | 1654 | EA | 1654 |  |  | 125
| 126 | 1 | Supply &fixing safety inst/SS Op. inst board | Electrical | Labour | SWR22090 | 2205 | EA | 2205 |  |  | 126
| 127 | 1 | Supply of 10ft Aluminium Ladder | Electrical | Supply | SMR12378 | 1654 | EA | 1654 |  |  | 127 | 2101655.9451
| 128 | 1 | survey line&cabl inc peg mark&tree clear | Electrical | Labour | SWR22092 | 765 | KM | 765 | 33KV LINE MATERIAL |  | 1
| 129 | 29 | Load-11/33KV XLPE UG Cable for all sizes | Electrical | Labour | SWR11230 | 1024 | DR | 29696 |  |  | 2
| 130 | 29 | Unload-11/33KV XLPE UG Cable all sizes | Electrical | Labour | SWR11231 | 1024 | DR | 29696 |  |  | 3
| 131 | 15 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Upto 10 Km with Lorry for each trip | Electrical | Labour | SWR11860 | 2720.34 | EA | 40805.1 |  |  | 4
| 132 | 4350 | Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters,providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts,Along the CC / BT multi layer road requiring compressor for 33 KV 3x400 Sqmm Cable | Electrical | Labour | SWR11980 | 1388.84 | M | 6041454 |  |  | 5
| 133 | 4350 | Laying of 2nd cable in excavated trench | Electrical | Labour | SWR10988 | 204.1 | M | 887835 |  |  | 6
| 134 | 44 | Supply & Erection of Smart RFID marker | Electrical | Labour | SWR25089 | 2745 | EA | 120780 |  |  | 7
| 135 | 35 | Making of Straight through joint 33kv 3x400 xlpe | Electrical | Labour | SWR10382 | 5700.78 | EA | 199527.3 |  |  | 8
| 136 | 1756 | Supply of 6" B class GI pipe | Electrical | Supply | SMR40081 | 1044 | M | 1833264 |  |  | 9
| 137 | 100 | Supply of 6" DWC pipe | Electrical | Supply | SMR11610 | 1012 | M | 101200 |  |  | 10
| 138 | 100 | Supply of Hume pipe 9" size | Electrical | Supply | SMR40001 | 125 | M | 12500 |  |  | 11
| 139 | 10 | Making of OD/Idoor end termination 33kv 3x400 xlpe | Electrical | Labour | SWR10387 | 2764.76 | EA | 27647.6 |  |  | 12
| 140 | 80 | Raising of single run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) 33KV 3x400sqmm UG Cb on support | Electrical | Labour | SWR11954 | 135.66 | M | 10852.8 |  |  | 13
| 141 | 4350 | Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours. | Electrical | Labour | SWR21903 | 30 | M | 130500 |  |  | 14
| 142 | 1.1 | LOADING of MS Channel,Angles,Flats&Rods | Electrical | Labour | SWR10206 | 221 | TO | 243.1 |  |  | 15
| 143 | 1.1 | UNLOADING of MS Channel,Angles,Flats&Rod | Electrical | Labour | SWR10524 | 185 | TO | 203.5 |  |  | 16
| 144 | 12 | LOADING of R.S. Joists 175 x 85 mm | Electrical | Labour | SWR10204 | 76 | EA | 912 |  |  | 17
| 145 | 12 | UNLOADING of R.S. Joists 175 x 85 mm | Electrical | Labour | SWR10522 | 50 | EA | 600 |  |  | 18
| 146 | 12 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Electrical | Labour | SWR10642 | 512.55 | EA | 6150.6 |  |  | 19
| 147 | 4.1 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 KM and upto 20 KM | Electrical | Labour | SWR10132 | 412.08 | TO | 1689.528 |  |  | 20
| 148 | 12 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Electrical | Labour | SWR10640 | 1132 | EA | 13584 |  |  | 21
| 149 | 6 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Electrical | Labour | SWR11040 | 990.68 | EA | 5944.08 |  |  | 22
| 150 | 2 | Erection of 9/10/11Meter Box pole | Electrical | Labour | SWR11266 | 2643.83 | EA | 5287.66 |  |  | 23
| 151 | 208.3 | Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc.M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) | Electrical | Labour | SWR10919 | 41 | RMT | 8540.3 |  |  | 24
| 152 | 5.64 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.Including the cost of cement | Electrical | Labour | SWR10356 | 6579 | M3 | 37105.56 |  |  | 25
| 153 | 0.186 | Coping & Muffing-Iron Pole,Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Electrical | Labour | SWR11890 | 3893.01 | M3 | 724.0999 |  |  | 26
| 154 | 0.6 | Fabrication of Main and Auxiliary structures with welding using raw steel such as RS joist, M.S.Angles, Plates, Channels, including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Electrical | Labour | SWR10869 | 3426 | TO | 2055.6 |  |  | 27
| 155 | 2 | Erection of 33 KV LAS station/Line type including earthing | Electrical | Labour | SWR10396 | 880 | SET | 1760 |  |  | 28
| 156 | 2 | LOADING of 33 KV AB SWCH Con 400/800 A | Electrical | Labour | SWR10239 | 126 | EA | 252 |  |  | 29
| 157 | 2 | UNLOADING of 33 KV AB SWCH Con 400/800 A | Electrical | Labour | SWR10557 | 79 | EA | 158 |  |  | 30
| 158 | 2 | Erection of 33 KV AB Switch including alignment and earthing | Electrical | Labour | SWR10392 | 4500 | EA | 9000 |  |  | 31
| 159 | 6 | S-CI Pipe earthing 80mm dia 2.75m long | Electrical | Supply | SMR11483 | 2789 | EA | 16734 |  |  | 32
| 160 | 6 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and | Electrical | Labour | SWR10357 | 1234.2 | EA | 7405.2 |  |  | 33
| 161 | 6 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Electrical | Labour | SWR10359 | 386 | EA | 2316 |  |  | 34
| 162 | 44 | Supply of Pre-cast cable Joint markersSupply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters , CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | Electrical | Supply | SMR40085 | 484 | EA | 21296 |  |  | 35
| 163 | 6 | Painting of feeder name on support including cost of paint | Electrical | Labour | SWR12101 | 53 | EA | 318 |  |  | 36
| 164 | 100 | Supply of GI Bolts & Nuts,Washers etc., | Electrical | Supply | SMR11488 | 117.5 | KG | 11750 |  |  | 37
| 165 | 2 | 33 KV DP Structure with 175x85/150x75mm RS joist Assembly and erection of Structure as per specification which includes fixing of top channels and cross bracings, transport of all materials from road side to the location, earthing, back filling with earth ramming etc excluding pit excavation and concreting. | Electrical | Labour | SWR11276 | 5670 | SET | 11340
| 166 | 6 | Loading of 33 KV, 10 KA LAs Station type | Electrical | Labour | SWR10266 | 41 | EA | 246
| 167 | 6 | Un loading of 33 KV, 10 KA LAs Station type | Electrical | Labour | SWR10584 | 35 | EA | 210
| 168 | 2 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Electrical | Labour | SWR12331 | 146.63 | EA | 293.26
| 169 | 2 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Electrical | Labour | SWR10881 | 142 | EA | 284
| 170 | 1 | Survey line&cabl inc peg mark&tree clear | Electrical | Labour | SWR22092 | 765 | KM | 765 | 11KV LINE LABOUR |  | 1 | 9632925.29
| 171 | 14 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Electrical | Labour | SWR11230 | 1024 | DR | 14336 |  |  | 2
| 172 | 14 | Un loading of 11KV/33KV XLPE UG Cable for all sizes | Electrical | Labour | SWR11231 | 1024 | DR | 14336 |  |  | 3
| 173 | 7 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Above 10 Km and upto 20 Km with Lorry for each trip | Electrical | Labour | SWR11861 | 3299.7 | EA | 23097.9 |  |  | 4
| 174 | 4200 | Laying of Single Run XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions ofEngineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.Along the CC / BT multi layer road requiring compressor for 11 KV 3x300 Sqmm Cable | Electrical | Labour | SWR11928 | 1073.94 | M | 4510548 |  |  | 5
| 175 | 80 | Raising of Single Run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)11 KV 3x300 Sqmm Cable | Electrical | Labour | SWR11955 | 144.08 | M | 11526.4 |  |  | 6
| 176 | 43 | Supply & Erecting of Smart RFID marker | Electrical | Labour | SWR25089 | 2745 | EA | 118035 |  |  | 7
| 177 | 20 | Making of Straight through joint 11kv 3x300 xlpe | Electrical | Labour | SWR10386 | 3725.45 | EA | 74509 |  |  | 8
| 178 | 856 | Supply of 4" B class GI pipe | Electrical | Supply | SMR40080 | 740 | M | 633440 |  |  | 9
| 179 | 100 | supply of 4" DWC pipe | Electrical | Supply | SMR11609 | 759 | M | 75900 |  |  | 10
| 180 | 200 | Suppy of Hume pipe 4" size | Electrical | Supply | SMR40003 | 80 | M | 16000 |  |  | 11
| 181 | 16 | Making 11 KV 3x300 Sqmm Cable Out Door/Indoor end termination | Electrical | Labour | SWR10391 | 2370.63 | EA | 37930.08 |  |  | 12
| 182 | 4200 | Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours. | Electrical | Labour | SWR21903 | 30 | M | 126000 |  |  | 13
| 183 | 1.4 | Loading of M.S.Channels, Angles, Flats & Rods etc., | Electrical | Labour | SWR10206 | 221 | TO | 309.4 |  |  | 14
| 184 | 1.4 | Un loading of M.S.Channels, Angles, Flats & Rods etc., | Electrical | Labour | SWR10524 | 185 | TO | 259 |  |  | 15
| 185 | 5.4 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading )Above 10 KM and upto 20 KM | Electrical | Labour | SWR10132 | 412.08 | TO | 2225.232 |  |  | 16
| 186 | 16 | LOADING of R.S. Joists 175 x 85 mm | Electrical | Labour | SWR10204 | 76 | EA | 1216 |  |  | 17
| 187 | 16 | UNLOADING of R.S. Joists 175 x 85 mm | Electrical | Labour | SWR10522 | 50 | EA | 800 |  |  | 18
| 188 | 16 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Electrical | Labour | SWR10642 | 512.55 | EA | 8200.8 |  |  | 19
| 189 | 16 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Electrical | Labour | SWR10640 | 1132 | EA | 18112 |  |  | 20
| 190 | 8 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Electrical | Labour | SWR11040 | 990.68 | EA | 7925.44 |  |  | 21
| 191 | 8 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Box pole 9/10/11 Mtr | Electrical | Labour | SWR11266 | 2643.83 | EA | 21150.64 |  |  | 22
| 192 | 208.33 | M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground)Fabrication and connecting to risers from earth mat to structures, equipment,marshalling boxes, electrical panels, PLCC panels, fencing posts etc. | Electrical | Labour | SWR10919 | 41 | RMT | 8541.53 |  |  | 23
| 193 | 7.52 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.Including the cost of cement | Electrical | Labour | SWR10356 | 6579 | M3 | 49474.08 |  |  | 24
| 194 | 0.248 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Electrical | Labour | SWR11890 | 3892.98 | M3 | 965.459 |  |  | 25
| 195 | 0.9 | Fabrication of Main and Auxiliary structures with welding using raw steel such as RS joist, M.S.Angles, Plates, Channels, including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Electrical | Labour | SWR10869 | 3426 | TO | 3083.4 |  |  | 26
| 196 | 8 | LOADING of 11 KV AB SWCH Con 200/400 A | Electrical | Labour | SWR10238 | 80 | EA | 640 |  |  | 27
| 197 | 8 | UNLOADING of 11 KV AB SWCH Con 200/400 A | Electrical | Labour | SWR10556 | 80 | EA | 640 |  |  | 28
| 198 | 8 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Electrical | Labour | SWR10393 | 3200 | EA | 25600 |  |  | 29
| 199 | 8 | Supply of CI eath pipe with 80mm dia,2.75 M Length | Electrical | Supply | SMR11483 | 2789 | EA | 22312 |  |  | 30
| 200 | 8 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Electrical | Labour | SWR10357 | 1234.2 | EA | 9873.6 |  |  | 31
| 201 | 8 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Electrical | Labour | SWR10359 | 386 | EA | 3088 |  |  | 32
| 202 | 43 | Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters , CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | Electrical | Supply | SMR40085 | 484 | EA | 20812 |  |  | 33
| 203 | 8 | Painting of feeder name on support including cost of paint | Electrical | Labour | SWR12101 | 53 | EA | 424 |  |  | 34
| 204 | 100 | Supply of GI Bolts & Nuts,Washers etc., | Electrical | Supply | SMR11488 | 117.5 | KG | 11750 |  |  | 35
| 205 | 8 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Electrical | Labour | SWR12331 | 146.63 | EA | 1173.04 |  |  | 36
| 206 | 8 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Electrical | Labour | SWR10881 | 142 | EA | 1136 |  |  | 37 | 5876135.001
| 207 | 2 | Erection of 33 KV AB Switch including alignment and earthing | Electrical | Labour | SWR10392 | 4500 | EA | 9000 | 132KV BAY EXTENSION LABOUR |  | 1
| 208 | 1 | Erection of 33 KV LAS station/Line type including earthing | Electrical | Labour | SWR10396 | 880 | SET | 880 |  |  | 2
| 209 | 1 | Loading of 33 KV VCBs along with Panel boards | Electrical | Labour | SWR10198 | 1024 | EA | 1024 |  |  | 3
| 210 | 1 | Un loading of 33 KV VCBs along with Panel boards | Electrical | Labour | SWR10516 | 1044.48 | EA | 1044.48 |  |  | 4
| 211 | 2 | Loading of 33KV 800 Amps AB Switch | Electrical | Labour | SWR10239 | 126 | EA | 252 |  |  | 5
| 212 | 2 | Un loading of 33KV 800 Amps AB Switch | Electrical | Labour | SWR10557 | 79 | EA | 158 |  |  | 6
| 213 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)Above 10 Km and upto 20 Km with Lorry for each trip | Electrical | Labour | SWR11861 | 3299.7 | EA | 3299.7 |  |  | 7
| 214 | 1.4 | Loading of M.S.Channels, Angles, Flats & Rods etc., | Electrical | Labour | SWR10206 | 221 | TO | 309.4 |  |  | 8
| 215 | 1.4 | Un loading of M.S.Channels, Angles, Flats & Rods etc., | Electrical | Labour | SWR10524 | 185 | TO | 259 |  |  | 9
| 216 | 1.4 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading )Upto 10 KM | Electrical | Labour | SWR10131 | 339.66 | TO | 475.524 |  |  | 10
| 217 | 4.8 | Excavation of Pit for 33KV VCB | Electrical | Labour | SWR23224 | 331 | M3 | 1588.8 |  |  | 11
| 218 | 6 | Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x 1.8 x 0.75 cum for VCB Plinth | Electrical | Labour | SWR20685 | 5160 | M3 | 30960 |  |  | 12
| 219 | 6.4 | Plastering 2 Coats,20/16mm(1:6)(1:4) | Electrical | Labour | SWR10862 | 373 | M2 | 2387.2 |  |  | 13
| 220 | 1 | Painting of coping with two coats of white cement including cost of paint & conveyance charges for PTR/VCB plinths | Electrical | Labour | SWR12334 | 160 | EA | 160 |  |  | 14
| 221 | 1 | Erection of 33 KV VCB with Control Panel | Electrical | Labour | SWR10460 | 12500 | EA | 12500 |  |  | 15
| 222 | 1 | Erection of 33 KV CTs | Electrical | Labour | SWR10399 | 1079 | SET | 1079 |  |  | 16
| 223 | 1 | Erection of 33kV Twin feeder control & Relay panel in the control room duly mounting them on channels and grouting them with foundation bolts excluding cost of channels & foundation bolts | Electrical | Labour | SWR10934 | 1729 | EA | 1729 |  |  | 17
| 224 | 2 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rockboulders)9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Electrical | Labour | SWR11039 | 928 | EA | 1856 |  |  | 18
| 225 | 1.526 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.Including the cost of cement | Electrical | Labour | SWR10356 | 6579 | M3 | 10039.554 |  |  | 19
| 226 | 0.062 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Electrical | Labour | SWR11890 | 3893.06 | M3 | 241.3697 |  |  | 20
| 227 | 2 | Supply of stepped tubular poles single way made of steel oflength 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9 mm, 2.1 mtrs with outer dia 76.1 mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79 kgf as per IS 2713. | Electrical | Supply | SMR40051 | 13913 | EA | 27826 |  |  | 21
| 228 | 2 | Erection of tubular poles | Electrical | Labour | SWR10955 | 1379 | EA | 2758 |  |  | 22
| 229 | 2 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTUREROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA/OSRAM/SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years arranty 90W LED Fixture set | Electrical | Supply | SMR11594 | 8200 | EA | 16400 |  |  | 23
| 230 | 2 | Fixing of Metal halide lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5 GI pipe complete | Electrical | Labour | SWR10956 | 1268 | EA | 2536 |  |  | 24
| 231 | 21 | Labour for Fixing of all types of clamps | Electrical | Labour | SWR10917 | 65 | EA | 1365 |  |  | 25
| 232 | 1200 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends | Electrical | Labour | SWR11879 | 27 | EA | 32400 |  |  | 26
| 233 | 0.08 | Extention of 33KV Bay at 132/33KV Sub-station Zebra condutor | Electrical | Supply | SMR24910 | 299369 | KM | 23949.52 |  |  | 27
| 234 | 9 | Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | Electrical | Labour | SWR10884 | 224 | EA | 2016 |  |  | 28
| 235 | 6 | Supply of I hook | Electrical | Supply | SMR12099 | 158 | EA | 948 |  |  | 29
| 236 | 6 | Erection of I hook | Electrical | Labour | SWR12099 | 55 | EA | 330 |  |  | 30
| 237 | 3 | Supply of Spacer T-Clamps with double dropper suitable for Zebra / Panther | Electrical | Supply | SMR40013 | 788 | EA | 2364 |  |  | 31
| 238 | 6 | Supply of Tension Hardware 3 Bolted for Twin Zebra/panther with 150 mm spacing | Electrical | Supply | SMR40016 | 2512 | EA | 15072 |  |  | 32
| 239 | 12 | Alluminum alloy Pad clamps minimum 15 mm Thickness, 75 mm Width 150 Mm Length conforming to IS:5561-1970, IS 617, IS 2633-1964, IS 1363-1967, IS1367-1961), Six bolted with hot dip galvanized bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 ") minimum weight of 900 gms to suit for Panther ACSR Conductor of pad size 75 X 75 X 15mm for carrying 600 A current | Electrical | Supply | SMR24942 | 360 | EA | 4320 |  |  | 33
| 240 | 6 | Supply of CT stud clamps with hot dip galvanised bolts and nuts suitable for zebra / Panther conductor on one side and 28/30/40 mm CT stud on other side with stud size for single zebra / panther (4 bolted) with bimetallic sleeve for carrying 800 A | Electrical | Supply | SMR40023 | 399 | EA | 2394 |  |  | 34
| 241 | 6 | Supply of U-Bolts 16 mm | Electrical | Supply | SMR40040 | 37 | EA | 222 |  |  | 35
| 242 | 43 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 33 kV bus comprising of three phases with Twin Zebra/Panther conductor to a tension of 900kgs including fixing of spacer clamps.(Bus section of 4.5mt) | Electrical | Labour | SWR10882 | 1302 | EA | 55986 |  |  | 36
| 243 | 2 | Room fire extinguisher (2 ltrs capacity) for control room | Electrical | Supply | SMR40089 | 4620 | EA | 9240 |  |  | 37
| 244 | 6 | Supply & spreading of 20mm machine crushed metal (HBG) including cost of conveneyance of all materials, labour charges etc complete for finished item of work and directed by the engineer incharge | Electrical | Labour | SWR10860 | 2113 | M3 | 12678 |  |  | 38
| 245 | 6 | Supply &Filling with Borrowed Stone Dust | Electrical | Labour | SWR33054 | 1062 | M3 | 6372 |  |  | 39
| 246 | 15 | Brick masonry in cement mortar (1:6) for superstructure using well burnt country made second class bricks of approved quality including cost and conveyance of all materials curing, scaffolding with all leads and lifts etc., complete for finished item of work - Ground Floor | Civil | Labour | SWR33068 | 7209 | M3 | 108135 |  |  | 40
| 247 | 25 | Earth Work Mass Excavation to a depth as directed, in soils such as Mixture of Gravel and Soft Disintegrated Rock like Shales, Ordinary Gravel, Stoney Earth and Earth Mixed with Fair Sized Boulders and in all conditions such as dry, wet, slurry etc.and in dense or hard soils, disposal and depositing of excavated soil with intial lead of 10 mt and intial lift of 2m or as directed, including cost and conveyance of all materials, ramping and lifting of materials, and labour charges, hire charges of machinery, tools & plants, bailing of water ( either sub soil water, stoMts water, rain water, surface water or of any kind) if any at any stage of work until all works below ground level is finished to the satisfaction ,and from work such as shoring, timbering, strutting with required supports etc. for the work and removal of form work after completion of work etc all complete as directed by the engineer-incharge. | Civil | Labour | SWR33015 | 486 | M3 | 12150
| 248 | 3 | S&F of 15 mm brass body CP finish bib tap of not less than 300 grams weight with quarter turn spindle with either internal or external threaded connection conforming to IS 8931 including all operational, incidental and labour charges etc. complete for the finished item of work | Civil | Supply | SWR34330 | 684 | EA | 2052
| 249 | 20 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007) 22.20mm OD Pipe - SDR 11 including all operational, incidental and labour charges etc. complete for the finished item of work | Civil | Supply | SWR34362 | 313 | M | 6260
| 250 | 2 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) in existing Substation | Electrical | Labour | SWR11769 | 144.84 | EA | 289.68
| 251 | 2 | Supply of GI wire No 8 | Electrical | Supply | SMR11486 | 105 | KG | 210
| 252 | 2 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Electrical | Labour | SWR12331 | 146.63 | EA | 293.26
| 253 | 25 | Supply of GI Bolts & Nuts etc | Electrical | Supply | SMR11488 | 117.5 | KG | 2937.5
| 254 | 3 | Excavation of earth pit, supply of cast iron pipe with flange on one end (as per ISS7181/86) of nominal dia 125mm and 2.75 meters long in side the pit including supply and fixing RCC collars 0.75 meter dia (OD), 50mm thick and 0.60meters long complete as per APTRANSCO standards | Electrical | Labour | SWR10924 | 9804 | EA | 29412
| 255 | 3 | Supply of 33KV TC Structure as per DATA-II | Electrical | Supply | SMR40102 | 50703 | EA | 152109
| 256 | 6 | Supply of33KV BD Boom as per DATA-IV | Electrical | Supply | SMR40104 | 18244 | EA | 109464
| 257 | 3 | Erection of33KV TC Structure as per DATA-II | Electrical | Labour | SWR11010 | 17393.04 | EA | 52179.12
| 258 | 6 | Erection of 33KV TD Structure as per DATA-I | Electrical | Labour | SWR11009 | 14839.78 | EA | 89038.68
| 259 | 167 | Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc.M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) | Electrical | Labour | SWR10919 | 41 | RMT | 6847
| 260 | 24 | Supplying of Earth Mat 100x16mm GI Flat from Earth | Electrical | Supply | SMR23228 | 975 | M | 23400
| 261 | 24 | Laying of earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication100x16mm M.S./G.I earth flat | Electrical | Labour | SWR22054 | 65 | RMT | 1560
| 262 | 6 | Supply of Alluminum LA clamps conforming to A6 of IS 617, with hot dip galvanised bolts and nuts suitable for single zebra/Panther | Electrical | Supply | SMR40027 | 357 | EA | 2142
| 263 | 10 | Providing of control cable trench as per DATA-XII | Electrical | Labour | SWR22093 | 3148 | RMT | 31480
| 264 | 1 | Supply of MS Powder coated CT Marshalling Box | Electrical | Supply | SMR40047 | 3675 | EA | 3675
| 265 | 6 | Painting of feeder name on support including cost of paint | Electrical | Labour | SWR12101 | 53 | EA | 318
| 266 | 1 | Erection of Marshalling boxes | Electrical | Labour | SWR10940 | 374.85 | EA | 374.85
|  |  | Total | [5 empty] | 18543462.8717 | 18543462.8717
|  |  | 18% GST | [5 empty] | 3337823.3169
| Total Cost (Without GST)=Electrical | [7 empty] | 18543462.8717
| Total Cost (With 18 % GST)=Electrical | [7 empty] | 21881286.1886 | 21881286.18 | 0.0086178
2101655.95
9632925.29
5876135
932746.63
18543462.87

## Road No.10 Zaheera Nagar (hidden)
SCHEDULE
Name of the work: Erection, testing and commissioning of 33/11KV Indoor Sub Station with 2x 8MVA PTRs at Road No.10,Zaheera Nagar , BanjaraHills Operation Division, Kairathabad Constituency in SD-IV, Div-1,Masterplan, Hyderabad Circle under T&D Improvement works.
WBS No: S-1750-12-01-01-01-001 (Electrical)
Electrical Portion
SNo | S No. | Estimate Quantity (only FigurEs) | Item Detailed Specification Description | Work Type | Item Short Descripti | Service Code | Rate | UOM | Amount
| 1 | 2 | Loading of 8MVA PTR | Electrical | Labour | SWR10613 | 5805.84 | EA | 11611.68 | SS LABOUR |  | 1
| 2 | 2 | Transport of Power transformers (0 to 100 KM) from one place to another place in GHMC Area.(excluding of loading & unloading )-8MVA power transformer | Electrical | Labour | SWR10854 | 21945 | EA | 43890 |  |  | 2
| 3 | 2 | Unloading of 8MVA PTR | Electrical | Labour | SWR10627 | 5805.84 | EA | 11611.68 |  |  | 3
| 4 | 2 | Erection of PTR on constructed plinth-Erection of 8 MVA PTR. | Electrical | Labour | SWR21321 | 49480.2 | EA | 98960.4 |  |  | 4
| 5 | 1 | Loading of 50,63, 75 & 100 KVA DTR | Electrical | Labour | SWR10195 | 350 | EA | 350 |  |  | 5
| 6 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | Electrical | Labour | SWR11861 | 3299.7 | EA | 3299.7 |  |  | 6
| 7 | 1 | Un loading of 50,63, 75 & 100 KVA DTR | Electrical | Labour | SWR10513 | 280 | EA | 280 |  |  | 7
| 8 | 1 | Construction of DTR Plinth- RCC Column type DTR Plinth of size 1'X1'X10',topslab 4'x4'x6" & beam size 4'X8'X8" upto 160KVA | Electrical | Labour | SWR21843 | 25967.57 | EA | 25967.57 |  |  | 8
| 9 | 1 | Erection of 3 Phase DTRs 63,75 & 100 KVA including loading and Unloading DTR on the Structure/Plinth etc | Electrical | Labour | SWR20905 | 1650 | EA | 1650 |  |  | 9
| 10 | 16 | Loading of 11 KV VCBs along with Panel boards | Electrical | Labour | SWR10199 | 1024 | EA | 16384 |  |  | 10
| 11 | 8 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | Electrical | Labour | SWR11861 | 3299.7 | EA | 26397.6 |  |  | 11
| 12 | 16 | Un loading of 11 KV VCBs along with Panel boards | Electrical | Labour | SWR10517 | 1044.48 | EA | 16711.68 |  |  | 12
| 13 | 16 | Erection of 11KV indoor switch gear panel/indoor PT panel /Bus section panel / Bus raiser panel/Capacitor panel/Switch fuse panel for DTR. | Electrical | Labour | SWR10931 | 8894 | EA | 142304 |  |  | 13
| 14 | 10 | Loading of 33 KV VCBs along with Panel boards | Electrical | Labour | SWR10198 | 1024 | EA | 10240 |  |  | 14
| 15 | 5 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | Electrical | Labour | SWR11861 | 3299.7 | EA | 16498.5 |  |  | 15
| 16 | 10 | Un loading of 33 KV VCBs along with Panel boards | Electrical | Labour | SWR10516 | 1044.48 | EA | 10444.8 |  |  | 16
| 17 | 10 | Erection of 33KV indoor switch gear panel/33KV indoor PT panel / Bus section panel / Bus raiser panel | Electrical | Labour | SWR10930 | 9847 | EA | 98470 |  |  | 17
| 18 | 1 | Loading of 220 V Batterry with charger | Electrical | Labour | SWR11166 | 1612 | SET | 1612 |  |  | 18
| 19 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | Electrical | Labour | SWR11861 | 3299.7 | EA | 3299.7 |  |  | 19
| 20 | 1 | Un loading of 220 V Batterry with charger | Electrical | Labour | SWR11147 | 1024 | SET | 1024 |  |  | 20
| 21 | 1 | Erection of 220 V, 80 AH battery in complete shape fit for charging . Conventional lead acid | Electrical | Labour | SWR12295 | 7666 | EA | 7666 |  |  | 21
| 22 | 1 | Supply of AC Supply panel inluding providing of changeover switch, SFU, metering unit, 32 A three phase MCB, 16 A Single phase MCB complete as per specification. | Electrical | Supply | SMR40045 | 42000 | EA | 42000 |  |  | 22
| 23 | 1 | Erection of control/Relay panels, AC Panels, announciationpanels etc in the control room duly mounting them on channels and grouting them with foundation bolts excluding cost of channels & foundation bolts | Electrical | Labour | SWR11893 | 2122 | EA | 2122 |  |  | 23
| 24 | 44 | Cutting Charges for RS joist 150x150mm | Electrical | Labour | SWR10297 | 48 | EA | 2112 |  |  | 29
| 25 | 0.83 | Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Electrical | Labour | SWR10869 | 3426 | TO | 2843.58 |  |  | 30
| 26 | 3.83 | Alligning the Main and Auxiliary structures such as RS joist,M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication. | Electrical | Labour | SWR10867 | 1470 | TO | 5630.1 |  |  | 31
| 27 | 3.83 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes,labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Electrical | Supply | SMR40009 | 2181 | TO | 8353.23 |  |  | 32
| 28 | 3.83 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters ofthinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes,labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Electrical | Labour | SWR10877 | 851 | TO | 3259.33 |  |  | 33
| 29 | 3.83 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc | Electrical | Supply | SMR40010 | 1293 | TO | 4952.19 |  |  | 34
| 30 | 3.83 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium | Electrical | Labour | SWR10879 | 482 | TO | 1846.06 |  |  | 35
| 31 | 43 | Painting of Name Plates for any equipment | Electrical | Labour | SWR10963 | 122 | EA | 5246 |  |  | 36
| 32 | 36 | Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness10mm with flange as per specication | Electrical | Supply | SMR11482 | 3486 | EA | 125496 |  |  | 37
| 33 | 36 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Electrical | Labour | SWR10357 | 1234.2 | EA | 44431.2 |  |  | 38
| 34 | 36 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50M height | Electrical | Labour | SWR10359 | 386 | EA | 13896 |  |  | 39
| 35 | 531.9 | Laying of MS Flats /GI Flats 75x 8mm earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment andconnecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes including fabrication | Electrical | Labour | SWR10920 | 65 | RMT | 34573.5 |  |  | 43
| 36 | 208.3 | Fabrication and connecting of M.S./ G.I. Flat 50x6mm to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. | Electrical | Labour | SWR10919 | 41 | RMT | 8540.3 |  |  | 44
| 37 | 50 | Supply of GI Bolts & Nuts | Electrical | Supply | SMR11488 | 117.5 | KG | 5875 |  |  | 45
| 38 | 314 | Paint-Black to all Earth Flat incl. Pain | Electrical | Labour | SWR12217 | 55 | M | 17270 |  |  | 46
| 39 | 2 | Supply of Copper Flexible jumper with 75 X 8 of length 250 mm at neutral of Power tranformer end and 50 X 6 of length 50mm two Nos at double neutral end duly brasing with flexible jumper of capacity of 5kA/3 sec for power transformer neutral | Electrical | Supply | SMR40033 | 4725 | EA | 9450 |  |  | 47
| 40 | 2 | Providing of double earthing for neutral with flexible copper jumpers including arrangement by fixing M.S.Channel 100x50mm | Electrical | Labour | SWR11892 | 1323 | EA | 2646 |  |  | 48
| 41 | 106 | Laying of 4No's single core 630 sqmm UG cable (Single Circuit with one spare cable) including excavation of trench of size 0.7 Mtrs width and 1.2 Mtrs depth from road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.Lay-4 SC 33KV 630sqmm UG Cb HG/BC/RE/NS | Electrical | Labour | SWR12110 | 2463.3 | M | 261109.8 |  |  | 49
| 42 | 56 | Raise-SR 33KV 1x630sqmm UG Cb on Support | Electrical | Labour | SWR12448 | 133 | M | 7448 |  |  | 50
| 43 | 106 | Laying of second cable 33KV UG Cb in Existing Duct | Electrical | Labour | SWR12452 | 200 | M | 21200 |  |  | 51
| 44 | 14 | Raising of single run 33kV 3x400 Sqmm Cu cable on already erected support with wooden / MS clamps and connecting it to over head line withcable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Electrical | Labour | SWR11954 | 135.66 | M | 1899.24 |  |  | 52
| 45 | 8 | Supply of 33KV 1x630Sqmm GIS ID Unit EndTermtn | Electrical | Supply | SMR12473 | 2500 | EA | 20000 |  |  | 53
| 46 | 8 | Supply of33KV 1x630Sqmm OD Unit EndTermtn | Electrical | Supply | SMR12474 | 4200 | EA | 33600 |  |  | 54
| 47 | 8 | Installation of 33KV 1x630Sqmm GIS ID EndTermtn | Electrical | Labour | SWR12473 | 17600 | EA | 140800 |  |  | 55
| 48 | 8 | Installation of 33KV 1x630Sqmm OD Unit EndTermtn | Electrical | Labour | SWR12474 | 4000 | EA | 32000 |  |  | 56
| 49 | 4 | Making of Outdoor/Indoor 33 KV 3x400 Sqmm End Termination | Electrical | Labour | SWR10387 | 2764.76 | EA | 11059.04 |  |  | 57
| 50 | 85 | Laying of XLPE UG cable Single Run including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the siteinluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders/Normal soil / CC/BT Road 11KV 3x185 Sqmm Cable | Electrical | Labour | SWR11920 | 465.46 | M | 39564.1 |  |  | 58
| 51 | 15 | Raising of Single Run 11 KV 3x185 Sqmm Cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Electrical | Labour | SWR11956 | 126.23 | M | 1893.45 |  |  | 59
| 52 | 2 | Making of Outdoor/Indoor 11 KV 3x185 Sqmm Cable End Termination | Electrical | Labour | SWR10390 | 2370.63 | EA | 4741.26 |  |  | 60
| 53 | 90 | Laying of XLPE UG cable Single Run including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders/Normal soil / CC/BT Road LT 3 1/2 x 185 Sqmm Cable | Electrical | Labour | SWR11923 | 377.63 | M | 33986.7 |  |  | 61
| 54 | 10 | Raising of Single Run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-LT 3 1/2 x 185 Sqmm Cable | Electrical | Labour | SWR11959 | 85.43 | M | 854.3 |  |  | 62
| 55 | 2 | Fixing of Oout Door/Indoor end termination LT 3 1/2 x185 Sqmm Cable | Electrical | Labour | SWR10765 | 968.9 | EA | 1937.8 |  |  | 63
| 56 | 2200 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends . | Electrical | Labour | SWR11879 | 27 | M | 59400 |  |  | 64
| 57 | 500 | Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per specification (including cost of ferrules, lugs and glands) | Electrical | Labour | SWR12510 | 27 | EA | 13500 |  |  | 65
| 58 | 1.6 | Fabrication of Main and Auxiliary structures with welding using raw steel such as RS joist, M.S.Angles, Plates, Channels, including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Electrical | Labour | SWR10869 | 3426 | TO | 5481.6 |  |  | 69
| 59 | 1.6 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Electrical | Supply | SMR40009 | 2181 | TO | 3489.6 |  |  | 70
| 60 | 1.6 | Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Electrical | Labour | SWR10877 | 851 | TO | 1361.6 |  |  | 71
| 61 | 1.6 | Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. | Electrical | Supply | SMR40010 | 1293 | TO | 2068.8 |  |  | 72
| 62 | 1.6 | Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . | Electrical | Labour | SWR10879 | 482 | TO | 771.2 |  |  | 73
| 63 | 5 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Electrical | Labour | SWR11040 | 990.68 | EA | 4953.4 |  |  | 74
| 64 | 5 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Box pole 9/10/11 Mtr | Electrical | Labour | SWR11266 | 2643.83 | EA | 13219.15 |  |  | 75
| 65 | 4.7 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.-Including the cost of cement | Electrical | Labour | SWR10356 | 6579 | M3 | 30921.3 |  |  | 76
| 66 | 0.155 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Electrical | Labour | SWR11890 | 3893.03 | M3 | 603.4197 |  |  | 77
| 67 | 5 | Paint of coping with 2 coats of white cement incl cost of paints etc. | Electrical | Labour | SWR11089 | 48 | EA | 240 |  |  | 78
| 68 | 1 | Erection of 11 KV HG Fuse set including earthing | Electrical | Labour | SWR10395 | 740.52 | SET | 740.52 |  |  | 81
| 69 | 1 | Erection of 11KV 200A TT type AB Switch including fixing of cross angles and alignment complete | Electrical | Labour | SWR20102 | 1813.49 | EA | 1813.49 |  |  | 84
| 70 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.-Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Electrical | Labour | SWR10881 | 142 | EA | 142 |  |  | 85
| 71 | 1 | Erection of LT distribution box including laying of LT cable from distribution box to LT OH line and DTR to distribution box including earthing of distribution box and crimping of lugs connecting of jumpers etc | Electrical | Labour | SWR10674 | 1594.67 | EA | 1594.67 |  |  | 86
| 72 | 18 | Supply of earthing pipe with materials GI Flat 25X3 mm | Electrical | Supply | SMR11485 | 105 | KG | 1890 |  |  | 87
| 73 | 30 | Running of GI eartn flat of size 25X3mm from all metallic parts of channels, AB Switch, HG fuse set, DTr neutral and LT Distribution box and inter connection of earth pits etc complete. | Electrical | Labour | SWR12125 | 14.03 | M | 420.9 |  |  | 88
| 74 | 2 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Electrical | Labour | SWR11230 | 1024 | DR | 2048 |  |  | 89
| 75 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | Electrical | Labour | SWR11861 | 3299.7 | EA | 3299.7 |  |  | 90
| 76 | 2 | Un loading of 11KV/33KV XLPE UG Cable for all sizes | Electrical | Labour | SWR11231 | 1024 | DR | 2048 |  |  | 91
| 77 | 8 | Supply of stepped tubular poles single way made of steel of length 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9 mm, 2.1 mtrs with outer dia 76.1 mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79 kgf as per IS 2713. | Electrical | Supply | SMR40051 | 13913 | EA | 111304 |  |  | 92
| 78 | 8 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Electrical | Labour | SWR11039 | 928 | EA | 7424 |  |  | 93
| 79 | 8 | Erection of tubular poles | Electrical | Labour | SWR10955 | 1379 | EA | 11032 |  |  | 94
| 80 | 6.1 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.-Including the cost of cement | Electrical | Labour | SWR10356 | 6579 | M3 | 40131.9 |  |  | 95
| 81 | 0.248 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Electrical | Labour | SWR11890 | 3892.98 | M3 | 965.459 |  |  | 96
| 82 | 8 | Paint of coping with 2 coats of white cement incl cost of paints etc. | Electrical | Labour | SWR11089 | 48 | EA | 384 |  |  | 97
| 83 | 8 | Supply of Metal Handle Lamp 150W | Electrical | Supply | SMR24635 | 6450 | EA | 51600 |  |  | 98
| 84 | 50 | Supply of GI Bolts & Nuts,washers etc. | Electrical | Supply | SMR11488 | 117.5 | KG | 5875 |  |  | 99
| 85 | 8 | Fixing of Metal halide lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5 GI pipe complete. | Electrical | Labour | SWR10956 | 1268 | EA | 10144 |  |  | 100
| 86 | 1 | Supply of Steel almarah(61/2 X 3ft) Godrej | Electrical | Supply | SMR40061 | 9818 | EA | 9818 |  |  | 101
| 87 | 750 | Supplying & fabrication erection of 6mm Checkerd plates as per the field conditions | Electrical | Labour | SWR10873 | 83 | KG | 62250 |  |  | 102
| 88 | 12 | Supply of Rubber mats ( 6’x3’) size for indoor SS | Electrical | Supply | SMR40068 | 1386 | EA | 16632 |  |  | 103
| 89 | 1 | Supply of Alluminium Ladder for indoor works | Electrical | Supply | SMR40062 | 4410 | EA | 4410 |  |  | 104
| 90 | 2 | Supply of Trolley mounted CO2 (6.5Kgs)(IS-2878) | Electrical | Supply | SMR40087 | 9240 | EA | 18480 |  |  | 105
| 91 | 2 | Supply of Fire Buckets Stand with Buckets | Electrical | Supply | SMR40088 | 1386 | SET | 2772 |  |  | 106
| 92 | 6 | Supply of Fire Extinguisher for Control Room | Electrical | Supply | SMR40089 | 4620 | EA | 27720 |  |  | 107
| 93 | 4 | Supply of Safety Helmet of standard make | Electrical | Supply | SMR40071 | 231 | EA | 924 |  |  | 108
| 94 | 4 | Supply of Earth Rods (8ft) Screw & clamp type | Electrical | Supply | SMR40066 | 578 | EA | 2312 |  |  | 109
| 95 | 4 | Supply of Hand Gloves | Electrical | Supply | SMR40067 | 289 | SET | 1156 |  |  | 110
| 96 | 1 | Supply of Stand basic cell phone with charger | Electrical | Supply | SMR40069 | 1386 | EA | 1386 |  |  | 111
| 97 | 1 | Supply of Table (3x6ft) Godrej | Electrical | Supply | SMR40057 | 6050 | EA | 6050 |  |  | 112
| 98 | 4 | Supply of S type chairs (Godrej) | Electrical | Supply | SMR40058 | 924 | EA | 3696 |  |  | 113
| 99 | 1 | Supply of Angle racks(18x36.6inches) Godrej | Electrical | Supply | SMR40060 | 1733 | EA | 1733 |  |  | 114
| 100 | 10 | Supply of Danger boards with clamps | Electrical | Supply | SMR40070 | 116 | EA | 1160 |  |  | 115
| 101 | 1 | Supply of 33/11kv S.S Permanent name board | Electrical | Supply | SMR40086 | 10238 | EA | 10238 |  |  | 116
| 102 | 1 | Supply of Wall clock standard make | Electrical | Supply | SMR40059 | 578 | EA | 578 |  |  | 117
| 103 | 1 | Supply of Taparia Tool kit complete as per Spec | Electrical | Supply | SMR40063 | 4925 | SET | 4925 |  |  | 118
| 104 | 1 | Supply of Rechargeable LED torch light. | Electrical | Supply | SMR40064 | 1733 | EA | 1733 |  |  | 119
| 105 | 1 | Supply of Hack saw (12 inches) | Electrical | Supply | SMR40065 | 289 | EA | 289 |  |  | 120
| 106 | 8 | Supply of LC Boards | Electrical | Supply | SMR40072 | 116 | EA | 928 |  |  | 121
| 107 | 2 | Supply of Gum Boots | Electrical | Supply | SMR40073 | 693 | EA | 1386 |  |  | 122
| 108 | 1 | Supply of Digital clamp meter. | Electrical | Supply | SMR40076 | 2888 | EA | 2888 |  |  | 123
| 109 | 1 | Supply of 5000v megger | Electrical | Supply | SMR40074 | 13860 | EA | 13860 |  |  | 124
| 110 | 1 | Supply &fixing of board ind Switchyard layout | Electrical | Labour | SWR20032 | 1654 | EA | 1654 |  |  | 125
| 111 | 1 | Supply &fixing safety inst/SS Op. inst board | Electrical | Labour | SWR22090 | 2205 | EA | 2205 |  |  | 126
| 112 | 1 | Supply of 10ft Aluminium Ladder | Electrical | Supply | SMR12378 | 1654 | EA | 1654 |  |  | 127 | 2093014.1987
| 113 | 3000 | Supply of RS Joist Grider Pole (150x150mm) | Electrical | Supply | SMR12302 | 59.25 | KG | 177750
| 114 | 830 | Supply of MS Channel 100x50mm | Electrical | Supply | SMR22745 | 57.45 | KG | 47683.5
| 115 | 2500 | Supply of MS Flat 75x8mm | Electrical | Supply | SMR12321 | 56.42 | KG | 141050
| 116 | 500 | Supply of MS Flat 50x6mm | Electrical | Supply | SMR12322 | 56.5 | KG | 28250
| 117 | 400 | Supply of MS Channel 100x50mm | Electrical | Supply | SMR22745 | 57.45 | KG | 22980
| 118 | 2 | Supply of 33KV 3x400Sqmm O/D End Kit | Electrical | Supply | SMR22222 | 4554 | EA | 9108
| 119 | 2 | Supply of of 33KV 3x400Sqmm Indoor end kit | Electrical | Supply | SMR11506 | 3589.96 | EA | 7179.92
| 120 | 1 | Supply of 11KV 3x185 Heat Shble O/d End Term Kit | Electrical | Supply | SMR25201 | 1182.97 | EA | 1182.97
| 121 | 1 | Supply of 11KV 3x185 Heat Shble I/d End Term Kit | Electrical | Supply | SMR25202 | 1085 | EA | 1085
| 122 | 100 | Supply of LT XLPE Cable 3 1/2 C 185 sqmm | Electrical | Supply | SMR25204 | 547 | M | 54700
| 123 | 100 | Supply of MS Channel 75x40 mm | Electrical | Supply | SMR25205 | 58.45 | KG | 5845
| 124 | 1500 | Supply of RS Joist Pole (175x85mm) | Electrical | Supply | SMR12303 | 60.75 | KG | 91125
| 125 | 1 | Supply of 11KV HG FuseSet for StationTransformer | Electrical | Supply | SMR12324 | 1974 | EA | 1974
| 126 | 1 | Supply of 11KV 200A Tilting Type AB Switch | Electrical | Supply | SMR12318 | 8991 | EA | 8991
| 127 | 1 | Supply of LT Distribution Box (SMC) | Electrical | Supply | SMR25200 | 7797 | EA | 7797
| 128 | 60 | Supply of LT XLPE Cable 1C 150 sqmm | Electrical | Supply | SMR25203 | 114.83 | M | 6889.8 | 2706605.3887
| 129 | 1 | survey line&cabl inc peg mark&tree clear | Electrical | Labour | SWR22092 | 765 | KM | 765 | 33KV LINE MATERIAL |  | 1
| 130 | 29 | Load-11/33KV XLPE UG Cable for all sizes | Electrical | Labour | SWR11230 | 1024 | DR | 29696 |  |  | 2
| 131 | 29 | Unload-11/33KV XLPE UG Cable all sizes | Electrical | Labour | SWR11231 | 1024 | DR | 29696 |  |  | 3
| 132 | 15 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Upto 10 Km with Lorry for each trip | Electrical | Labour | SWR11860 | 2720.34 | EA | 40805.1 |  |  | 4
| 133 | 4350 | Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters,providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts,Along the CC / BT multi layer road requiring compressor for 33 KV 3x400 Sqmm Cable | Electrical | Labour | SWR11980 | 1388.84 | M | 6041454 |  |  | 5
| 134 | 4350 | Laying of 2nd cable in excavated trench | Electrical | Labour | SWR10988 | 204.1 | M | 887835 |  |  | 6
| 135 | 44 | Supply & Erection of Smart RFID marker | Electrical | Labour | SWR25089 | 2745 | EA | 120780 |  |  | 7
| 136 | 35 | Making of Straight through joint 33kv 3x400 xlpe | Electrical | Labour | SWR10382 | 5700.78 | EA | 199527.3 |  |  | 8
| 137 | 1756 | Supply of 6" B class GI pipe | Electrical | Supply | SMR40081 | 1044 | M | 1833264 |  |  | 9
| 138 | 100 | Supply of 6" DWC pipe | Electrical | Supply | SMR11610 | 1012 | M | 101200 |  |  | 10
| 139 | 100 | Supply of Hume pipe 9" size | Electrical | Supply | SMR40001 | 125 | M | 12500 |  |  | 11
| 140 | 10 | Making of OD/Idoor end termination 33kv 3x400 xlpe | Electrical | Labour | SWR10387 | 2764.76 | EA | 27647.6 |  |  | 12
| 141 | 80 | Raising of single run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) 33KV 3x400sqmm UG Cb on support | Electrical | Labour | SWR11954 | 135.66 | M | 10852.8 |  |  | 13
| 142 | 4350 | Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours. | Electrical | Labour | SWR21903 | 30 | M | 130500 |  |  | 14
| 143 | 12 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Electrical | Labour | SWR10642 | 512.55 | EA | 6150.6 |  |  | 19
| 144 | 12 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Electrical | Labour | SWR10640 | 1132 | EA | 13584 |  |  | 21
| 145 | 6 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Electrical | Labour | SWR11040 | 990.68 | EA | 5944.08 |  |  | 22
| 146 | 2 | Erection of 9/10/11Meter Box pole | Electrical | Labour | SWR11266 | 2643.83 | EA | 5287.66 |  |  | 23
| 147 | 208.3 | Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc.M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) | Electrical | Labour | SWR10919 | 41 | RMT | 8540.3 |  |  | 24
| 148 | 5.64 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.Including the cost of cement | Electrical | Labour | SWR10356 | 6579 | M3 | 37105.56 |  |  | 25
| 149 | 0.186 | Coping & Muffing-Iron Pole,Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Electrical | Labour | SWR11890 | 3893.01 | M3 | 724.0999 |  |  | 26
| 150 | 0.6 | Fabrication of Main and Auxiliary structures with welding using raw steel such as RS joist, M.S.Angles, Plates, Channels, including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Electrical | Labour | SWR10869 | 3426 | TO | 2055.6 |  |  | 27
| 151 | 2 | Erection of 33 KV LAS station/Line type including earthing | Electrical | Labour | SWR10396 | 880 | SET | 1760 |  |  | 28
| 152 | 2 | Erection of 33 KV AB Switch including alignment and earthing | Electrical | Labour | SWR10392 | 4500 | EA | 9000 |  |  | 31
| 153 | 6 | S-CI Pipe earthing 80mm dia 2.75m long | Electrical | Supply | SMR11483 | 2789 | EA | 16734 |  |  | 32
| 154 | 6 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and | Electrical | Labour | SWR10357 | 1234.2 | EA | 7405.2 |  |  | 33
| 155 | 6 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Electrical | Labour | SWR10359 | 386 | EA | 2316 |  |  | 34
| 156 | 44 | Supply of Pre-cast cable Joint markersSupply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters , CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | Electrical | Supply | SMR40085 | 484 | EA | 21296 |  |  | 35
| 157 | 6 | Painting of feeder name on support including cost of paint | Electrical | Labour | SWR12101 | 53 | EA | 318 |  |  | 36
| 158 | 100 | Supply of GI Bolts & Nuts,Washers etc., | Electrical | Supply | SMR11488 | 117.5 | KG | 11750 |  |  | 37
| 159 | 2 | 33 KV DP Structure with 175x85/150x75mm RS joist Assembly and erection of Structure as per specification which includes fixing of top channels and cross bracings, transport of all materials from road side to the location, earthing, back filling with earth ramming etc excluding pit excavation and concreting. | Electrical | Labour | SWR11276 | 5670 | SET | 11340
| 160 | 6 | Loading of 33 KV, 10 KA LAs Station type | Electrical | Labour | SWR10266 | 41 | EA | 246
| 161 | 6 | Un loading of 33 KV, 10 KA LAs Station type | Electrical | Labour | SWR10584 | 35 | EA | 210
| 162 | 2 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Electrical | Labour | SWR12331 | 146.63 | EA | 293.26
| 163 | 2 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Electrical | Labour | SWR10881 | 142 | EA | 284
| 164 | 35 | Supply of 33KV3x400Sqmm Straight thr kit | Electrical | Supply | SMR22223 | 24151 | EA | 845285
| 165 | 8 | Supply of 33KV 3x400Sqmm O/D End Kit | Electrical | Supply | SMR22222 | 4554 | EA | 36432
| 166 | 2 | Supply of 33KV 3x400Sqmm Indoor end kit | Electrical | Supply | SMR11506 | 3589.96 | EA | 7179.92
| 167 | 3000 | Supply of RS Joist Pole (175x85mm) | Electrical | Supply | SMR12303 | 60.75 | KG | 182250
| 168 | 500 | Supply of MS Flat 50x6mm | Electrical | Supply | SMR12322 | 56.5 | KG | 28250
| 169 | 600 | Supply of MS Channel 100x50mm | Electrical | Supply | SMR22745 | 57.45 | KG | 34470
| 170 | 2 | Supply of 33KV 800A DB Break AB Switch | Electrical | Supply | SMR12315 | 40658.78 | EA | 81317.56 | 10844051.6399
| 171 | 1 | Survey line&cabl inc peg mark&tree clear | Electrical | Labour | SWR22092 | 765 | KM | 765 | 11KV LINE LABOUR |  | 1 | 9632925.29
| 172 | 14 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Electrical | Labour | SWR11230 | 1024 | DR | 14336 |  |  | 2
| 173 | 14 | Un loading of 11KV/33KV XLPE UG Cable for all sizes | Electrical | Labour | SWR11231 | 1024 | DR | 14336 |  |  | 3
| 174 | 7 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Above 10 Km and upto 20 Km with Lorry for each trip | Electrical | Labour | SWR11861 | 3299.7 | EA | 23097.9 |  |  | 4
| 175 | 4200 | Laying of Single Run XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions ofEngineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.Along the CC / BT multi layer road requiring compressor for 11 KV 3x300 Sqmm Cable | Electrical | Labour | SWR11928 | 1073.94 | M | 4510548 |  |  | 5
| 176 | 80 | Raising of Single Run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)11 KV 3x300 Sqmm Cable | Electrical | Labour | SWR11955 | 144.08 | M | 11526.4 |  |  | 6
| 177 | 43 | Supply & Erecting of Smart RFID marker | Electrical | Labour | SWR25089 | 2745 | EA | 118035 |  |  | 7
| 178 | 20 | Making of Straight through joint 11kv 3x300 xlpe | Electrical | Labour | SWR10386 | 3725.45 | EA | 74509 |  |  | 8
| 179 | 856 | Supply of 4" B class GI pipe | Electrical | Supply | SMR40080 | 740 | M | 633440 |  |  | 9
| 180 | 100 | supply of 4" DWC pipe | Electrical | Supply | SMR11609 | 759 | M | 75900 |  |  | 10
| 181 | 200 | Suppy of Hume pipe 4" size | Electrical | Supply | SMR40003 | 80 | M | 16000 |  |  | 11
| 182 | 16 | Making 11 KV 3x300 Sqmm Cable Out Door/Indoor end termination | Electrical | Labour | SWR10391 | 2370.63 | EA | 37930.08 |  |  | 12
| 183 | 4200 | Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours. | Electrical | Labour | SWR21903 | 30 | M | 126000 |  |  | 13
| 184 | 16 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Electrical | Labour | SWR10642 | 512.55 | EA | 8200.8 |  |  | 19
| 185 | 16 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Electrical | Labour | SWR10640 | 1132 | EA | 18112 |  |  | 20
| 186 | 8 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Electrical | Labour | SWR11040 | 990.68 | EA | 7925.44 |  |  | 21
| 187 | 8 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Box pole 9/10/11 Mtr | Electrical | Labour | SWR11266 | 2643.83 | EA | 21150.64 |  |  | 22
| 188 | 208.33 | M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground)Fabrication and connecting to risers from earth mat to structures, equipment,marshalling boxes, electrical panels, PLCC panels, fencing posts etc. | Electrical | Labour | SWR10919 | 41 | RMT | 8541.53 |  |  | 23
| 189 | 7.52 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.Including the cost of cement | Electrical | Labour | SWR10356 | 6579 | M3 | 49474.08 |  |  | 24
| 190 | 0.248 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Electrical | Labour | SWR11890 | 3892.98 | M3 | 965.459 |  |  | 25
| 191 | 0.9 | Fabrication of Main and Auxiliary structures with welding using raw steel such as RS joist, M.S.Angles, Plates, Channels, including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Electrical | Labour | SWR10869 | 3426 | TO | 3083.4 |  |  | 26
| 192 | 8 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Electrical | Labour | SWR10393 | 3200 | EA | 25600 |  |  | 29
| 193 | 8 | Supply of CI eath pipe with 80mm dia,2.75 M Length | Electrical | Supply | SMR11483 | 2789 | EA | 22312 |  |  | 30
| 194 | 8 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Electrical | Labour | SWR10357 | 1234.2 | EA | 9873.6 |  |  | 31
| 195 | 8 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Electrical | Labour | SWR10359 | 386 | EA | 3088 |  |  | 32
| 196 | 43 | Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters , CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | Electrical | Supply | SMR40085 | 484 | EA | 20812 |  |  | 33
| 197 | 8 | Painting of feeder name on support including cost of paint | Electrical | Labour | SWR12101 | 53 | EA | 424 |  |  | 34
| 198 | 100 | Supply of GI Bolts & Nuts,Washers etc., | Electrical | Supply | SMR11488 | 117.5 | KG | 11750 |  |  | 35
| 199 | 8 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Electrical | Labour | SWR12331 | 146.63 | EA | 1173.04 |  |  | 36
| 200 | 8 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Electrical | Labour | SWR10881 | 142 | EA | 1136 |  |  | 37 | 5870045.369
| 201 | 20 | Supply of 11KV 3x300 Heat Shble str thr JointKit | Electrical | Supply | SMR25210 | 4110.17 | EA | 82203.4
| 202 | 8 | Supply of 11KV 3x300 Heat Shble O/d End Term Kit | Electrical | Supply | SMR25208 | 1372.88 | EA | 10983.04
| 203 | 8 | Supply of 11KV 3x300 Heat Shble I/d End Term Kit | Electrical | Supply | SMR25209 | 1459.83 | EA | 11678.64
| 204 | 4000 | Supply of RS Joist Pole (175x85mm) | Electrical | Supply | SMR12303 | 60.75 | KG | 243000
| 205 | 500 | Supply of MS Flat 50x6mm | Electrical | Supply | SMR12322 | 56.5 | KG | 28250
| 206 | 600 | Supply of MS Channel 75x40 mm | Electrical | Supply | SMR25205 | 58.45 | KG | 35070
| 207 | 300 | Supply of MS Angle 65X65X6 | Electrical | Supply | SMR25207 | 57.25 | KG | 17175
| 208 | 8 | Supply of 11KV 800A DB Break AB Switch | Electrical | Supply | SMR12316 | 30847.46 | EA | 246779.68 | 6545185.129
| 209 | 2 | Erection of 33 KV AB Switch including alignment and earthing | Electrical | Labour | SWR10392 | 4500 | EA | 9000 | 132KV BAY EXTENSION LABOUR |  | 1
| 210 | 1 | Erection of 33 KV LAS station/Line type including earthing | Electrical | Labour | SWR10396 | 880 | SET | 880 |  |  | 2
| 211 | 1 | Loading of 33 KV VCBs along with Panel boards | Electrical | Labour | SWR10198 | 1024 | EA | 1024 |  |  | 3
| 212 | 1 | Un loading of 33 KV VCBs along with Panel boards | Electrical | Labour | SWR10516 | 1044.48 | EA | 1044.48 |  |  | 4
| 213 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)Above 10 Km and upto 20 Km with Lorry for each trip | Electrical | Labour | SWR11861 | 3299.7 | EA | 3299.7 |  |  | 7
| 214 | 4.8 | Excavation of Pit for 33KV VCB | Electrical | Labour | SWR23224 | 331 | M3 | 1588.8 |  |  | 11
| 215 | 6 | Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x 1.8 x 0.75 cum for VCB Plinth | Electrical | Labour | SWR20685 | 5160 | M3 | 30960 |  |  | 12
| 216 | 6.4 | Plastering 2 Coats,20/16mm(1:6)(1:4) | Electrical | Labour | SWR10862 | 373 | M2 | 2387.2 |  |  | 13
| 217 | 1 | Painting of coping with two coats of white cement including cost of paint & conveyance charges for PTR/VCB plinths | Electrical | Labour | SWR12334 | 160 | EA | 160 |  |  | 14
| 218 | 1 | Erection of 33 KV VCB with Control Panel | Electrical | Labour | SWR10460 | 12500 | EA | 12500 |  |  | 15
| 219 | 1 | Erection of 33 KV CTs | Electrical | Labour | SWR10399 | 1079 | SET | 1079 |  |  | 16
| 220 | 1 | Erection of 33kV Twin feeder control & Relay panel in the control room duly mounting them on channels and grouting them with foundation bolts excluding cost of channels & foundation bolts | Electrical | Labour | SWR10934 | 1729 | EA | 1729 |  |  | 17
| 221 | 2 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rockboulders)9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Electrical | Labour | SWR11039 | 928 | EA | 1856 |  |  | 18
| 222 | 1.526 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.Including the cost of cement | Electrical | Labour | SWR10356 | 6579 | M3 | 10039.554 |  |  | 19
| 223 | 0.062 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Electrical | Labour | SWR11890 | 3893.06 | M3 | 241.3697 |  |  | 20
| 224 | 2 | Supply of stepped tubular poles single way made of steel oflength 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9 mm, 2.1 mtrs with outer dia 76.1 mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79 kgf as per IS 2713. | Electrical | Supply | SMR40051 | 13913 | EA | 27826 |  |  | 21
| 225 | 2 | Erection of tubular poles | Electrical | Labour | SWR10955 | 1379 | EA | 2758 |  |  | 22
| 226 | 2 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTUREROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA/OSRAM/SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years arranty 90W LED Fixture set | Electrical | Supply | SMR11594 | 8200 | EA | 16400 |  |  | 23
| 227 | 2 | Fixing of Metal halide lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5 GI pipe complete | Electrical | Labour | SWR10956 | 1268 | EA | 2536 |  |  | 24
| 228 | 21 | Labour for Fixing of all types of clamps | Electrical | Labour | SWR10917 | 65 | EA | 1365 |  |  | 25
| 229 | 1200 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends | Electrical | Labour | SWR11879 | 27 | EA | 32400 |  |  | 26
| 230 | 0.08 | Extention of 33KV Bay at 132/33KV Sub-station Zebra condutor | Electrical | Supply | SMR24910 | 299369 | KM | 23949.52 |  |  | 27
| 231 | 9 | Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | Electrical | Labour | SWR10884 | 224 | EA | 2016 |  |  | 28
| 232 | 6 | Supply of I hook | Electrical | Supply | SMR12099 | 158 | EA | 948 |  |  | 29
| 233 | 6 | Erection of I hook | Electrical | Labour | SWR12099 | 55 | EA | 330 |  |  | 30
| 234 | 3 | Supply of Spacer T-Clamps with double dropper suitable for Zebra / Panther | Electrical | Supply | SMR40013 | 788 | EA | 2364 |  |  | 31
| 235 | 6 | Supply of Tension Hardware 3 Bolted for Twin Zebra/panther with 150 mm spacing | Electrical | Supply | SMR40016 | 2512 | EA | 15072 |  |  | 32
| 236 | 12 | Alluminum alloy Pad clamps minimum 15 mm Thickness, 75 mm Width 150 Mm Length conforming to IS:5561-1970, IS 617, IS 2633-1964, IS 1363-1967, IS1367-1961), Six bolted with hot dip galvanized bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 ") minimum weight of 900 gms to suit for Panther ACSR Conductor of pad size 75 X 75 X 15mm for carrying 600 A current | Electrical | Supply | SMR24942 | 360 | EA | 4320 |  |  | 33
| 237 | 6 | Supply of CT stud clamps with hot dip galvanised bolts and nuts suitable for zebra / Panther conductor on one side and 28/30/40 mm CT stud on other side with stud size for single zebra / panther (4 bolted) with bimetallic sleeve for carrying 800 A | Electrical | Supply | SMR40023 | 399 | EA | 2394 |  |  | 34
| 238 | 6 | Supply of U-Bolts 16 mm | Electrical | Supply | SMR40040 | 37 | EA | 222 |  |  | 35
| 239 | 43 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 33 kV bus comprising of three phases with Twin Zebra/Panther conductor to a tension of 900kgs including fixing of spacer clamps.(Bus section of 4.5mt) | Electrical | Labour | SWR10882 | 1302 | EA | 55986 |  |  | 36
| 240 | 2 | Room fire extinguisher (2 ltrs capacity) for control room | Electrical | Supply | SMR40089 | 4620 | EA | 9240 |  |  | 37
| 241 | 6 | Supply & spreading of 20mm machine crushed metal (HBG) including cost of conveneyance of all materials, labour charges etc complete for finished item of work and directed by the engineer incharge | Electrical | Labour | SWR10860 | 2113 | M3 | 12678 |  |  | 38
| 242 | 6 | Supply &Filling with Borrowed Stone Dust | Electrical | Labour | SWR33054 | 1062 | M3 | 6372 |  |  | 39
| 243 | 15 | Brick masonry in cement mortar (1:6) for superstructure using well burnt country made second class bricks of approved quality including cost and conveyance of all materials curing, scaffolding with all leads and lifts etc., complete for finished item of work - Ground Floor | Civil | Labour | SWR33068 | 7209 | M3 | 108135 |  |  | 40
| 244 | 25 | Earth Work Mass Excavation to a depth as directed, in soils such as Mixture of Gravel and Soft Disintegrated Rock like Shales, Ordinary Gravel, Stoney Earth and Earth Mixed with Fair Sized Boulders and in all conditions such as dry, wet, slurry etc.and in dense or hard soils, disposal and depositing of excavated soil with intial lead of 10 mt and intial lift of 2m or as directed, including cost and conveyance of all materials, ramping and lifting of materials, and labour charges, hire charges of machinery, tools & plants, bailing of water ( either sub soil water, stoMts water, rain water, surface water or of any kind) if any at any stage of work until all works below ground level is finished to the satisfaction ,and from work such as shoring, timbering, strutting with required supports etc. for the work and removal of form work after completion of work etc all complete as directed by the engineer-incharge. | Civil | Labour | SWR33015 | 486 | M3 | 12150
| 245 | 3 | S&F of 15 mm brass body CP finish bib tap of not less than 300 grams weight with quarter turn spindle with either internal or external threaded connection conforming to IS 8931 including all operational, incidental and labour charges etc. complete for the finished item of work | Civil | Labour | SWR34330 | 684 | EA | 2052
| 246 | 20 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007) 22.20mm OD Pipe - SDR 11 including all operational, incidental and labour charges etc. complete for the finished item of work | Civil | Labour | SWR34362 | 313 | M | 6260
| 247 | 2 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) in existing Substation | Electrical | Labour | SWR11769 | 144.84 | EA | 289.68
| 248 | 2 | Supply of GI wire No 8 | Electrical | Supply | SMR11486 | 105 | KG | 210
| 249 | 2 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Electrical | Labour | SWR12331 | 146.63 | EA | 293.26
| 250 | 25 | Supply of GI Bolts & Nuts etc | Electrical | Supply | SMR11488 | 117.5 | KG | 2937.5
| 251 | 3 | Excavation of earth pit, supply of cast iron pipe with flange on one end (as per ISS7181/86) of nominal dia 125mm and 2.75 meters long in side the pit including supply and fixing RCC collars 0.75 meter dia (OD), 50mm thick and 0.60meters long complete as per APTRANSCO standards | Electrical | Labour | SWR10924 | 9804 | EA | 29412
| 252 | 3 | Supply of 33KV TC Structure as per DATA-II | Electrical | Supply | SMR40102 | 50703 | EA | 152109
| 253 | 6 | Supply of33KV BD Boom as per DATA-IV | Electrical | Supply | SMR40104 | 18244 | EA | 109464
| 254 | 3 | Erection of33KV TC Structure as per DATA-II | Electrical | Labour | SWR11010 | 17393.04 | EA | 52179.12
| 255 | 6 | Erection of 33KV TD Structure as per DATA-I | Electrical | Labour | SWR11009 | 14839.78 | EA | 89038.68
| 256 | 167 | Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc.M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) | Electrical | Labour | SWR10919 | 41 | RMT | 6847
| 257 | 24 | Supplying of Earth Mat 100x16mm GI Flat from Earth | Electrical | Supply | SMR23228 | 975 | M | 23400
| 258 | 24 | Laying of earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication100x16mm M.S./G.I earth flat | Electrical | Labour | SWR22054 | 65 | RMT | 1560
| 259 | 6 | Supply of Alluminum LA clamps conforming to A6 of IS 617, with hot dip galvanised bolts and nuts suitable for single zebra/Panther | Electrical | Supply | SMR40027 | 357 | EA | 2142
| 260 | 10 | Providing of control cable trench as per DATA-XII | Electrical | Labour | SWR22093 | 3148 | RMT | 31480
| 261 | 1 | Supply of MS Powder coated CT Marshalling Box | Electrical | Supply | SMR40047 | 3675 | EA | 3675
| 262 | 6 | Painting of feeder name on support including cost of paint | Electrical | Labour | SWR12101 | 53 | EA | 318
| 263 | 1 | Erection of Marshalling boxes | Electrical | Labour | SWR10940 | 374.85 | EA | 374.85
| 264 | 2 | Supply of 33KV 800A DB Break AB Switch | Electrical | Supply | SMR12315 | 40658.78 | EA | 81317.56
| 265 | 400 | Supply of MS Flat 50x6mm | Electrical | Supply | SMR12322 | 56.5 | KG | 22600
| 266 | 1000 | Supply of MS Channel 100x50mm | Electrical | Supply | SMR22745 | 57.45 | KG | 57450 | 1092660.2737
|  |  | Total | [5 empty] | 21188502.4313 | 21188502.4313
|  |  | 18% GST | [5 empty] | 3813930.4376
| Total Cost (Without GST)=Electrical | [7 empty] | 21188502.4313
| Total Cost (With 18 % GST)=Electrical | [7 empty] | 25002432.8689 |  | 25002432.8689
|  |  | 33KV Cable | 4350 | Mtrs
|  |  | 11 KV Cable | 4200 | Mtrs

## Jubileehills (hidden)
SCHEDULE
Name of the work: Erection, testing and commissioning of 33/11KV Indoor Sub Station with 2x 8MVA PTRs at Jubileehills, BanjaraHills Operation Division, Sherilingampally Constituency Under T& D Improvement Works.
WBS No: S-1751-12-01-01-01-001 (Electrical)
SNo | S No. | Estimate Quantity (only FigurEs) | Item DEtailEd SpEcification Description | Work Type | Item Short Descripti | Service Code | Rate | UOM | Amount
Electrical Portion
| 1 | 2 | Loading of 8MVA PTR | Elect | Labour | SWR10613 | 5805.84 | EA | 11611.68
| 2 | 2 | Transport of Power transformers (0 to 100 KM) from one place to another place inGHMC Area.(excluding of loading & unloading )-8MVA power transformer | Elect | Labour | SWR10854 | 21945 | EA | 43890
| 3 | 2 | Unloading of PTR on Constructed Plinth 8MVA PTR | Elect | Labour | SWR10627 | 5805.84 | EA | 11611.68
| 4 | 2 | Erection of PTR on constructed plinth-Erection of 8 MVA PTR. | Elect | Labour | SWR21321 | 49480.2 | EA | 98960.4
| 5 | 1 | Loading of 50,63, 75 & 100 KVA DTR | Elect | Labour | SWR10195 | 350 | EA | 350
| 6 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 3299.7
| 7 | 1 | Un loading of 50,63, 75 & 100 KVA DTR | Elect | Labour | SWR10513 | 280 | EA | 280
| 8 | 1 | Construction of DTR Plinth- RCC Column type DTR Plinth of size 1'X1'X10',topslab 4'x4'x6" & beam size 4'X8'X8" upto 160KVA | Elect | Labour | SWR21843 | 25967.57 | EA | 25967.57
| 9 | 1 | Erection of 3 Phase DTRs 63,75 & 100 KVA including loading and Unloading DTR on the Structure/Plinth etc | Elect | Labour | SWR20905 | 1650 | EA | 1650
| 10 | 16 | Loading of 11 KV VCBs along with Panel boards | Elect | Labour | SWR10199 | 1024 | EA | 16384
| 11 | 8 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 26397.6
| 12 | 16 | Un loading of 11 KV VCBs along with Panel boards | Elect | Labour | SWR10517 | 1044.48 | EA | 16711.68
| 13 | 16 | Erection of 11KV indoor switch gear panel/indoor PT panel /Bus section panel / Bus raiser panel/Capacitor panel/Switch fuse panel for DTR. | Elect | Labour | SWR10931 | 8894 | EA | 142304
| 14 | 10 | Loading of 33 KV VCBs along with Panel boards | Elect | Labour | SWR10198 | 1024 | EA | 10240
| 15 | 5 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 16498.5
| 16 | 10 | Un loading of 33 KV VCBs along with Panel boards | Elect | Labour | SWR10516 | 1044.48 | EA | 10444.8
| 17 | 10 | Erection of 33KV indoor switch gear panel/33KV indoor PT panel / Bus section panel / Bus raiser panel | Elect | Labour | SWR10930 | 9847 | EA | 98470
| 18 | 1 | Loading of 220 V Batterry with charger | Elect | Labour | SWR11166 | 1612 | SET | 1612
| 19 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 3299.7
| 20 | 1 | Un loading of 220 V Batterry with charger | Elect | Labour | SWR11147 | 1024 | SET | 1024
| 21 | 1 | Erection of 220 V, 80 AH battery in complete shape fit for charging . Conventional lead acid | Elect | Labour | SWR12295 | 7666 | EA | 7666
| 22 | 1 | Supply of AC Supply panel inluding providing of changeover switch, SFU, metering unit, 32 A three phase MCB, 16 A Single phase MCB complete as per specification. | Elect | Supply | SMR40045 | 42000 | EA | 42000
| 23 | 1 | Erection of control/Relay panels, AC Panels, announciationpanels etc in the control room duly mounting them on channels and grouting them with foundation bolts excluding cost of channels & foundation bolts | Elect | Labour | SWR11893 | 2122 | EA | 2122
| 24 | 44 | Cutting Charges for RS joist 150x150mm | Elect | Labour | SWR10297 | 48 | EA | 2112
| 25 | 0.83 | Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elect | Labour | SWR10869 | 3426 | TO | 2843.58
| 26 | 3.83 | Alligning the Main and Auxiliary structures such as RS joist,M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication. | Elect | Labour | SWR10867 | 1470 | TO | 5630.1
| 27 | 3.83 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes,labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Elect | Supply | SMR40009 | 2181 | TO | 8353.23
| 28 | 3.83 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters ofthinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes,labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Elect | Labour | SWR10877 | 851 | TO | 3259.33
| 29 | 3.83 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc | Elect | Supply | SMR40010 | 1293 | TO | 4952.19
| 30 | 3.83 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium | Elect | Labour | SWR10879 | 482 | TO | 1846.06
| 31 | 43 | Painting of Name Plates for any equipment | Elect | Labour | SWR10963 | 122 | EA | 5246
| 32 | 36 | Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Elect | Supply | SMR11482 | 3486 | EA | 125496
| 33 | 36 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 44431.2
| 34 | 36 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50M height | Elect | Labour | SWR10359 | 386 | EA | 13896
| 35 | 531.9 | Laying of MS Flats /GI Flats 75x 8mm earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment andconnecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes including fabrication | Elect | Labour | SWR10920 | 65 | RMT | 34573.5
| 36 | 208.3 | Fabrication and connecting of M.S./ G.I. Flat 50x6mm to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. | Elect | Labour | SWR10919 | 41 | RMT | 8540.3
| 37 | 50 | Supply of GI Bolts & Nuts | Elect | Supply | SMR11488 | 117.5 | KG | 5875
| 38 | 314 | Paint-Black to all Earth Flat incl. Pain | Elect | Labour | SWR12217 | 55 | M | 17270
| 39 | 2 | Supply of Copper Flexible jumper with 75 X 8 of length 250 mm at neutral of Power tranformer end and 50 X 6 of length 50mm two Nos at double neutral end duly brasing with flexible jumper of capacity of 5kA/3 sec for power transformer neutral | Elect | Supply | SMR40033 | 4725 | EA | 9450
| 40 | 2 | Providing of double earthing for neutral with flexible copper jumpers including arrangement by fixing M.S.Channel 100x50mm | Elect | Labour | SWR11892 | 1323 | EA | 2646
| 41 | 106 | Laying of 4No's single core 630 sqmm UG cable (Single Circuit with one spare cable) including excavation of trench of size 0.7 Mtrs width and 1.2 Mtrs depth from road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the siteinluding the cost of lead and lift etc.Lay-4 SC 33KV 630sqmm UG Cb HG/BC/RE/NS | Elect | Labour | SWR12110 | 2463.3 | M | 261109.8
| 42 | 56 | Raising of Single Run 33KV 1x630sqmm UG Cb on Support | Elect | Labour | SWR12448 | 133 | M | 7448
| 43 | 106 | Laying of second cable 33KV UG Cb in Existing Duct | Elect | Labour | SWR12452 | 200 | M | 21200
| 44 | 14 | Raising of 33kV 3x400 Sqmm Cu cable on already erected support with wooden / MS clamps and connecting it to over head line withcable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Elect | Labour | SWR11954 | 135.66 | M | 1899.24
| 45 | 8 | Supply of 33KV 1x630Sqmm GIS ID Unit EndTerminations | Elect | Supply | SMR12473 | 2500 | EA | 20000
| 46 | 8 | Supply of 33KV 1x630Sqmm OD Unit EndTerminations | Elect | Supply | SMR12474 | 4200 | EA | 33600
| 47 | 8 | Installation of 33KV 1x630Sqmm GIS ID EndTerminations | Elect | Labour | SWR12473 | 17600 | EA | 140800
| 48 | 8 | Installation of 33KV 1x630Sqmm OD Unit EndTerminations | Elect | Labour | SWR12474 | 4000 | EA | 32000
| 49 | 4 | Making of Outdoor/Indoor 33 KV 3x400 Sqmm End Termination | Elect | Labour | SWR10387 | 2764.76 | EA | 11059.04
| 50 | 85 | Laying of XLPE UG cable Single Run including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders/Normal soil / CC/BT Road 11KV 3x185 Sqmm Cable | Elect | Labour | SWR11920 | 465.46 | M | 39564.1
| 51 | 15 | Raising of Single RUN 11 KV 3x185 Sqmm Cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Elect | Labour | SWR11956 | 126.23 | M | 1893.45
| 52 | 2 | Making of Outdoor/Indoor 11 KV 3x185 Sqmm Cable End Termination | Elect | Labour | SWR10390 | 2370.63 | EA | 4741.26
| 53 | 90 | Laying of XLPE UG cable Single Run including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders/Normal soil / CC/BT Road LT 3 1/2 x 185 Sqmm Cable | Elect | Labour | SWR11923 | 377.63 | M | 33986.7
| 54 | 10 | Raising of Single Run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-LT 3 1/2 x 185 Sqmm Cable | Elect | Labour | SWR11959 | 85.43 | M | 854.3
| 55 | 2 | Fixing of Oout Door/Indoor end termination LT 3 1/2 x185 Sqmm Cable | Elect | Labour | SWR10765 | 968.9 | EA | 1937.8
| 56 | 2200 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends . | Elect | Labour | SWR11879 | 27 | M | 59400
| 57 | 500 | Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per specification (including cost of ferrules, lugs and glands) | Elect | Labour | SWR12510 | 27 | EA | 13500
| 58 | 1.6 | Fabrication of Main and Auxiliary structures with welding using raw steel such as RS joist, M.S.Angles, Plates, Channels, including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elect | Labour | SWR10869 | 3426 | TO | 5481.6
| 59 | 1.6 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Elect | Supply | SMR40009 | 2181 | TO | 3489.6
| 60 | 1.6 | Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Elect | Labour | SWR10877 | 851 | TO | 1361.6
| 61 | 1.6 | Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. | Elect | Supply | SMR40010 | 1293 | TO | 2068.8
| 62 | 1.6 | Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . | Elect | Labour | SWR10879 | 482 | TO | 771.2
| 63 | 5 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Elect | Labour | SWR11040 | 990.68 | EA | 4953.4
| 64 | 5 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Box pole 9/10/11 Mtr | Elect | Labour | SWR11266 | 2643.83 | EA | 13219.15
| 65 | 4.7 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.-Including the cost of cement | Elect | Labour | SWR10356 | 6579 | M3 | 30921.3
| 66 | 0.155 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Elect | Labour | SWR11890 | 3893.03 | M3 | 603.4197
| 67 | 5 | Paint of coping with 2 coats of white cement incl cost of paints etc. | Elect | Labour | SWR11089 | 48 | EA | 240
| 68 | 1 | Erection of 11 KV HG Fuse set including earthing | Elect | Labour | SWR10395 | 740.52 | SET | 740.52
| 69 | 1 | Erection of 11KV 200A TT type AB Switch including fixing of cross angles and alignment complete | Elect | Labour | SWR20102 | 1813.49 | EA | 1813.49
| 70 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.-Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elect | Labour | SWR10881 | 142 | EA | 142
| 71 | 1 | Erection of LT distribution box including laying of LT cable from distribution box to LT OH line and DTR to distribution box including earthing of distribution box and crimping of lugs connecting of jumpers etc | Elect | Labour | SWR10674 | 1594.67 | EA | 1594.67
| 72 | 18 | Supply of earthing pipe with materials GI Flat 25X3 mm | Elect | Supply | SMR11485 | 105 | KG | 1890
| 73 | 30 | Running of GI eartn flat of size 25X3mm from all metallic parts of channels, AB Switch, HG fuse set, DTr neutral and LT Distribution box and inter connection of earth pits etc complete. | Elect | Labour | SWR12125 | 14.03 | M | 420.9
| 74 | 2 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 2048
| 75 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 3299.7
| 76 | 2 | Un loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11231 | 1024 | DR | 2048
| 77 | 8 | Supply of stepped tubular poles single way made of steel of length 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9 mm, 2.1 mtrs with outer dia 76.1 mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79 kgf as per IS 2713. | Elect | Supply | SMR40051 | 13913 | EA | 111304
| 78 | 8 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rockboulders) 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M(2.6" x 2.6" x 6.0") | Elect | Labour | SWR11039 | 928 | EA | 7424
| 79 | 8 | Erection of tubular poles | Elect | Labour | SWR10955 | 1379 | EA | 11032
| 80 | 6.1 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.-Including the cost of cement | Elect | Labour | SWR10356 | 6579 | M3 | 40131.9
| 81 | 0.248 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Elect | Labour | SWR11890 | 3893 | M3 | 965.464
| 82 | 8 | Paint of coping with 2 coats of white cement incl cost of paints etc. | Elect | Labour | SWR11089 | 48 | EA | 384
| 83 | 8 | Supply of Metal Handle Lamp 150W | Elect | Supply | SMR24635 | 6450 | EA | 51600
| 84 | 50 | Supply of GI Bolts & Nuts,washers etc. | Elect | Supply | SMR11488 | 117.5 | KG | 5875
| 85 | 8 | Fixing of Metal halide lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5 GI pipe complete. | Elect | Labour | SWR10956 | 1268 | EA | 10144
| 86 | 1 | Supply of Steel almarah(61/2 X 3ft) Godrej | Elect | Supply | SMR40061 | 9818 | EA | 9818
| 87 | 750 | Supplying & fabrication erection of 6mm Checkerd plates as per the field conditions | Elect | Labour | SWR10873 | 83 | KG | 62250
| 88 | 12 | Supply of Rubber mats ( 6’x3’) size for indoor SS | Elect | Supply | SMR40068 | 1386 | EA | 16632
| 89 | 1 | Supply of Alluminium Ladder for indoor works | Elect | Supply | SMR40062 | 4410 | EA | 4410
| 90 | 2 | Supply of Trolley mounted CO2 (6.5Kgs) | Elect | Supply | SMR40087 | 9240 | EA | 18480
| 91 | 2 | Supply of Fire Buckets Stand with Buckets | Elect | Supply | SMR40088 | 1386 | SET | 2772
| 92 | 6 | Supply of Fire Extinguisher for Control Room | Elect | Supply | SMR40089 | 4620 | EA | 27720
| 93 | 4 | Supply of Safety Helmet of standard make | Elect | Supply | SMR40071 | 231 | EA | 924
| 94 | 4 | Supply of Earth Rods (8ft) Screw & clamp type | Elect | Supply | SMR40066 | 578 | EA | 2312
| 95 | 4 | Supply of Hand Gloves | Elect | Supply | SMR40067 | 289 | SET | 1156
| 96 | 1 | Supply of Stand basic cell phone with charger | Elect | Supply | SMR40069 | 1386 | EA | 1386
| 97 | 1 | Supply of Table (3x6ft) Godrej | Elect | Supply | SMR40057 | 6050 | EA | 6050
| 98 | 4 | Supply of S type chairs (Godrej) | Elect | Supply | SMR40058 | 924 | EA | 3696
| 99 | 1 | Supply of Angle racks(18x36.6inches) Godrej | Elect | Supply | SMR40060 | 1733 | EA | 1733
| 100 | 10 | Supply of Danger boards with clamps | Elect | Supply | SMR40070 | 116 | EA | 1160
| 101 | 1 | Supply of 33/11kv S.S Permanent name board | Elect | Supply | SMR40086 | 10238 | EA | 10238
| 102 | 1 | Supply of Wall clock standard make | Elect | Supply | SMR40059 | 578 | EA | 578
| 103 | 1 | Supply of Taparia Tool kit complete as per Spec | Elect | Supply | SMR40063 | 4925 | SET | 4925
| 104 | 1 | Supply of Rechargeable LED torch light. | Elect | Supply | SMR40064 | 1733 | EA | 1733
| 105 | 1 | Supply of Hack saw (12 inches) | Elect | Supply | SMR40065 | 289 | EA | 289
| 106 | 8 | Supply of LC Boards | Elect | Supply | SMR40072 | 116 | EA | 928
| 107 | 2 | Supply of Gum Boots | Elect | Supply | SMR40073 | 693 | EA | 1386
| 108 | 1 | Supply of Digital clamp meter. | Elect | Supply | SMR40076 | 2888 | EA | 2888
| 109 | 1 | Supply of 5000v megger | Elect | Supply | SMR40074 | 13860 | EA | 13860
| 110 | 1 | Supply &fixing of board ind Switchyard layout | Elect | Labour | SWR20032 | 1654 | EA | 1654
| 111 | 1 | Supply & fixing safety inst/SS Op. inst board | Elect | Labour | SWR22090 | 2205 | EA | 2205
| 112 | 1 | Supply of 10ft Aluminium Ladder | Elect | Supply | SMR12378 | 1654 | EA | 1654
| 113 | 3000 | Supply of RS Joist Grider Pole (150x150mm) | Elect | Supply | SMR12302 | 59.25 | KG | 177750
| 114 | 830 | Supply of MS Channel 100x50mm | Elect | Supply | SMR22745 | 57.45 | KG | 47683.5
| 115 | 2500 | Supply of MS Flat 75x8mm | Elect | Supply | SMR12321 | 56.42 | KG | 141050
| 116 | 500 | Supply of MS Flat 50x6mm | Elect | Supply | SMR12322 | 56.5 | KG | 28250
| 117 | 400 | Supply of MS Channel 100x50mm | Elect | Supply | SMR22745 | 57.45 | KG | 22980
| 118 | 2 | Supply of 33KV 3x400Sqmm O/D End Kit | Elect | Supply | SMR22222 | 4554 | EA | 9108
| 119 | 2 | Supply of of 33KV 3x400Sqmm Indoor end kit | Elect | Supply | SMR11506 | 3589.96 | EA | 7179.92
| 120 | 1 | Supply of 11KV 3x185 Heat Shble O/d End Term Kit | Elect | Supply | SMR25201 | 1182.97 | EA | 1182.97
| 121 | 1 | Supply of 11KV 3x185 Heat Shble I/d End Term Kit | Elect | Supply | SMR25202 | 1085 | EA | 1085
| 122 | 100 | Supply of LT XLPE Cable 3 1/2 C 185 sqmm | Elect | Supply | SMR25204 | 547 | M | 54700
| 123 | 1500 | Supply of RS Joist Pole (175x85mm) | Elect | Supply | SMR12303 | 60.75 | KG | 91125
| 124 | 100 | Supply of MS Channel 75x40 mm | Elect | Supply | SMR25205 | 58.45 | KG | 5845
| 125 | 1 | Supply of 11KV HG FuseSet for StationTransformer | Elect | Supply | SMR12324 | 1974 | EA | 1974
| 126 | 1 | Supply of 11KV 200A Tilting Type AB Switch | Elect | Supply | SMR12318 | 8991 | EA | 8991
| 127 | 1 | Supply of LT Distribution Box (SMC) | Elect | Supply | SMR25200 | 7797 | EA | 7797
| 128 | 60 | Supply of LT XLPE Cable 1C 150 sqmm | Elect | Supply | SMR25203 | 114.83 | M | 6889.8 | 2706605.3936 | SS LABOUR
| 129 | 1 | survey line&cabl inc peg mark&tree clear | Elect | Labour | SWR22092 | 765 | KM | 765
| 130 | 27 | Load-11/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 27648
| 131 | 27 | Unload-11/33KV XLPE UG Cable all sizes | Elect | Labour | SWR11231 | 1024 | DR | 27648
| 132 | 14 | Transport of Cond Drum,VCBs upto 10Km | Elect | Labour | SWR11860 | 2720.34 | EA | 38084.76
| 133 | 4000 | Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters ,providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet,3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts,Along the CC / BT multi layer road requiring compressor for 33 KV 3x400 Sqmm Cable | Elect | Labour | SWR11980 | 1388.84 | M | 5555360
| 134 | 4000 | Laying of 2nd Cable in Excavated Trench | Elect | Labour | SWR10988 | 204.1 | M | 816400
| 135 | 40 | Supply & Erection of Smart RFID marker | Elect | Labour | SWR25089 | 2745 | EA | 109800
| 136 | 32 | Making of Straight through joint 33kv 3x400 xlpe | Elect | Labour | SWR10382 | 5700.78 | EA | 182424.96
| 137 | 1616 | Supply of 6" B class GI pipe | Elect | Supply | SMR40081 | 1044 | M | 1687104
| 138 | 100 | Supply of 6" DWC pipe | Elect | Supply | SMR11610 | 1012 | M | 101200
| 139 | 100 | Supply of Hume pipe 9" size | Elect | Supply | SMR40001 | 125 | M | 12500
| 140 | 12 | Making of OD/Idoor end termination 33kv 3x400 xlpe | Elect | Labour | SWR10387 | 2764.76 | EA | 33177.12
| 141 | 80 | Raising of single run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)33KV 3x400sqmm UG Cb on support | Elect | Labour | SWR11954 | 135.66 | M | 10852.8
| 142 | 4000 | Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours. | Elect | Labour | SWR21903 | 30 | M | 120000
| 143 | 12 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Elect | Labour | SWR10642 | 512.55 | EA | 6150.6
| 144 | 12 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Elect | Labour | SWR10640 | 1132 | EA | 13584
| 145 | 6 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Elect | Labour | SWR11040 | 990.68 | EA | 5944.08
| 146 | 2 | Erection of 9/10/11Meter Box pole | Elect | Labour | SWR11266 | 2643.83 | EA | 5287.66
| 147 | 208.3 | Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc.M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) | Elect | Labour | SWR10919 | 41 | RMT | 8540.3
| 148 | 5.64 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.Including the cost of cement | Elect | Labour | SWR10356 | 6579 | M3 | 37105.56
| 149 | 0.186 | Coping & Muffing-Iron Pole,Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes(0.031Cumt.) | Elect | Labour | SWR11890 | 3893.01 | M3 | 724.0999
| 150 | 0.6 | Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elect | Labour | SWR10869 | 3426 | TO | 2055.6
| 151 | 2 | Erection of 33 KV LAS station/Line type including earthing | Elect | Labour | SWR10396 | 880 | SET | 1760
| 152 | 2 | Erection of 33 KV AB Switch including alignment and earthing | Elect | Labour | SWR10392 | 4500 | EA | 9000
| 153 | 4 | Supply of CI Pipe earthing 80mm dia 2.75m long | Elect | Supply | SMR11483 | 2789 | EA | 11156
| 154 | 4 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and | Elect | Labour | SWR10357 | 1234.2 | EA | 4936.8
| 155 | 4 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Elect | Labour | SWR10359 | 386 | EA | 1544
| 156 | 40 | Supply of Pre-cast cable Joint markersSupply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters , CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | Elect | Supply | SMR40085 | 484 | EA | 19360
| 157 | 6 | Painting of feeder name on support including cost of paint | Elect | Labour | SWR12101 | 53 | EA | 318
| 158 | 100 | Supply of GI Bolts & Nuts,Washers etc., | Elect | Supply | SMR11488 | 117.5 | KG | 11750
| 159 | 2 | AB Switch Coil Earthing GI No. 8 Wire | Elect | Labour | SWR12331 | 146.63 | EA | 293.26
| 160 | 2 | Painting AB switch OP rods with PO red | Elect | Labour | SWR10881 | 142 | EA | 284
| 161 | 2 | Assembly and erection of Structure as per specification which includes fixing of top channels and cross bracings, transport of all materials from road side to the location, earthing, back filling with earth ramming etc excluding pit excavation and concreting.33 KV DP Structure with 175x85/150x75mm RS joist | Elect | Labour | SWR11276 | 5670 | SET | 11340
| 162 | 6 | Loading of 33 KV, 10 KA LAs Station type | Elect | Labour | SWR10266 | 41 | EA | 246
| 163 | 6 | Un loading of 33 KV, 10 KA LAs Station type | Elect | Labour | SWR10584 | 35 | EA | 210
| 164 | 6 | Supply of 33KV 1Cx400Sqmm PlugTerminationKit | Elect | Supply | SMR24773 | 90915 | EA | 545490
| 165 | 6 | Making of Outdoor/Indoor End Termination, Installation of 33KV 1Cx400Sqmm PlugTerminationKit | Elect | Labour | SWR24773 | 15675 | EA | 94050
| 166 | 32 | Supply of 33KV3x400Sqmm Straight thr kit | Elect | Supply | SMR22223 | 24151 | EA | 772832
| 167 | 8 | Supply of 33KV 3x400Sqmm O/D End Kit | Elect | Supply | SMR22222 | 4554 | EA | 36432
| 168 | 4 | Supply of 33KV 3x400Sqmm Indoor end kit | Elect | Supply | SMR11506 | 3589.96 | EA | 14359.84
| 169 | 3000 | Supply of RS Joist Pole (175x85mm) | Elect | Supply | SMR12303 | 60.75 | KG | 182250
| 170 | 500 | Supply of MS Flat 50x6mm | Elect | Supply | SMR12322 | 56.5 | KG | 28250
| 171 | 600 | Supply of MS Channel 100x50mm | Elect | Supply | SMR22745 | 57.45 | KG | 34470
| 172 | 2 | Supply of 33KV 800A DB Break AB Switch | Elect | Supply | SMR12315 | 40658.78 | EA | 81317.56 | 10664005.9999 | 33KV LINE LABOUR
| 173 | 1 | survey line&cabl inc peg mark&tree clear | Elect | Labour | SWR22092 | 765 | KM | 765
| 174 | 11 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 11264
| 175 | 11 | Un loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11231 | 1024 | DR | 11264
| 176 | 6 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 19798.2
| 177 | 3120 | Laying of Single Run XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.Along the CC / BT multi layer road requiring compressor for 11 KV 3x300 Sqmm Cable | Elect | Labour | SWR11928 | 1073.94 | M | 3350692.8
| 178 | 80 | Raising of Single Run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)11 KV 3x300 Sqmm Cable | Elect | Labour | SWR11955 | 144.08 | M | 11526.4
| 179 | 32 | Supply & Erection of Smart RFID marker | Elect | Labour | SWR25089 | 2745 | EA | 87840
| 180 | 13 | Making of Straight through joint 11kv 3x300 xlpe | Elect | Labour | SWR10386 | 3725.45 | EA | 48430.85
| 181 | 640 | Supply of 4" B class GI pipe | Elect | Supply | SMR40080 | 740 | M | 473600
| 182 | 100 | supply of 4" DWC pipe | Elect | Supply | SMR11609 | 759 | M | 75900
| 183 | 200 | Suppy of Hume pipe 4" size | Elect | Supply | SMR40003 | 80 | M | 16000
| 184 | 16 | Making 11 KV 3x300 Sqmm Cable Out Door/Indoor end termination | Elect | Labour | SWR10391 | 2370.63 | EA | 37930.08
| 185 | 3120 | Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during latenight hours and wee hours. | Elect | Labour | SWR21903 | 30 | M | 93600
| 186 | 16 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost ofconsumable. | Elect | Labour | SWR10642 | 512.55 | EA | 8200.8
| 187 | 16 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Elect | Labour | SWR10640 | 1132 | EA | 18112
| 188 | 8 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Elect | Labour | SWR11040 | 990.68 | EA | 7925.44
| 189 | 8 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Box pole 9/10/11 Mtr | Elect | Labour | SWR11266 | 2643.83 | EA | 21150.64
| 190 | 208.33 | Fabrication and connecting to risers from earth mat to structures, equipment,marshalling boxes, electrical panels, PLCC panels, fencing posts etc.M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) | Elect | Labour | SWR10919 | 41 | RMT | 8541.53
| 191 | 7.52 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.Including the cost of cement | Elect | Labour | SWR10356 | 6579 | M3 | 49474.08
| 192 | 0.248 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Elect | Labour | SWR11890 | 3892.98 | M3 | 965.459
| 193 | 0.9 | Fabrication of Main and Auxiliary structures with welding using raw steel such as RS joist, M.S.Angles, Plates, Channels, including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elect | Labour | SWR10869 | 3426 | TO | 3083.4
| 194 | 8 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Elect | Labour | SWR10393 | 3200 | EA | 25600
| 195 | 8 | Supply of CI eath pipe with 80mm dia,2.0 M Length | Elect | Supply | SMR11483 | 2789 | EA | 22312
| 196 | 8 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 9873.6
| 197 | 8 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Elect | Labour | SWR10359 | 386 | EA | 3088
| 198 | 32 | Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters , CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | Elect | Supply | SMR40085 | 484 | EA | 15488
| 199 | 8 | Painting of feeder name on support including cost of paint | Elect | Labour | SWR12101 | 53 | EA | 424
| 200 | 100 | Supply of GI Bolts & Nuts,Washers etc., | Elect | Supply | SMR11488 | 117.5 | KG | 11750
| 201 | 8 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Elect | Labour | SWR12331 | 146.63 | EA | 1173.04
| 202 | 8 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elect | Labour | SWR10881 | 142 | EA | 1136
| 203 | 13 | Supply of 11KV 3x300 Heat Shble str thr JointKit | Elect | Supply | SMR25210 | 4110.17 | EA | 53432.21
| 204 | 8 | Supply of 11KV 3x300 Heat Shble O/d End Term Kit | Elect | Supply | SMR25208 | 1372.88 | EA | 10983.04
| 205 | 8 | Supply of 11KV 3x300 Heat Shble I/d End Term Kit | Elect | Supply | SMR25209 | 1459.83 | EA | 11678.64
| 206 | 4000 | Supply of RS Joist Pole (175x85mm) | Elect | Supply | SMR12303 | 60.75 | KG | 243000
| 207 | 500 | Supply of MS Flat 50x6mm | Elect | Supply | SMR12322 | 56.5 | KG | 28250
| 208 | 600 | Supply of MS Channel 75x40 mm | Elect | Supply | SMR25205 | 58.45 | KG | 35070
| 209 | 300 | Supply of MS Angle 65X65X6 | Elect | Supply | SMR25207 | 57.25 | KG | 17175
| 210 | 8 | Supply of 11KV 800A DB Break AB Switch | Elect | Supply | SMR12316 | 30847.46 | EA | 246779.68 | 5093277.889 | 11KV LINE LABOUR
| 211 | 2 | Erection of 33 KV AB Switch including alignment and earthing | Elect | Labour | SWR10392 | 4500 | EA | 9000
| 212 | 1 | Erection of 33 KV LAS station/Line type including earthing | Elect | Labour | SWR10396 | 880 | SET | 880
| 213 | 1 | Loading of 33 KV VCBs along with Panel boards | Elect | Labour | SWR10198 | 1024 | EA | 1024
| 214 | 1 | Un loading of 33 KV VCBs along with Panel boards | Elect | Labour | SWR10516 | 1044.48 | EA | 1044.48
| 215 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 3299.7
| 216 | 4.8 | Excavation of Pit for 33KV VCB | Elect | Labour | SWR23224 | 331 | M3 | 1588.8
| 217 | 6 | Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x 1.8 x 0.75 cum for VCB Plinth | Elect | Labour | SWR20685 | 5160 | M3 | 30960
| 218 | 6.4 | Plastering 2 Coats,20/16mm(1:6)(1:4) | Elect | Labour | SWR10862 | 373 | M2 | 2387.2
| 219 | 1 | Painting of coping with two coats of white cement including cost of paint & conveyance charges for PTR/VCB plinths | Elect | Labour | SWR12334 | 160 | EA | 160
| 220 | 1 | Erection of 33 KV VCB with Control Panel | Elect | Labour | SWR10460 | 12500 | EA | 12500
| 221 | 1 | Erection of 33 KV CTs | Elect | Labour | SWR10399 | 1079 | SET | 1079
| 222 | 1 | Erection of 33kV Twin feeder control & Relay panel in the control room duly mounting them on channels and grouting them with foundation bolts excluding cost of channels & foundation bolts | Elect | Labour | SWR10934 | 1729 | EA | 1729
| 223 | 2 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rockboulders)9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Elect | Labour | SWR11039 | 928 | EA | 1856
| 224 | 1.526 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.Including the cost of cement | Elect | Labour | SWR10356 | 6579 | M3 | 10039.554
| 225 | 0.062 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Elect | Labour | SWR11890 | 3893.06 | M3 | 241.3697
| 226 | 2 | Supply of stepped tubular poles single way made of steel oflength 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9 mm, 2.1 mtrs with outer dia 76.1 mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79 kgf as per IS 2713. | Elect | Supply | SMR40051 | 13913 | EA | 27826
| 227 | 2 | Erection of tubular poles | Elect | Labour | SWR10955 | 1379 | EA | 2758
| 228 | 2 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTUREROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA/OSRAM/SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years arranty 90W LED Fixture set | Elect | Supply | SMR11594 | 8200 | EA | 16400
| 229 | 2 | Fixing of Metal halide lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5 GI pipe complete | Elect | Labour | SWR10956 | 1268 | EA | 2536
| 230 | 21 | Labour for Fixing of all types of clamps | Elect | Labour | SWR10917 | 65 | EA | 1365
| 231 | 1200 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends | Elect | Labour | SWR11879 | 27 | EA | 32400
| 232 | 0.08 | Extention of 33KV Bay at 132/33KV Sub-station Zebra condutor | Elect | Supply | SMR24910 | 299369 | KM | 23949.52
| 233 | 9 | Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | Elect | Labour | SWR10884 | 224 | EA | 2016
| 234 | 6 | Supply of I hook | Elect | Supply | SMR12099 | 158 | EA | 948
| 235 | 6 | Erection of I hook | Elect | Labour | SWR12099 | 55 | EA | 330
| 236 | 3 | Supply of Spacer T-Clamps with double dropper suitable for Zebra / Panther | Elect | Supply | SMR40013 | 788 | EA | 2364
| 237 | 6 | Supply of Tension Hardware 3 Bolted for Twin Zebra/panther with 150 mm spacing | Elect | Supply | SMR40016 | 2512 | EA | 15072
| 238 | 12 | Alluminum alloy Pad clamps minimum 15 mm Thickness, 75 mm Width 150 Mm Length conforming to IS:5561-1970, IS 617, IS 2633-1964, IS 1363-1967, IS1367-1961), Six bolted with hot dip galvanized bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 ") minimum weight of 900 gms to suit for Panther ACSR Conductor of pad size 75 X 75 X 15mm for carrying 600 A current | Elect | Supply | SMR24942 | 360 | EA | 4320
| 239 | 6 | Supply of CT stud clamps with hot dip galvanised bolts and nuts suitable for zebra / Panther conductor on one side and 28/30/40 mm CT stud on other side with stud size for single zebra / panther (4 bolted) with bimetallic sleeve for carrying 800 A | Elect | Supply | SMR40023 | 399 | EA | 2394
| 240 | 6 | Supply of U-Bolts 16 mm | Elect | Supply | SMR40040 | 37 | EA | 222
| 241 | 43 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 33 kV bus comprising of three phases with Twin Zebra/Panther conductor to a tension of 900kgs including fixing of spacer clamps.(Bus section of 4.5mt) | Elect | Labour | SWR10882 | 1302 | EA | 55986
| 242 | 2 | Room fire extinguisher (2 ltrs capacity) for control room | Elect | Supply | SMR40089 | 4620 | EA | 9240
| 243 | 6 | Supply & spreading of 20mm machine crushed metal (HBG) including cost of conveneyance of all materials, labour charges etc complete for finished item of work and directed by the engineer incharge | Elect | Labour | SWR10860 | 2113 | M3 | 12678
| 244 | 6 | Supply &Filling with Borrowed Stone Dust | Elect | Labour | SWR33054 | 1062 | M3 | 6372
| 245 | 15 | Brick masonry in cement mortar (1:6) for superstructure using well burnt country made second class bricks of approved quality including cost and conveyance of all materials curing, scaffolding with all leads and lifts etc., complete for finished item of work - Ground Floor | Civil | Labour | SWR33068 | 7209 | M3 | 108135
| 246 | 25 | Earth Work Mass Excavation to a depth as directed, in soils such as Mixture of Gravel and Soft Disintegrated Rock like Shales, Ordinary Gravel, Stoney Earth and Earth Mixed with Fair Sized Boulders and in all conditions such as dry, wet, slurry etc.and in dense or hard soils, disposal and depositing of excavated soil with intial lead of 10 mt and intial lift of 2m or as directed, including cost and conveyance of all materials, ramping and lifting of materials, and labour charges, hire charges of machinery, tools & plants, bailing of water ( either sub soil water, stoMts water, rain water, surface water or of any kind) if any at any stage of work until all works below ground level is finished to the satisfaction ,and from work such as shoring, timbering, strutting with required supports etc. for the work and removal of form work after completion of work etc all complete as directed by the engineer-incharge. | Civil | Labour | SWR33015 | 486 | M3 | 12150
| 247 | 3 | S&F of 15 mm brass body CP finish bib tap of not less than 300 grams weight with quarter turn spindle with either internal or external threaded connection conforming to IS 8931 including all operational, incidental and labour charges etc. complete for the finished item of work | Civil | Labour | SWR34330 | 684 | EA | 2052
| 248 | 20 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007) 22.20mm OD Pipe - SDR 11 including all operational, incidental and labour charges etc. complete for the finished item of work | Civil | Labour | SWR34362 | 313 | M | 6260
| 249 | 2 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) in existing Substation | Elect | Labour | SWR11769 | 144.84 | EA | 289.68
| 250 | 2 | Supply of GI wire No 8 | Elect | Supply | SMR11486 | 105 | KG | 210
| 251 | 2 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Elect | Labour | SWR12331 | 146.63 | EA | 293.26
| 252 | 25 | Supply of GI Bolts & Nuts etc | Elect | Supply | SMR11488 | 117.5 | KG | 2937.5
| 253 | 3 | Excavation of earth pit, supply of cast iron pipe with flange on one end (as per ISS7181/86) of nominal dia 125mm and 2.75 meters long in side the pit including supply and fixing RCC collars 0.75 meter dia (OD), 50mm thick and 0.60meters long complete as per APTRANSCO standards | Elect | Labour | SWR10924 | 9804 | EA | 29412
| 254 | 3 | Supply of 33KV TC Structure as per DATA-II | Elect | Supply | SMR40102 | 50703 | EA | 152109
| 255 | 6 | Supply of33KV BD Boom as per DATA-IV | Elect | Supply | SMR40104 | 18244 | EA | 109464
| 256 | 3 | Erection of33KV TC Structure as per DATA-II | Elect | Labour | SWR11010 | 17393.04 | EA | 52179.12
| 257 | 6 | Erection of 33KV TD Structure as per DATA-I | Elect | Labour | SWR11009 | 14839.78 | EA | 89038.68
| 258 | 167 | Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc.M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) | Elect | Labour | SWR10919 | 41 | RMT | 6847
| 259 | 24 | Supplying of Earth Mat 100x16mm GI Flat from Earth | Elect | Supply | SMR23228 | 975 | M | 23400
| 260 | 24 | Laying of earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication100x16mm M.S./G.I earth flat | Elect | Labour | SWR22054 | 65 | RMT | 1560
| 261 | 6 | Supply of Alluminum LA clamps conforming to A6 of IS 617, with hot dip galvanised bolts and nuts suitable for single zebra/Panther | Elect | Supply | SMR40027 | 357 | EA | 2142
| 262 | 10 | Providing of control cable trench as per DATA-XII | Elect | Labour | SWR22093 | 3148 | RMT | 31480
| 263 | 1 | Supply of MS Powder coated CT Marshalling Box | Elect | Supply | SMR40047 | 3675 | EA | 3675
| 264 | 6 | Painting of feeder name on support including cost of paint | Elect | Labour | SWR12101 | 53 | EA | 318
| 265 | 1 | Erection of Marshalling boxes | Elect | Labour | SWR10940 | 374.85 | EA | 374.85
| 266 | 2 | Supply of 33KV 800A DB Break AB Switch | Elect | Supply | SMR12315 | 40658.78 | EA | 81317.56
| 267 | 400 | Supply of MS Flat 50x6mm | Elect | Supply | SMR12322 | 56.5 | KG | 22600
| 268 | 1000 | Supply of MS Channel 100x50mm | Elect | Supply | SMR22745 | 57.45 | KG | 57450 | 1092660.2737 | 132KV BAY EXTENSION
|  |  | Total | [5 empty] | 19556549.5563 | 19556549.5563
|  |  | 18% GST | [5 empty] | 3520178.9201
| Total Cost (Without GST)=Electrical | [7 empty] | 19556549.5563
| Total Cost (With 18 % GST)=Electrical | [7 empty] | 23076728.4764
|  |  | 33KV Cable | 4000 | Mtrs
|  |  | 11 KV Cable | 3120 | Mtrs
33 KV Cable
11KV Cable

## Madhapur TGIIC (hidden)
SCHEDULE
Name of the work: Erection, testing and commissioning of 33/11KV Indoor Sub Station with 2x 8MVA PTRs at MADHAPUR area under TGIIC, BanjaraHills Operation Division, Sherilingampally Constituency Under T& D Improvement Works.
WBS No: S-1752-12-01-01-01-001 (Electrical)
SNo | S No. | Estimate Quantity (only FigurEs) | Item DEtailEd SpEcification Description | Work Type | Item Short Descripti | Service Code | Rate | UOM | Amount
Electrical Portion
| 1 | 2 | Loading of 8MVA PTR | Elect | Labour | SWR10613 | 5805.84 | EA | 11611.68
| 2 | 2 | Transport of Power transformers (0 to 100 KM) from one place to another place in GHMC Area.(excluding of loading & unloading )-8MVA power transformer | Elect | Labour | SWR10854 | 21945 | EA | 43890
| 3 | 2 | Unloading of PTR on constructed plinth 8MVA PTR | Elect | Labour | SWR10627 | 5805.84 | EA | 11611.68
| 4 | 2 | Erection of PTR on constructed plinth-Erection of 8 MVA PTR. | Elect | Labour | SWR21321 | 49480.2 | EA | 98960.4
| 5 | 1 | Loading of 50,63, 75 & 100 KVA DTR | Elect | Labour | SWR10195 | 350 | EA | 350
| 6 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 3299.7
| 7 | 1 | Un loading of 50,63, 75 & 100 KVA DTR | Elect | Labour | SWR10513 | 280 | EA | 280
| 8 | 1 | Construction of DTR Plinth- RCC Column type DTR Plinth of size 1'X1'X10',topslab 4'x4'x6" & beam size 4'X8'X8" upto 160KVA | Elect | Labour | SWR21843 | 25967.57 | EA | 25967.57
| 9 | 1 | Erection of 3 Phase DTRs 63,75 & 100 KVA including loading and Unloading DTR on the Structure/Plinth etc | Elect | Labour | SWR20905 | 1650 | EA | 1650
| 10 | 16 | Loading of 11 KV VCBs along with Panel boards | Elect | Labour | SWR10199 | 1024 | EA | 16384
| 11 | 8 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 26397.6
| 12 | 16 | Un loading of 11 KV VCBs along with Panel boards | Elect | Labour | SWR10517 | 1044.48 | EA | 16711.68
| 13 | 16 | Erection of 11KV indoor switch gear panel/indoor PT panel /Bus section panel / Bus raiser panel/Capacitor panel/Switch fuse panel for DTR. | Elect | Labour | SWR10931 | 8894 | EA | 142304
| 14 | 10 | Loading of 33 KV VCBs along with Panel boards | Elect | Labour | SWR10198 | 1024 | EA | 10240
| 15 | 5 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 16498.5
| 16 | 10 | Un loading of 33 KV VCBs along with Panel boards | Elect | Labour | SWR10516 | 1044.48 | EA | 10444.8
| 17 | 10 | Erection of 33KV indoor switch gear panel/33KV indoor PT panel / Bus section panel / Bus raiser panel | Elect | Labour | SWR10930 | 9847 | EA | 98470
| 18 | 1 | Loading of 220 V Batterry with charger | Elect | Labour | SWR11166 | 1612 | SET | 1612
| 19 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 3299.7
| 20 | 1 | Un loading of 220 V Batterry with charger | Elect | Labour | SWR11147 | 1024 | SET | 1024
| 21 | 1 | Erection of 220 V, 80 AH battery in complete shape fit for charging . Conventional lead acid | Elect | Labour | SWR12295 | 7666 | EA | 7666
| 22 | 1 | Supply of AC Supply panel inluding providing of changeover switch, SFU, metering unit, 32 A three phase MCB, 16 A Single phase MCB complete as per specification. | Elect | Supply | SMR40045 | 42000 | EA | 42000
| 23 | 1 | Erection of control/Relay panels, AC Panels, announciationpanels etc in the control room duly mounting them on channels and grouting them with foundation bolts excluding cost of channels & foundation bolts | Elect | Labour | SWR11893 | 2122 | EA | 2122
| 24 | 44 | Cutting Charges for RS joist 150x150mm | Elect | Labour | SWR10297 | 48 | EA | 2112
| 25 | 0.83 | Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elect | Labour | SWR10869 | 3426 | TO | 2843.58
| 26 | 3.83 | Alligning the Main and Auxiliary structures such as RS joist,M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication. | Elect | Labour | SWR10867 | 1470 | TO | 5630.1
| 27 | 3.83 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes,labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Elect | Supply | SMR40009 | 2181 | TO | 8353.23
| 28 | 3.83 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters ofthinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes,labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Elect | Labour | SWR10877 | 851 | TO | 3259.33
| 29 | 3.83 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc | Elect | Supply | SMR40010 | 1293 | TO | 4952.19
| 30 | 3.83 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium | Elect | Labour | SWR10879 | 482 | TO | 1846.06
| 31 | 43 | Painting of Name Plates for any equipment | Elect | Labour | SWR10963 | 122 | EA | 5246
| 32 | 36 | Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Elect | Supply | SMR11482 | 3486 | EA | 125496
| 33 | 36 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 44431.2
| 34 | 36 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50M height | Elect | Labour | SWR10359 | 386 | EA | 13896
| 35 | 531.9 | Laying of MS Flats /GI Flats 75x 8mm earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment andconnecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes including fabrication | Elect | Labour | SWR10920 | 65 | RMT | 34573.5
| 36 | 208.3 | Fabrication and connecting of M.S./ G.I. Flat 50x6mm to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. | Elect | Labour | SWR10919 | 41 | RMT | 8540.3
| 37 | 50 | Supply of GI Bolts & Nuts | Elect | Supply | SMR11488 | 117.5 | KG | 5875
| 38 | 314 | Paint-Black to all Earth Flat incl. Pain | Elect | Labour | SWR12217 | 55 | M | 17270
| 39 | 2 | Supply of Copper Flexible jumper with 75 X 8 of length 250 mm at neutral of Power tranformer end and 50 X 6 of length 50mm two Nos at double neutral end duly brasing with flexible jumper of capacity of 5kA/3 sec for power transformer neutral | Elect | Supply | SMR40033 | 4725 | EA | 9450
| 40 | 2 | Providing of double earthing for neutral with flexible copper jumpers including arrangement by fixing M.S.Channel 100x50mm | Elect | Labour | SWR11892 | 1323 | EA | 2646
| 41 | 106 | Laying of 4No's single core 630 sqmm UG cable (Single Circuit with one spare cable)including excavation of trench of size 0.7 Mtrs width and 1.2 Mtrs depth from road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.Lay-4 SC 33KV 630sqmm UG Cb HG/BC/RE/NS | Elect | Labour | SWR12110 | 2463.3 | M | 261109.8
| 42 | 56 | Raising of Single Run 33KV 1x630sqmm UG Cable on Support | Elect | Labour | SWR12448 | 133 | M | 7448
| 43 | 106 | Laying of second 33KV UG Cable in Existing Duct | Elect | Labour | SWR12452 | 200 | M | 21200
| 44 | 14 | Raising of 33kV 3x400 Sqmm Cu cable on already erected support with wooden / MS clamps and connecting it to over head line withcable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Elect | Labour | SWR11954 | 135.66 | M | 1899.24
| 45 | 8 | Supply of 33KV 1x630Sqmm GIS ID Unit End Terminations | Elect | Supply | SMR12473 | 2500 | EA | 20000
| 46 | 8 | Supply of 33KV 1x630Sqmm OD Unit End Terminations | Elect | Supply | SMR12474 | 4200 | EA | 33600
| 47 | 8 | Installation of 33KV 1x630Sqmm GIS ID End Terminations | Elect | Labour | SWR12473 | 17600 | EA | 140800
| 48 | 8 | Installation of 33KV 1x630Sqmm OD Unit EndTerminations | Elect | Labour | SWR12474 | 4000 | EA | 32000
| 49 | 4 | Making of Outdoor/Indoor 33 KV 3x400 Sqmm End Termination | Elect | Labour | SWR10387 | 2764.76 | EA | 11059.04
| 50 | 85 | Laying of XLPE UG cable Single Run including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders/Normal soil / CC/BT Road 11KV 3x185 Sqmm Cable | Elect | Labour | SWR11920 | 465.46 | M | 39564.1
| 51 | 15 | Raising of Single Run 11 KV 3x185 Sqmm Cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Elect | Labour | SWR11956 | 126.23 | M | 1893.45
| 52 | 2 | Making of Outdoor/Indoor 11 KV 3x185 Sqmm Cable End Termination | Elect | Labour | SWR10390 | 2370.63 | EA | 4741.26
| 53 | 90 | Laying of XLPE UG cable Single Run including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders/Normal soil / CC/BT Road LT 3 1/2 x 185 Sqmm Cable | Elect | Labour | SWR11923 | 377.63 | M | 33986.7
| 54 | 10 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-LT 3 1/2 x 185 Sqmm Cable | Elect | Labour | SWR11959 | 85.43 | M | 854.3
| 55 | 2 | Fixing of Oout Door/Indoor end termination LT 3 1/2 x185 Sqmm Cable | Elect | Labour | SWR10765 | 968.9 | EA | 1937.8
| 56 | 2200 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends . | Elect | Labour | SWR11879 | 27 | M | 59400
| 57 | 500 | Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per specification (including cost of ferrules, lugs and glands) | Elect | Labour | SWR12510 | 27 | EA | 13500
| 58 | 1.6 | Fabrication of Main and Auxiliary structures with welding using raw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to theRS-Joist poles excluding cost of Mild Steel and transportcharges to substation site, including erection. | Elect | Labour | SWR10869 | 3426 | TO | 5481.6
| 59 | 1.6 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Elect | Supply | SMR40009 | 2181 | TO | 3489.6
| 60 | 1.6 | Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Elect | Labour | SWR10877 | 851 | TO | 1361.6
| 61 | 1.6 | Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. | Elect | Supply | SMR40010 | 1293 | TO | 2068.8
| 62 | 1.6 | Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . | Elect | Labour | SWR10879 | 482 | TO | 771.2
| 63 | 5 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Elect | Labour | SWR11040 | 990.68 | EA | 4953.4
| 64 | 5 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Box pole 9/10/11 Mtr | Elect | Labour | SWR11266 | 2643.83 | EA | 13219.15
| 65 | 4.7 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.-Including the cost of cement | Elect | Labour | SWR10356 | 6579 | M3 | 30921.3
| 66 | 0.155 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Elect | Labour | SWR11890 | 3893.03 | M3 | 603.4197
| 67 | 5 | Paint of coping with 2 coats of white cement incl cost of paints etc. | Elect | Labour | SWR11089 | 48 | EA | 240
| 68 | 1 | Erection of 11 KV HG Fuse set including earthing | Elect | Labour | SWR10395 | 740.52 | SET | 740.52
| 69 | 1 | Erection of 11KV 200A TT type AB Switch including fixing of cross angles and alignment complete | Elect | Labour | SWR20102 | 1813.49 | EA | 1813.49
| 70 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.-Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elect | Labour | SWR10881 | 142 | EA | 142
| 71 | 1 | Erection of LT distribution box including laying of LT cable from distribution box to LT OH line and DTR to distribution box including earthing of distribution box and crimping of lugs connecting of jumpers etc | Elect | Labour | SWR10674 | 1594.67 | EA | 1594.67
| 72 | 18 | Supply of GI Flat 25X3 mm | Elect | Supply | SMR11485 | 105 | KG | 1890
| 73 | 30 | Running of GI eartn flat of size 25X3mm from all metallic parts of channels, AB Switch, HG fuse set, DTr neutral and LT Distribution box and inter connection of earth pits etc complete. | Elect | Labour | SWR12125 | 14.03 | M | 420.9
| 74 | 2 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 2048
| 75 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 3299.7
| 76 | 2 | Un loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11231 | 1024 | DR | 2048
| 77 | 8 | Supply of stepped tubular poles single way made of steel of length 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9 mm, 2.1 mtrs with outer dia 76.1 mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79 kgf as per IS 2713. | Elect | Supply | SMR40051 | 13913 | EA | 111304
| 78 | 8 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rockboulders) 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M(2.6" x 2.6" x 6.0") | Elect | Labour | SWR11039 | 928 | EA | 7424
| 79 | 8 | Erection of tubular poles | Elect | Labour | SWR10955 | 1379 | EA | 11032
| 80 | 6.1 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.-Including the cost of cement | Elect | Labour | SWR10356 | 6579 | M3 | 40131.9
| 81 | 0.248 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Elect | Labour | SWR11890 | 3892.98 | M3 | 965.459
| 82 | 8 | Paint of coping with 2 coats of white cement incl cost of paints etc. | Elect | Labour | SWR11089 | 48 | EA | 384
| 83 | 8 | Supply of Metal Handle Lamp 150W | Elect | Supply | SMR24635 | 6450 | EA | 51600
| 84 | 50 | Supply of GI Bolts & Nuts,washers etc. | Elect | Supply | SMR11488 | 117.5 | KG | 5875
| 85 | 8 | Fixing of Metal halide lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5 GI pipe complete. | Elect | Labour | SWR10956 | 1268 | EA | 10144
| 86 | 1 | Supply of Steel almarah(61/2 X 3ft) Godrej | Elect | Supply | SMR40061 | 9818 | EA | 9818
| 87 | 750 | Supplying & fabrication erection of 6mm Checkerd plates as per the field conditions | Elect | Labour | SWR10873 | 83 | KG | 62250
| 88 | 12 | Supply of Rubber mats ( 6’x3’) size for indoor SS | Elect | Supply | SMR40068 | 1386 | EA | 16632
| 89 | 1 | Supply of Alluminium Ladder for indoor works | Elect | Supply | SMR40062 | 4410 | EA | 4410
| 90 | 2 | Supply of Trolley mounted CO2 (6.5Kgs) | Elect | Supply | SMR40087 | 9240 | EA | 18480
| 91 | 2 | Supply of Fire Buckets Stand with Buckets | Elect | Supply | SMR40088 | 1386 | SET | 2772
| 92 | 6 | Supply of Fire Extinguisher for Control Room | Elect | Supply | SMR40089 | 4620 | EA | 27720
| 93 | 4 | Supply of Safety Helmet of standard make | Elect | Supply | SMR40071 | 231 | EA | 924
| 94 | 4 | Supply of Earth Rods (8ft) Screw & clamp type | Elect | Supply | SMR40066 | 578 | EA | 2312
| 95 | 4 | Supply of Hand Gloves | Elect | Supply | SMR40067 | 289 | SET | 1156
| 96 | 1 | Supply of Stand basic cell phone with charger | Elect | Supply | SMR40069 | 1386 | EA | 1386
| 97 | 1 | Supply of Table (3x6ft) Godrej | Elect | Supply | SMR40057 | 6050 | EA | 6050
| 98 | 4 | Supply of S type chairs (Godrej) | Elect | Supply | SMR40058 | 924 | EA | 3696
| 99 | 1 | Supply of Angle racks(18x36.6inches) Godrej | Elect | Supply | SMR40060 | 1733 | EA | 1733
| 100 | 10 | Supply of Danger boards with clamps | Elect | Supply | SMR40070 | 116 | EA | 1160
| 101 | 1 | Supply of 33/11kv S.S Permanent name board | Elect | Supply | SMR40086 | 10238 | EA | 10238
| 102 | 1 | Supply of Wall clock standard make | Elect | Supply | SMR40059 | 578 | EA | 578
| 103 | 1 | Supply of Taparia Tool kit complete as per Spec | Elect | Supply | SMR40063 | 4925 | SET | 4925
| 104 | 1 | Supply of Rechargeable LED torch light. | Elect | Supply | SMR40064 | 1733 | EA | 1733
| 105 | 1 | Supply of Hack saw (12 inches) | Elect | Supply | SMR40065 | 289 | EA | 289
| 106 | 8 | Supply of LC Boards | Elect | Supply | SMR40072 | 116 | EA | 928
| 107 | 2 | Supply of Gum Boots | Elect | Supply | SMR40073 | 693 | EA | 1386
| 108 | 1 | Supply of Digital clamp meter. | Elect | Supply | SMR40076 | 2888 | EA | 2888
| 109 | 1 | Supply of 5000v megger | Elect | Supply | SMR40074 | 13860 | EA | 13860
| 110 | 1 | Supply &fixing of board ind Switchyard layout | Elect | Labour | SWR20032 | 1654 | EA | 1654
| 111 | 1 | Supply & fixing safety instructions/SS Op. instructions board | Elect | Labour | SWR22090 | 2205 | EA | 2205
| 112 | 1 | Supply of 10ft Aluminium Ladder | Elect | Supply | SMR12378 | 1654 | EA | 1654
| 113 | 3000 | Supply of RS Joist Grider Pole (150x150mm) | Elect | Supply | SMR12302 | 59.25 | KG | 177750
| 114 | 830 | Supply of MS Channel 100x50mm | Elect | Supply | SMR22745 | 57.45 | KG | 47683.5
| 115 | 2500 | Supply of MS Flat 75x8mm | Elect | Supply | SMR12321 | 56.42 | KG | 141050
| 116 | 500 | Supply of MS Flat 50x6mm | Elect | Supply | SMR12322 | 56.5 | KG | 28250
| 117 | 400 | Supply of MS Channel 100x50mm | Elect | Supply | SMR22745 | 57.45 | KG | 22980
| 118 | 2 | Supply of 33KV 3x400Sqmm O/D End Kit | Elect | Supply | SMR22222 | 4554 | EA | 9108
| 119 | 2 | Supply of of 33KV 3x400Sqmm Indoor end kit | Elect | Supply | SMR11506 | 3589.96 | EA | 7179.92
| 120 | 1 | Supply of 11KV 3x185 Heat Shble O/d End Term Kit | Elect | Supply | SMR25201 | 1182.97 | EA | 1182.97
| 121 | 1 | Supply of 11KV 3x185 Heat Shble I/d End Term Kit | Elect | Supply | SMR25202 | 1085 | EA | 1085
| 122 | 100 | Supply of LT XLPE Cable 3 1/2 C 185 sqmm | Elect | Supply | SMR25204 | 547 | M | 54700
| 123 | 1500 | Supply of RS Joist Pole (175x85mm) | Elect | Supply | SMR12303 | 60.75 | KG | 91125
| 124 | 100 | Supply of MS Channel 75x40 mm | Elect | Supply | SMR25205 | 58.45 | KG | 5845
| 125 | 1 | Supply of 11KV HG FuseSet for StationTransformer | Elect | Supply | SMR12324 | 1974 | EA | 1974
| 126 | 1 | Supply of 11KV 200A Tilting Type AB Switch | Elect | Supply | SMR12318 | 8991 | EA | 8991
| 127 | 1 | Supply of LT Distribution Box (SMC) | Elect | Supply | SMR25200 | 7797 | EA | 7797
| 128 | 60 | Supply of LT XLPE Cable 1C 150 sqmm | Elect | Supply | SMR25203 | 114.83 | M | 6889.8 | 2706605.3887 | ss Labour
| 129 | 1 | survey line&cabl inc peg mark&tree clear | Elect | Labour | SWR22092 | 765 | KM | 765
| 130 | 22 | Loading of 11/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 22528
| 131 | 22 | Unloading of 11/33KV XLPE UG Cable all sizes | Elect | Labour | SWR11231 | 1024 | DR | 22528
| 132 | 11 | Transport of Cond Drum,VCBs upto 10Km | Elect | Labour | SWR11860 | 2720.34 | EA | 29923.74
| 133 | 3200 | Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts,Along the CC / BT multi layer road requiring compressor for 33 KV 3x400 Sqmm Cable | Elect | Labour | SWR11980 | 1388.84 | M | 4444288
| 134 | 3200 | Laying of 2nd Cable in Excavated Trench | Elect | Labour | SWR10988 | 204.1 | M | 653120
| 135 | 32 | Supply & Erection of Smart RFID marker | Elect | Labour | SWR25089 | 2745 | EA | 87840
| 136 | 26 | Making of Straight through joint 33kv 3x400 xlpe | Elect | Labour | SWR10382 | 5700.78 | EA | 148220.28
| 137 | 1296 | Supply of 6" B class GI pipe | Elect | Supply | SMR40081 | 1044 | M | 1353024
| 138 | 100 | Supply of 6" DWC pipe | Elect | Supply | SMR11610 | 1012 | M | 101200
| 139 | 100 | Supply of Hume pipe 9" size | Elect | Supply | SMR40001 | 125 | M | 12500
| 140 | 12 | Making of OD/Idoor end termination 33kv 3x400 xlpe | Elect | Labour | SWR10387 | 2764.76 | EA | 33177.12
| 141 | 80 | Raising of single run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)33KV 3x400sqmm UG Cb on support | Elect | Labour | SWR11954 | 135.66 | M | 10852.8
| 142 | 3200 | Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours. | Elect | Labour | SWR21903 | 30 | M | 96000
| 143 | 12 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Elect | Labour | SWR10642 | 512.55 | EA | 6150.6
| 144 | 12 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Elect | Labour | SWR10640 | 1132 | EA | 13584
| 145 | 6 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Elect | Labour | SWR11040 | 990.68 | EA | 5944.08
| 146 | 2 | Erection of 9/10/11Meter Box pole | Elect | Labour | SWR11266 | 2643.83 | EA | 5287.66
| 147 | 208.3 | Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc.M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) | Elect | Labour | SWR10919 | 41 | RMT | 8540.3
| 148 | 5.64 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.Including the cost of cement | Elect | Labour | SWR10356 | 6579 | M3 | 37105.56
| 149 | 0.186 | Coping & Muffing-Iron Pole,Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Elect | Labour | SWR11890 | 3893.01 | M3 | 724.0999
| 150 | 0.6 | Fabrication of Main and Auxiliary structures with welding using raw steel such as RS joist, M.S.Angles, Plates, Channels, including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elect | Labour | SWR10869 | 3426 | TO | 2055.6
| 151 | 2 | Erection of 33 KV LAS station/Line type including earthing | Elect | Labour | SWR10396 | 880 | SET | 1760
| 152 | 2 | Erection of 33 KV AB Switch including alignment and earthing | Elect | Labour | SWR10392 | 4500 | EA | 9000
| 153 | 4 | Supply of CI Pipe earthing 80mm dia 2.75m long | Elect | Supply | SMR11483 | 2789 | EA | 11156
| 154 | 4 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and | Elect | Labour | SWR10357 | 1234.2 | EA | 4936.8
| 155 | 4 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X0.50 M height | Elect | Labour | SWR10359 | 386 | EA | 1544
| 156 | 40 | Supply of Pre-cast cable Joint markersSupply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters , CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | Elect | Supply | SMR40085 | 484 | EA | 19360
| 157 | 6 | Painting of feeder name on support including cost of paint | Elect | Labour | SWR12101 | 53 | EA | 318
| 158 | 100 | Supply of GI Bolts & Nuts,Washers etc., | Elect | Supply | SMR11488 | 117.5 | KG | 11750
| 159 | 2 | AB Switch Coil Earthing GI No.8 Wire | Elect | Labour | SWR12331 | 146.63 |  | 293.26
| 160 | 2 | Painting AB switch OP rods with PO red | Elect | Labour | SWR10881 | 142 | EA | 284
| 161 | 2 | Assembly and erection of Structure as per specification which includes fixing of topchannels and cross bracings, transport of all materials from road side to thelocation, earthing, back filling with earth ramming etc excluding pit excavation andconcreting.33 KV DP Structure with 175x85/150x75mm RS joist | Elect | Labour | SWR11276 | 5670 | SET | 11340
| 162 | 6 | Loading of 33 KV, 10 KA LAs Station type | Elect | Labour | SWR10266 | 41 | EA | 246
| 163 | 6 | Un loading of 33 KV, 10 KA LAs Station type | Elect | Labour | SWR10584 | 35 | EA | 210
| 164 | 6 | Supply of 33KV 1Cx400Sqmm PlugTerminationKit | Elect | Supply | SMR24773 | 90915 | EA | 545490
| 165 | 6 | Making of Outdoor/Indoor End TerminationInst-33KV 1Cx400Sqmm PlugTerminationKit | Elect | Labour | SWR24773 | 15675 | EA | 94050
| 166 | 26 | Supply of 33KV3x400Sqmm Straight thr kit | Elect | Supply | SMR22223 | 24151 | EA | 627926
| 167 | 8 | Supply of 33KV 3x400Sqmm O/D End Kit | Elect | Supply | SMR22222 | 4554 | EA | 36432
| 168 | 4 | Supply of 33KV 3x400Sqmm Indoor end kit | Elect | Supply | SMR11506 | 3589.96 | EA | 14359.84
| 169 | 3000 | Supply of RS Joist Pole (175x85mm) | Elect | Supply | SMR12303 | 60.75 | KG | 182250
| 170 | 500 | Supply of MS Flat 50x6mm | Elect | Supply | SMR12322 | 56.5 | KG | 28250
| 171 | 600 | Supply of MS Channel 100x50mm | Elect | Supply | SMR22745 | 57.45 | KG | 34470
| 172 | 2 | Supply of 33KV 800A DB Break AB Switch | Elect | Supply | SMR12315 | 40658.78 | EA | 81317.56 | 8812102.2999 | 33 LINE LABOUR
| 173 | 1 | survey line&cabl inc peg mark&tree clear | Elect | Labour | SWR22092 | 765 | KM | 765
| 174 | 14 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 14336
| 175 | 14 | Un loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11231 | 1024 | DR | 14336
| 176 | 7 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators,transformers, meters (which are less in weight and occupy more space) (excludingof loading unloading) Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 23097.9
| 177 | 4200 | Laying of Single Run XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depthof the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.Along the CC / BT multi layer road requiring compressor for 11 KV 3x300 Sqmm Cable | Elect | Labour | SWR11928 | 1073.94 | M | 4510548
| 178 | 80 | Raising of Single Run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)11 KV 3x300 Sqmm Cable | Elect | Labour | SWR11955 | 144.08 | M | 11526.4
| 179 | 43 | Supply & Erection of Smart RFID marker | Elect | Labour | SWR25089 | 2745 | EA | 118035
| 180 | 17 | Making of Straight through joint 11kv 3x300 xlpe | Elect | Labour | SWR10386 | 3725.45 | EA | 63332.65
| 181 | 856 | Supply of 4" B class GI pipe | Elect | Supply | SMR40080 | 740 | M | 633440
| 182 | 100 | supply of 4" DWC pipe | Elect | Supply | SMR11609 | 759 | M | 75900
| 183 | 200 | Suppy of Hume pipe 4" size | Elect | Supply | SMR40003 | 80 | M | 16000
| 184 | 16 | Making 11 KV 3x300 Sqmm Cable Out Door/Indoor end termination | Elect | Labour | SWR10391 | 2370.63 | EA | 37930.08
| 185 | 4200 | Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours. | Elect | Labour | SWR21903 | 30 | M | 126000
| 186 | 16 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Elect | Labour | SWR10642 | 512.55 | EA | 8200.8
| 187 | 16 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Elect | Labour | SWR10640 | 1132 | EA | 18112
| 188 | 8 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Elect | Labour | SWR11040 | 990.68 | EA | 7925.44
| 189 | 8 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properlyramming including transport of materials from road side to location excluding pit excavation Box pole 9/10/11 Mtr | Elect | Labour | SWR11266 | 2643.83 | EA | 21150.64
| 190 | 208.3 | Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc.M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) | Elect | Labour | SWR10919 | 41 | RMT | 8540.3
| 191 | 7.52 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.Including the cost of cement | Elect | Labour | SWR10356 | 6579 | M3 | 49474.08
| 192 | 0.248 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Elect | Labour | SWR11890 | 3892.98 | M3 | 965.459
| 193 | 0.9 | Fabrication of Main and Auxiliary structures with welding using raw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elect | Labour | SWR10869 | 3426 | TO | 3083.4
| 194 | 8 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Elect | Labour | SWR10393 | 3200 | EA | 25600
| 195 | 8 | Supply of CI eath pipe with 80mm dia,2.0 M Length | Elect | Supply | SMR11483 | 2789 | EA | 22312
| 196 | 8 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding costof RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 9873.6
| 197 | 8 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Elect | Labour | SWR10359 | 386 | EA | 3088
| 198 | 43 | Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters , CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | Elect | Supply | SMR40085 | 484 | EA | 20812
| 199 | 8 | Painting of feeder name on support including cost of paint | Elect | Labour | SWR12101 | 53 | EA | 424
| 200 | 100 | Supply GI Bolts & Nuts,Washers etc., | Elect | Supply | SMR11488 | 117.5 | KG | 11750
| 201 | 8 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Elect | Labour | SWR12331 | 146.63 | EA | 1173.04
| 202 | 8 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elect | Labour | SWR10881 | 142 | EA | 1136
| 203 | 17 | Supply of 11KV 3x300 Heat Shble str thr JointKit | Elect | Supply | SMR25210 | 4110.17 | EA | 69872.89
| 204 | 8 | Supply of 11KV 3x300 Heat Shble O/d End Term Kit | Elect | Supply | SMR25208 | 1372.88 | EA | 10983.04
| 205 | 8 | Supply of 11KV 3x300 Heat Shble I/d End Term Kit | Elect | Supply | SMR25209 | 1459.83 | EA | 11678.64
| 206 | 4000 | Supply of RS Joist Pole (175x85mm) | Elect | Supply | SMR12303 | 60.75 | KG | 243000
| 207 | 500 | Supply of MS Flat 50x6mm | Elect | Supply | SMR12322 | 56.5 | KG | 28250
| 208 | 600 | Supply of MS Channel 75x40 mm | Elect | Supply | SMR25205 | 58.45 | KG | 35070
| 209 | 300 | Supply of MS Angle 65X65X6 | Elect | Supply | SMR25207 | 57.25 | KG | 17175
| 210 | 8 | Supply of 11KV 800A DB Break AB Switch | Elect | Supply | SMR12316 | 30847.46 | EA | 246779.68 | 6521677.039 | 11KV LINE LABOUR
| 211 | 3 | Erection of 33 KV AB Switch including alignment and earthing | Elect | Labour | SWR10392 | 4500 | EA | 13500
| 212 | 1 | Erection of 33 KV LAS station/Line type including earthing | Elect | Labour | SWR10396 | 880 | SET | 880
| 213 | 1 | Loading of 33 KV VCBs along with Panel boards | Elect | Labour | SWR10198 | 1024 | EA | 1024
| 214 | 1 | Un loading of 33 KV VCBs along with Panel boards | Elect | Labour | SWR10516 | 1044.48 | EA | 1044.48
| 215 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excludingof loading unloading)Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 3299.7
| 216 | 1 | Erection of 33 KV VCB with Control Panel | Elect | Labour | SWR10460 | 12500 | EA | 12500
| 217 | 1 | Erection of 33 KV CTs | Elect | Labour | SWR10399 | 1079 | EA | 1079
| 218 | 4.8 | Excavate-Pit for 33KV VCB | Elect | Labour | SWR23224 | 331 | EA | 1588.8
| 219 | 40 | Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per specification (including cost of ferrules, lugs and glands) | Elect | Labour | SWR12510 | 27 | EA | 1080
| 220 | 3 | Supply of stepped tubular poles single way made of steel of length 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9 mm, 2.1 mtrs with outer dia 76.1 mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79 kgf as per IS 2713. | Elect | Supply | SMR40051 | 13913 | EA | 41739
| 221 | 3 | Erection of tubular poles | Elect | Labour | SWR10955 | 1379 | EA | 4137
| 222 | 3 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE / CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA/OSRAM/SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life morethan 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existingpoles in the Substations, with five years warranty,90W LED Fixture set | Elect | Supply | SMR11594 | 8200 | EA | 24600
| 223 | 3 | Fixing of Metal halide lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5GI pipe complete | Elect | Labour | SWR10956 | 1268 | EA | 3804
| 224 | 60 | Labour for Fixing of all types of clamps | Elect | Labour | SWR10917 | 65 | EA | 3900
| 225 | 1100 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends . | Elect | Labour | SWR11879 | 27 | EA | 29700
| 226 | 5.109 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc, Including the cost of cement | Elect | Labour | SWR10356 | 6579 | M3 | 33612.111
| 227 | 0.186 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Elect | Labour | SWR11890 | 3893 | M3 | 724.098
| 228 | 6 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Elect | Labour | SWR10642 | 512.55 | EA | 3075.3
| 229 | 3 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Box pole 9/10/11 Mtr | Elect | Labour | SWR11266 | 2643.83 | EA | 7931.49
| 230 | 6 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Elect | Labour | SWR10640 | 1132 | EA | 6792
| 231 | 0.04 | Extention of 33KV Bay at 132/33KV Sub-station Supply of Zebra condutor | Elect | Supply | SMR24910 | 299369 | KM | 11974.76
| 232 | 9 | Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | Elect | Labour | SWR10884 | 224 | EA | 2016
| 233 | 7 | Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Elect | Supply | SMR11482 | 3486 | EA | 24402
| 234 | 18 | Supply of T Clamps | Elect | Supply | SMR24912 | 500 | EA | 9000
| 235 | 9 | Supply of Twin Zebra connector | Elect | Supply | SMR24911 | 600 | EA | 5400
| 236 | 10 | Supply & spreading of 20mm machine crushed metal (HBG) including cost of conveneyance of all materials, labour charges etc complete for finished item of work and directed by the engineer incharge | Elect | Labour | SWR10860 | 2113 | M3 | 21130
| 237 | 7 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4Mts.) duly filling with bentonite, earth , running of earth wireetc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 8639.4
| 238 | 7 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Elect | Labour | SWR10359 | 386 | EA | 2702
| 239 | 6 | Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x1.8 x 0.75 cum for VCB Plinth | Elect | Labour | SWR20685 | 5160 | M3 | 30960
| 240 | 6.4 | Plastering 2 Coats,20/16mm(1:6)(1:4) | Elect | Labour | SWR10862 | 373 | Sqm | 2387.2
| 241 | 3 | Making of coil earthing pole with 8mm GI wireNut&Bolts for ABSwitch | Elect | Labour | SWR12331 | 146.63 | EA | 439.89
| 242 | 3 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elect | Labour | SWR10881 | 142 | EA | 426
| 243 | 3 | 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M (1.31cum) | Elect | Labour | SWR10108 | 629.85 | EA | 1889.55
| 244 | 3 | Loading of 33 KV, 10 KA LAs Station type | Elect | Labour | SWR10266 | 41 | EA | 123
| 245 | 3 | Un loading of 33 KV, 10 KA LAs Station type | Elect | Labour | SWR10584 | 35 | EA | 105
| 246 | 166.67 | Fabrication and connecting to risers from earth mat to structures, equipment,marshalling boxes, electrical panels, PLCC panels, fencing posts etc.M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) | Elect | Labour | SWR10919 | 41 | RMT | 6833.47
| 247 | 1 | Fabrication of Main and Auxiliary structures with welding using raw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elect | Labour | SWR10869 | 3426 | MT | 3426
| 248 | 3 | Excavation of pits in all soils except hard rock requiring blasting 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") 1.05 cum | Elect | Labour | SWR10107 | 700 | EA | 2100
| 249 | 3 | Supply of 33KV 800A DB Break AB Switch | Elect | Supply | SMR12315 | 40658.78 | EA | 121976.34
| 250 | 1500 | Supply of RS Joist 175x85mm | Elect | Supply | SMR12303 | 60.75 | KG | 91125
| 251 | 1000 | Supply of MS Channel 100x50mm | Elect | Supply | SMR22745 | 57.45 | KG | 57450
| 252 | 400 | Supply of MS Flat 50x6mm | Elect | Supply | SMR12322 | 56.5 | KG | 22600 | 623116.589 | 33KV BAY EXTENSION
|  |  | Total | [5 empty] | 18663501.3166
|  |  | 18% GST | [5 empty] | 3359430.237
| Total Cost (Without GST)=Electrical | [7 empty] | 18663501.3166
| Total Cost (With 18 % GST)=Electrical | [7 empty] | 22022931.5536
|  |  | 33KV Cable | 3200 | Mtrs
|  |  | 11 KV Cable | 4200 | Mtrs

## Chest Hospital (hidden)
SCHEDULE
Name of the work: Erection, testing and commissioning of 33/11KV Indoor Sub Station with 2x 8MVA PTRs at CHEST HOSPITAL, BanjaraHills Operation Division, Jubileehills Constituency Under T& D Improvement Works.
WBS No: S-1753-12-01-01-01-001 (Electrical)
SNo | S No. | Estimate Quantity (only FigurEs) | Item DEtailEd SpEcification Description | Work Type | Item Short Descripti | Service Code | Rate | UOM | Amount
Electrical Portion
| 1 | 2 | Loading of 8MVA PTR | Elect | Labour | SWR10613 | 5805.84 | EA | 11611.68
| 2 | 2 | Transport of Power transformers (0 to 100 KM) from one place to another place in GHMC Area.(excluding of loading & unloading )-8MVA power transformer | Elect | Labour | SWR10854 | 21945 | EA | 43890
| 3 | 2 | Unloading of PTR on constructed plinth 8MVA PTR | Elect | Labour | SWR10627 | 5805.84 | EA | 11611.68
| 4 | 2 | Erection of PTR on constructed plinth-Erection of 8 MVA PTR. | Elect | Labour | SWR21321 | 49480.2 | EA | 98960.4
| 5 | 1 | Loading of 50,63, 75 & 100 KVA DTR | Elect | Labour | SWR10195 | 350 | EA | 350
| 6 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 3299.7
| 7 | 1 | Un loading of 50,63, 75 & 100 KVA DTR | Elect | Labour | SWR10513 | 280 | EA | 280
| 8 | 1 | Construction of DTR Plinth- RCC Column type DTR Plinth of size 1'X1'X10',topslab 4'x4'x6" & beam size 4'X8'X8" upto 160KVA | Elect | Labour | SWR21843 | 25967.57 | EA | 25967.57
| 9 | 1 | Erection of 3 Phase DTRs 63,75 & 100 KVA including loading and Unloading DTR on the Structure/Plinth etc | Elect | Labour | SWR20905 | 1650 | EA | 1650
| 10 | 16 | Loading of 11 KV VCBs along with Panel boards | Elect | Labour | SWR10199 | 1024 | EA | 16384
| 11 | 8 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 26397.6
| 12 | 16 | Un loading of 11 KV VCBs along with Panel boards | Elect | Labour | SWR10517 | 1044.48 | EA | 16711.68
| 13 | 16 | Erection of 11KV indoor switch gear panel/indoor PT panel /Bus section panel / Bus raiser panel/Capacitor panel/Switch fuse panel for DTR. | Elect | Labour | SWR10931 | 8894 | EA | 142304
| 14 | 10 | Loading of 33 KV VCBs along with Panel boards | Elect | Labour | SWR10198 | 1024 | EA | 10240
| 15 | 5 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 16498.5
| 16 | 10 | Un loading of 33 KV VCBs along with Panel boards | Elect | Labour | SWR10516 | 1044.48 | EA | 10444.8
| 17 | 10 | Erection of 33KV indoor switch gear panel/33KV indoor PT panel / Bus section panel / Bus raiser panel | Elect | Labour | SWR10930 | 9847 | EA | 98470
| 18 | 1 | Loading of 220 V Batterry with charger | Elect | Labour | SWR11166 | 1612 | SET | 1612
| 19 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 3299.7
| 20 | 1 | Un loading of 220 V Batterry with charger | Elect | Labour | SWR11147 | 1024 | SET | 1024
| 21 | 1 | Erection of 220 V, 80 AH battery in complete shape fit for charging . Conventional lead acid | Elect | Labour | SWR12295 | 7666 | EA | 7666
| 22 | 1 | Supply of AC Supply panel inluding providing of changeover switch, SFU, metering unit, 32 A three phase MCB, 16 A Single phase MCB complete as per specification. | Elect | Supply | SMR40045 | 42000 | EA | 42000
| 23 | 1 | Erection of control/Relay panels, AC Panels, announciationpanels etc in the control room duly mounting them on channels and grouting them with foundation bolts excluding cost of channels & foundation bolts | Elect | Labour | SWR11893 | 2122 | EA | 2122
| 24 | 44 | Cutting Charges for RS joist 150x150mm | Elect | Labour | SWR10297 | 48 | EA | 2112
| 25 | 0.83 | Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elect | Labour | SWR10869 | 3426 | TO | 2843.58
| 26 | 3.83 | Alligning the Main and Auxiliary structures such as RS joist,M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication. | Elect | Labour | SWR10867 | 1470 | TO | 5630.1
| 27 | 3.83 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes,labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Elect | Supply | SMR40009 | 2181 | TO | 8353.23
| 28 | 3.83 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters ofthinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes,labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Elect | Labour | SWR10877 | 851 | TO | 3259.33
| 29 | 3.83 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc | Elect | Supply | SMR40010 | 1293 | TO | 4952.19
| 30 | 3.83 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium | Elect | Labour | SWR10879 | 482 | TO | 1846.06
| 31 | 43 | Painting of Name Plates for any equipment | Elect | Labour | SWR10963 | 122 | EA | 5246
| 32 | 36 | Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Elect | Supply | SMR11482 | 3486 | EA | 125496
| 33 | 36 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 44431.2
| 34 | 36 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50M height | Elect | Labour | SWR10359 | 386 | EA | 13896
| 35 | 531.9 | Laying of MS Flats /GI Flats 75x 8mm earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment andconnecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes including fabrication | Elect | Labour | SWR10920 | 65 | RMT | 34573.5
| 36 | 208.3 | Fabrication and connecting of M.S./ G.I. Flat 50x6mm to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. | Elect | Labour | SWR10919 | 41 | RMT | 8540.3
| 37 | 50 | Supply of GI Bolts & Nuts | Elect | Supply | SMR11488 | 117.5 | KG | 5875
| 38 | 314 | Paint-Black to all Earth Flat incl. Pain | Elect | Labour | SWR12217 | 55 | M | 17270
| 39 | 2 | Supply of Copper Flexible jumper with 75 X 8 of length 250 mm at neutral of Power tranformer end and 50 X 6 of length 50mm two Nos at double neutral end duly brasing with flexible jumper of capacity of 5kA/3 sec for power transformer neutral | Elect | Supply | SMR40033 | 4725 | EA | 9450
| 40 | 2 | Providing of double earthing for neutral with flexible copper jumpers including arrangement by fixing M.S.Channel 100x50mm | Elect | Labour | SWR11892 | 1323 | EA | 2646
| 41 | 106 | Laying of 4No's single core 630 sqmm UG cable (Single Circuit with one spare cable)including excavation of trench of size 0.7 Mtrs width and 1.2 Mtrs depth from road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.Lay-4 SC 33KV 630sqmm UG Cb HG/BC/RE/NS | Elect | Labour | SWR12110 | 2463.3 | M | 261109.8
| 42 | 56 | Raising of Single Run 33KV 1x630sqmm UG Cable on Support | Elect | Labour | SWR12448 | 133 | M | 7448
| 43 | 106 | Laying of second 33KV UG Cable in Existing Duct | Elect | Labour | SWR12452 | 200 | M | 21200
| 44 | 14 | Raising of 33kV 3x400 Sqmm Cu cable on already erected support with wooden / MS clamps and connecting it to over head line withcable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Elect | Labour | SWR11954 | 135.66 | M | 1899.24
| 45 | 8 | Supply of 33KV 1x630Sqmm GIS ID Unit End Terminations | Elect | Supply | SMR12473 | 2500 | EA | 20000
| 46 | 8 | Supply of 33KV 1x630Sqmm OD Unit End Terminations | Elect | Supply | SMR12474 | 4200 | EA | 33600
| 47 | 8 | Installation of 33KV 1x630Sqmm GIS ID End Terminations | Elect | Labour | SWR12473 | 17600 | EA | 140800
| 48 | 8 | Installation of 33KV 1x630Sqmm OD Unit EndTerminations | Elect | Labour | SWR12474 | 4000 | EA | 32000
| 49 | 4 | Making of Outdoor/Indoor 33 KV 3x400 Sqmm End Termination | Elect | Labour | SWR10387 | 2764.76 | EA | 11059.04
| 50 | 85 | Laying of XLPE UG cable Single Run including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders/Normal soil / CC/BT Road 11KV 3x185 Sqmm Cable | Elect | Labour | SWR11920 | 465.46 | M | 39564.1
| 51 | 15 | Raising of Single Run 11 KV 3x185 Sqmm Cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Elect | Labour | SWR11956 | 126.23 | M | 1893.45
| 52 | 2 | Making of Outdoor/Indoor 11 KV 3x185 Sqmm Cable End Termination | Elect | Labour | SWR10390 | 2370.63 | EA | 4741.26
| 53 | 90 | Laying of XLPE UG cable Single Run including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders/Normal soil / CC/BT Road LT 3 1/2 x 185 Sqmm Cable | Elect | Labour | SWR11923 | 377.63 | M | 33986.7
| 54 | 10 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-LT 3 1/2 x 185 Sqmm Cable | Elect | Labour | SWR11959 | 85.43 | M | 854.3
| 55 | 2 | Fixing of Oout Door/Indoor end termination LT 3 1/2 x185 Sqmm Cable | Elect | Labour | SWR10765 | 968.9 | EA | 1937.8
| 56 | 2200 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends . | Elect | Labour | SWR11879 | 27 | M | 59400
| 57 | 500 | Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per specification (including cost of ferrules, lugs and glands) | Elect | Labour | SWR12510 | 27 | EA | 13500
| 58 | 1.6 | Fabrication of Main and Auxiliary structures with welding using raw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to theRS-Joist poles excluding cost of Mild Steel and transportcharges to substation site, including erection. | Elect | Labour | SWR10869 | 3426 | TO | 5481.6
| 59 | 1.6 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Elect | Supply | SMR40009 | 2181 | TO | 3489.6
| 60 | 1.6 | Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Elect | Labour | SWR10877 | 851 | TO | 1361.6
| 61 | 1.6 | Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. | Elect | Supply | SMR40010 | 1293 | TO | 2068.8
| 62 | 1.6 | Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . | Elect | Labour | SWR10879 | 482 | TO | 771.2
| 63 | 5 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Elect | Labour | SWR11040 | 990.68 | EA | 4953.4
| 64 | 5 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Box pole 9/10/11 Mtr | Elect | Labour | SWR11266 | 2643.83 | EA | 13219.15
| 65 | 4.7 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.-Including the cost of cement | Elect | Labour | SWR10356 | 6579 | M3 | 30921.3
| 66 | 0.155 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Elect | Labour | SWR11890 | 3893.03 | M3 | 603.4197
| 67 | 5 | Paint of coping with 2 coats of white cement incl cost of paints etc. | Elect | Labour | SWR11089 | 48 | EA | 240
| 68 | 1 | Erection of 11 KV HG Fuse set including earthing | Elect | Labour | SWR10395 | 740.52 | SET | 740.52
| 69 | 1 | Erection of 11KV 200A TT type AB Switch including fixing of cross angles and alignment complete | Elect | Labour | SWR20102 | 1813.49 | EA | 1813.49
| 70 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.-Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elect | Labour | SWR10881 | 142 | EA | 142
| 71 | 1 | Erection of LT distribution box including laying of LT cable from distribution box to LT OH line and DTR to distribution box including earthing of distribution box and crimping of lugs connecting of jumpers etc | Elect | Labour | SWR10674 | 1594.67 | EA | 1594.67
| 72 | 18 | Supply of GI Flat 25X3 mm | Elect | Supply | SMR11485 | 105 | KG | 1890
| 73 | 30 | Running of GI eartn flat of size 25X3mm from all metallic parts of channels, AB Switch, HG fuse set, DTr neutral and LT Distribution box and inter connection of earth pits etc complete. | Elect | Labour | SWR12125 | 14.03 | M | 420.9
| 74 | 2 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 2048
| 75 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 3299.7
| 76 | 2 | Un loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11231 | 1024 | DR | 2048
| 77 | 8 | Supply of stepped tubular poles single way made of steel of length 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9 mm, 2.1 mtrs with outer dia 76.1 mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79 kgf as per IS 2713. | Elect | Supply | SMR40051 | 13913 | EA | 111304
| 78 | 8 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rockboulders) 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M(2.6" x 2.6" x 6.0") | Elect | Labour | SWR11039 | 928 | EA | 7424
| 79 | 8 | Erection of tubular poles | Elect | Labour | SWR10955 | 1379 | EA | 11032
| 80 | 6.1 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.-Including the cost of cement | Elect | Labour | SWR10356 | 6579 | M3 | 40131.9
| 81 | 0.248 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Elect | Labour | SWR11890 | 3892.98 | M3 | 965.459
| 82 | 8 | Paint of coping with 2 coats of white cement incl cost of paints etc. | Elect | Labour | SWR11089 | 48 | EA | 384
| 83 | 8 | Supply of Metal Handle Lamp 150W | Elect | Supply | SMR24635 | 6450 | EA | 51600
| 84 | 50 | Supply of GI Bolts & Nuts,washers etc. | Elect | Supply | SMR11488 | 117.5 | KG | 5875
| 85 | 8 | Fixing of Metal halide lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5 GI pipe complete. | Elect | Labour | SWR10956 | 1268 | EA | 10144
| 86 | 1 | Supply of Steel almarah(61/2 X 3ft) Godrej | Elect | Supply | SMR40061 | 9818 | EA | 9818
| 87 | 750 | Supplying & fabrication erection of 6mm Checkerd plates as per the field conditions | Elect | Labour | SWR10873 | 83 | KG | 62250
| 88 | 12 | Supply of Rubber mats ( 6’x3’) size for indoor SS | Elect | Supply | SMR40068 | 1386 | EA | 16632
| 89 | 1 | Supply of Alluminium Ladder for indoor works | Elect | Supply | SMR40062 | 4410 | EA | 4410
| 90 | 2 | Supply of Trolley mounted CO2 (6.5Kgs) | Elect | Supply | SMR40087 | 9240 | EA | 18480
| 91 | 2 | Supply of Fire Buckets Stand with Buckets | Elect | Supply | SMR40088 | 1386 | SET | 2772
| 92 | 6 | Supply of Fire Extinguisher for Control Room | Elect | Supply | SMR40089 | 4620 | EA | 27720
| 93 | 4 | Supply of Safety Helmet of standard make | Elect | Supply | SMR40071 | 231 | EA | 924
| 94 | 4 | Supply of Earth Rods (8ft) Screw & clamp type | Elect | Supply | SMR40066 | 578 | EA | 2312
| 95 | 4 | Supply of Hand Gloves | Elect | Supply | SMR40067 | 289 | SET | 1156
| 96 | 1 | Supply of Stand basic cell phone with charger | Elect | Supply | SMR40069 | 1386 | EA | 1386
| 97 | 1 | Supply of Table (3x6ft) Godrej | Elect | Supply | SMR40057 | 6050 | EA | 6050
| 98 | 4 | Supply of S type chairs (Godrej) | Elect | Supply | SMR40058 | 924 | EA | 3696
| 99 | 1 | Supply of Angle racks(18x36.6inches) Godrej | Elect | Supply | SMR40060 | 1733 | EA | 1733
| 100 | 10 | Supply of Danger boards with clamps | Elect | Supply | SMR40070 | 116 | EA | 1160
| 101 | 1 | Supply of 33/11kv S.S Permanent name board | Elect | Supply | SMR40086 | 10238 | EA | 10238
| 102 | 1 | Supply of Wall clock standard make | Elect | Supply | SMR40059 | 578 | EA | 578
| 103 | 1 | Supply of Taparia Tool kit complete as per Spec | Elect | Supply | SMR40063 | 4925 | SET | 4925
| 104 | 1 | Supply of Rechargeable LED torch light. | Elect | Supply | SMR40064 | 1733 | EA | 1733
| 105 | 1 | Supply of Hack saw (12 inches) | Elect | Supply | SMR40065 | 289 | EA | 289
| 106 | 8 | Supply of LC Boards | Elect | Supply | SMR40072 | 116 | EA | 928
| 107 | 2 | Supply of Gum Boots | Elect | Supply | SMR40073 | 693 | EA | 1386
| 108 | 1 | Supply of Digital clamp meter. | Elect | Supply | SMR40076 | 2888 | EA | 2888
| 109 | 1 | Supply of 5000v megger | Elect | Supply | SMR40074 | 13860 | EA | 13860
| 110 | 1 | Supply &fixing of board ind Switchyard layout | Elect | Labour | SWR20032 | 1654 | EA | 1654
| 111 | 1 | Supply & fixing safety instructions/SS Op. instructions board | Elect | Labour | SWR22090 | 2205 | EA | 2205
| 112 | 1 | Supply of 10ft Aluminium Ladder | Elect | Supply | SMR12378 | 1654 | EA | 1654
| 113 | 3000 | Supply of RS Joist Grider Pole (150x150mm) | Elect | Supply | SMR12302 | 59.25 | KG | 177750
| 114 | 830 | Supply of MS Channel 100x50mm | Elect | Supply | SMR22745 | 57.45 | KG | 47683.5
| 115 | 2500 | Supply of MS Flat 75x8mm | Elect | Supply | SMR12321 | 56.42 | KG | 141050
| 116 | 500 | Supply of MS Flat 50x6mm | Elect | Supply | SMR12322 | 56.5 | KG | 28250
| 117 | 400 | Supply of MS Channel 100x50mm | Elect | Supply | SMR22745 | 57.45 | KG | 22980
| 118 | 2 | Supply of 33KV 3x400Sqmm O/D End Kit | Elect | Supply | SMR22222 | 4554 | EA | 9108
| 119 | 2 | Supply of of 33KV 3x400Sqmm Indoor end kit | Elect | Supply | SMR11506 | 3589.96 | EA | 7179.92
| 120 | 1 | Supply of 11KV 3x185 Heat Shble O/d End Term Kit | Elect | Supply | SMR25201 | 1182.97 | EA | 1182.97
| 121 | 1 | Supply of 11KV 3x185 Heat Shble I/d End Term Kit | Elect | Supply | SMR25202 | 1085 | EA | 1085
| 122 | 100 | Supply of LT XLPE Cable 3 1/2 C 185 sqmm | Elect | Supply | SMR25204 | 547 | M | 54700
| 123 | 1500 | Supply of RS Joist Pole (175x85mm) | Elect | Supply | SMR12303 | 60.75 | KG | 91125
| 124 | 100 | Supply of MS Channel 75x40 mm | Elect | Supply | SMR25205 | 58.45 | KG | 5845
| 125 | 1 | Supply of 11KV HG FuseSet for StationTransformer | Elect | Supply | SMR12324 | 1974 | EA | 1974
| 126 | 1 | Supply of 11KV 200A Tilting Type AB Switch | Elect | Supply | SMR12318 | 8991 | EA | 8991
| 127 | 1 | Supply of LT Distribution Box (SMC) | Elect | Supply | SMR25200 | 7797 | EA | 7797
| 128 | 60 | Supply of LT XLPE Cable 1C 150 sqmm | Elect | Supply | SMR25203 | 114.83 | M | 6889.8 | 2706605.3887 | SS LABOUR
| 129 | 1 | survey line&cable including peg mark&tree clear | Elect | Labour | SWR22092 | 765 | KM | 765
| 130 | 20 | Loading of 11/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 20480
| 131 | 20 | Unloading 11/33KV XLPE UG Cable all sizes | Elect | Labour | SWR11231 | 1024 | DR | 20480
| 132 | 10 | Transport of Cond Drum,VCBs upto 10Km | Elect | Labour | SWR11860 | 2720.34 | EA | 27203.4
| 133 | 3000 | Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts,Along the CC / BT multi layer road requiring compressor for 33 KV 3x400 Sqmm Cable | Elect | Labour | SWR11980 | 1388.84 | M | 4166520
| 134 | 3000 | Laying of 2nd Cable in Excavated Trench | Elect | Labour | SWR10988 | 204.1 | M | 612300
| 135 | 30 | Supply &Erection of Smart RFID marker | Elect | Labour | SWR25089 | 2745 | EA | 82350
| 136 | 24 | Making of Straight through joint 33kv 3x400 xlpe | Elect | Labour | SWR10382 | 5700.78 | EA | 136818.72
| 137 | 1208 | Supply of 6" B class GI pipe | Elect | Supply | SMR40081 | 1044 | M | 1261152
| 138 | 100 | Supply of 6" DWC pipe | Elect | Supply | SMR11610 | 1012 | M | 101200
| 139 | 100 | Supply of Hume pipe 9" size | Elect | Supply | SMR40001 | 125 | M | 12500
| 140 | 6 | Making of OD/Idoor end termination 33kv 3x400 xlpe | Elect | Labour | SWR10387 | 2764.76 | EA | 16588.56
| 141 | 40 | Raising of single run cable on already erected support with wooden / MS clampsand connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)33KV 3x400sqmm UG Cb on support | Elect | Labour | SWR11954 | 135.66 | M | 5426.4
| 142 | 3000 | Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours. | Elect | Labour | SWR21903 | 30 | M | 90000
| 143 | 6 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mmflat and MS channel on either side including the cost of consumable. | Elect | Labour | SWR10642 | 512.55 | EA | 3075.3
| 144 | 6 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Elect | Labour | SWR10640 | 1132 | EA | 6792
| 145 | 3 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Elect | Labour | SWR11040 | 990.68 | EA | 2972.04
| 146 | 1 | Erection of 9/10/11Meter Box pole | Elect | Labour | SWR11266 | 2643.83 | EA | 2643.83
| 147 | 208.33 | Fabrication and connecting to risers from earth mat to structures, equipment,marshalling boxes, electrical panels, PLCC panels, fencing posts etc.M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) | Elect | Labour | SWR10919 | 41 | RMT | 8541.53
| 148 | 2.82 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.Including the cost of cement | Elect | Labour | SWR10356 | 6579 | M3 | 18552.78
| 149 | 0.093 | Coping & Muffing-Iron Pole,Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Elect | Labour | SWR11890 | 3893.01 | M3 | 362.0499
| 150 | 0.3 | Fabrication of Main and Auxiliary structures with welding using raw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elect | Labour | SWR10869 | 3426 | TO | 1027.8
| 151 | 1 | Erection of 33 KV LAS station/Line type including earthing | Elect | Labour | SWR10396 | 880 | SET | 880
| 152 | 1 | Erection of 33 KV AB Switch including alignment and earthing | Elect | Labour | SWR10392 | 4500 | EA | 4500
| 153 | 2 | Supply of CI Pipe earthing 80mm dia 2.75m long | Elect | Supply | SMR11483 | 2789 | EA | 5578
| 154 | 2 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4Mts.) duly filling with bentonite, earth , running of earth wireetc., complete, including cost of bentonite and | Elect | Labour | SWR10357 | 1234.2 | EA | 2468.4
| 155 | 2 | Providing of RCC Collar guarding to the existing earth pits withdamaged masonry including dismantling and removing ofexisting masonry and fixing the RCC collar of 0.60 M dia X0.50 M height | Elect | Labour | SWR10359 | 386 | EA | 772
| 156 | 30 | Supply of Pre-cast cable Joint markersSupply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters , CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground levelconfirming to IS 5820 2001 | Elect | Supply | SMR40085 | 484 | EA | 14520
| 157 | 3 | Painting of feeder name on support including cost of paint | Elect | Labour | SWR12101 | 53 | EA | 159
| 158 | 100 | Supply of GI Bolts & Nuts,Washers etc., | Elect | Supply | SMR11488 | 117.5 | KG | 11750
| 159 | 1 | AB Switch Coil Earthing GI No.8 Wire | Elect | Labour | SWR12331 | 146.63 | EA | 146.63
| 160 | 1 | Painting AB switch OP rods with PO red | Elect | Labour | SWR10881 | 142 | EA | 142
| 161 | 1 | Assembly and erection of Structure as per specification which includes fixing of top channels and cross bracings, transport of all materials from road side to the location, earthing, back filling with earth ramming etc excluding pit excavation and concreting-33 KV DP Structure with 175x85/150x75mm RS joist | Elect | Labour | SWR11276 | 5670 | SET | 5670
| 162 | 3 | Loading of 33 KV, 10 KA LAs Station type | Elect | Labour | SWR10266 | 41 | EA | 123
| 163 | 3 | Un loading of 33 KV, 10 KA LAs Station type | Elect | Labour | SWR10584 | 35 | EA | 105
| 164 | 24 | Supply of 33KV3x400Sqmm Straight thr kit | Elect | Supply | SMR22223 | 24151 | EA | 579624
| 165 | 4 | Supply of 33KV 3x400Sqmm O/D End Kit | Elect | Supply | SMR22222 | 4554 | EA | 18216
| 166 | 2 | Supply of 33KV 3x400Sqmm Indoor end kit | Elect | Supply | SMR11506 | 3589.96 | EA | 7179.92
| 167 | 1500 | Supply of RS Joist Pole (175x85mm) | Elect | Supply | SMR12303 | 60.75 | KG | 91125
| 168 | 500 | Supply of MS Flat 50x6mm | Elect | Supply | SMR12322 | 56.5 | KG | 28250
| 169 | 300 | Supply of MS Channel 100x50mm | Elect | Supply | SMR22745 | 57.45 | KG | 17235
| 170 | 1 | Supply of 33KV 800A DB Break AB Switch | Elect | Supply | SMR12315 | 40658.78 | EA | 40658.78 | 7426854.1399 | 33KV LINE LABOUR
| 171 | 1 | survey line&cabl inc peg mark&tree clear | Elect | Labour | SWR22092 | 765 | KM | 765
| 172 | 18 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 18432
| 173 | 18 | Un loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11231 | 1024 | DR | 18432
| 174 | 9 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 29697.3
| 175 | 5420 | Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths andfilling with sand 250mm above the cable and 50mm below the cable, laying of cable,placing 40mm shabad protective slabs, back filling the trench with earth, levellingand and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.Along the CC / BT multi layer road requiring compressor for 11 KV 3x300 Sqmm Cable | Elect | Labour | SWR11928 | 1073.94 | M | 5820754.8
| 176 | 80 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)11 KV 3x300 Sqmm Cable | Elect | Labour | SWR11955 | 144.08 | M | 11526.4
| 177 | 55 | Supply &Erection of Smart RFID marker | Elect | Labour | SWR25089 | 2745 | EA | 150975
| 178 | 22 | Making of Straight through joint 11kv 3x300 xlpe | Elect | Labour | SWR10386 | 3725.45 | EA | 81959.9
| 179 | 1100 | Supply of 4" B class GI pipe | Elect | Supply | SMR40080 | 740 | M | 814000
| 180 | 100 | supply of 4" DWC pipe | Elect | Supply | SMR11609 | 759 | M | 75900
| 181 | 200 | Suppy of Hume pipe 4" size | Elect | Supply | SMR40003 | 80 | M | 16000
| 182 | 16 | Making 11 KV 3x300 Sqmm Cable Out Door/Indoor end termination | Elect | Labour | SWR10391 | 2370.63 | EA | 37930.08
| 183 | 5000 | Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours. | Elect | Labour | SWR21903 | 30 | M | 150000
| 184 | 16 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mmflat and MS channel on either side including the cost of consumable. | Elect | Labour | SWR10642 | 512.55 | EA | 8200.8
| 185 | 16 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Elect | Labour | SWR10640 | 1132 | EA | 18112
| 186 | 8 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Elect | Labour | SWR11040 | 990.68 | EA | 7925.44
| 187 | 8 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Box pole 9/10/11 Mtr | Elect | Labour | SWR11266 | 2643.83 | EA | 21150.64
| 188 | 208.3 | Fabrication and connecting to risers from earth mat to structures, equipment,marshalling boxes, electrical panels, PLCC panels, fencing posts etc.M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) | Elect | Labour | SWR10919 | 41 | RMT | 8540.3
| 189 | 7.52 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.Including the cost of cement | Elect | Labour | SWR10356 | 6579 | M3 | 49474.08
| 190 | 0.248 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Elect | Labour | SWR11890 | 3892.98 | M3 | 965.459
| 191 | 0.9 | Fabrication of Main and Auxiliary structures with welding using raw steel such as RS joist, M.S.Angles, Plates, Channels, including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elect | Labour | SWR10869 | 3426 | TO | 3083.4
| 192 | 8 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Elect | Labour | SWR10393 | 3200 | EA | 25600
| 193 | 8 | Supply of CI eath pipe with 80mm dia,2.0 M Length | Elect | Supply | SMR11483 | 2789 | EA | 22312
| 194 | 8 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 9873.6
| 195 | 8 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Elect | Labour | SWR10359 | 386 | EA | 3088
| 196 | 55 | Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters , CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | Elect | Supply | SMR40085 | 484 | EA | 26620
| 197 | 8 | Painting of feeder name on support including cost of paint | Elect | Labour | SWR12101 | 53 | EA | 424
| 198 | 100 | Supply of GI Bolts & Nuts,Washers etc., | Elect | Supply | SMR11488 | 117.5 | KG | 11750
| 199 | 8 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Elect | Labour | SWR12331 | 146.63 | EA | 1173.04
| 200 | 8 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elect | Labour | SWR10881 | 142 | EA | 1136
| 201 | 22 | Supply of 11KV 3x300 Heat Shble str thr JointKit | Elect | Supply | SMR25210 | 4110.17 | EA | 90423.74
| 202 | 8 | Supply of 11KV 3x300 Heat Shble O/d End Term Kit | Elect | Supply | SMR25208 | 1372.88 | EA | 10983.04
| 203 | 8 | Supply of 11KV 3x300 Heat Shble I/d End Term Kit | Elect | Supply | SMR25209 | 1459.83 | EA | 11678.64
| 204 | 4000 | Supply of RS Joist Pole (175x85mm) | Elect | Supply | SMR12303 | 60.75 | KG | 243000
| 205 | 500 | Supply of MS Flat 50x6mm | Elect | Supply | SMR12322 | 56.5 | KG | 28250
| 206 | 600 | Supply of MS Channel 75x40 mm | Elect | Supply | SMR25205 | 58.45 | KG | 35070
| 207 | 300 | Supply of MS Angle 65X65X6 | Elect | Supply | SMR25207 | 57.25 | KG | 17175
| 208 | 8 | Supply of 11KV 800A DB Break AB Switch | Elect | Supply | SMR12316 | 30847.46 | EA | 246779.68 | 8129161.339 | 11KV LINE LABOUR
| 209 | 2 | Erection of 33 KV AB Switch including alignment and earthing | Elect | Labour | SWR10392 | 4500 | EA | 9000
| 210 | 1 | Erection of 33 KV LAS station/Line type including earthing | Elect | Labour | SWR10396 | 880 | SET | 880
| 211 | 1 | Loading of 33 KV VCBs along with Panel boards | Elect | Labour | SWR10198 | 1024 | EA | 1024
| 212 | 1 | Un loading of 33 KV VCBs along with Panel boards | Elect | Labour | SWR10516 | 1044.48 | EA | 1044.48
| 213 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 3299.7
| 214 | 4.8 | Excavation of Pit for 33KV VCB | Elect | Labour | SWR23224 | 331 | M3 | 1588.8
| 215 | 6 | Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x 1.8 x 0.75 cum for VCB Plinth | Elect | Labour | SWR20685 | 5160 | M3 | 30960
| 216 | 6.4 | Plastering 2 Coats,20/16mm(1:6)(1:4) | Elect | Labour | SWR10862 | 373 | M2 | 2387.2
| 217 | 1 | Painting of coping with two coats of white cement including cost of paint & conveyance charges for PTR/VCB plinths | Elect | Labour | SWR12334 | 160 | EA | 160
| 218 | 1 | Erection of 33 KV VCB with Control Panel | Elect | Labour | SWR10460 | 12500 | EA | 12500
| 219 | 1 | Erection of 33 KV CTs | Elect | Labour | SWR10399 | 1079 | SET | 1079
| 220 | 1 | Erection of 33kV Twin feeder control & Relay panel in the control room duly mounting them on channels and grouting them with foundation bolts excluding cost of channels & foundation bolts | Elect | Labour | SWR10934 | 1729 | EA | 1729
| 221 | 2 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rockboulders)9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M(2.6" x 2.6" x 6.0") | Elect | Labour | SWR11039 | 928 | EA | 1856
| 222 | 1.526 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.Including the cost of cement | Elect | Labour | SWR10356 | 6579 | M3 | 10039.554
| 223 | 0.062 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Elect | Labour | SWR11890 | 3893.06 | M3 | 241.3697
| 224 | 2 | Supply of stepped tubular poles single way made of steel oflength 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9 mm, 2.1 mtrs with outer dia 76.1 mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79 kgf as per IS 2713. | Elect | Supply | SMR40051 | 13913 | EA | 27826
| 225 | 2 | Erection of tubular poles | Elect | Labour | SWR10955 | 1379 | EA | 2758
| 226 | 2 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTUREROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS MILEDS/CREE/NICHIA/ OSRAM/ SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years arranty 90W LED Fixture set | Elect | Supply | SMR11594 | 8200 | EA | 16400
| 227 | 2 | Fixing of Metal halide lamps with fixtures make:Philips,Crompton, Bajaj junction box with MCB with 1.5 GI pipe complete | Elect | Labour | SWR10956 | 1268 | EA | 2536
| 228 | 21 | Labour for Fixing of all types of clamps | Elect | Labour | SWR10917 | 65 | EA | 1365
| 229 | 1200 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends | Elect | Labour | SWR11879 | 27 | EA | 32400
| 230 | 0.08 | Extention of 33KV Bay at 132/33KV Sub-station Zebra condutor | Elect | Supply | SMR24910 | 299369 | KM | 23949.52
| 231 | 9 | Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | Elect | Labour | SWR10884 | 224 | EA | 2016
| 232 | 6 | Supply of I hook | Elect | Supply | SMR12099 | 158 | EA | 948
| 233 | 6 | Erection of I hook | Elect | Labour | SWR12099 | 55 | EA | 330
| 234 | 3 | Supply of Spacer T-Clamps with double dropper suitable for Zebra / Panther | Elect | Supply | SMR40013 | 788 | EA | 2364
| 235 | 6 | Supply of Tension Hardware 3 Bolted for Twin Zebra/panther with 150 mm spacing | Elect | Supply | SMR40016 | 2512 | EA | 15072
| 236 | 12 | Supply of Alluminum alloy Pad clamps minimum 15 mm Thickness, 75mm Width 150 Mm Length conforming to IS:5561-1970, IS617, IS 2633-1964, IS 1363-1967, IS1367-1961), Six bolted with hot dip galvanized bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 ") minimum weight of 900 gms to suit for Panther ACSR Conductor of pad size 75X 75 X 15mm for carrying 600 A current | Elect | Supply | SMR24942 | 360 | EA | 4320
| 237 | 6 | Supply of CT stud clamps with hot dip galvanised bolts and nuts suitable for zebra / Panther conductor on one side and 28/30/40 mm CT stud on other side with stud size for single zebra / panther (4 bolted) with bimetallic sleeve for carrying 800 A | Elect | Supply | SMR40023 | 399 | EA | 2394
| 238 | 6 | Supply of U-Bolts 16 mm | Elect | Supply | SMR40040 | 37 | EA | 222
| 239 | 43 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 33 kV bus comprising of three phases with Twin Zebra/Panther conductor to a tension of 900kgs including fixing of spacer clamps.(Bus section of 4.5mt) | Elect | Labour | SWR10882 | 1302 | EA | 55986
| 240 | 2 | Room fire extinguisher (2 ltrs capacity) for control room | Elect | Supply | SMR40089 | 4620 | EA | 9240
| 241 | 6 | Supply & spreading of 20mm machine crushed metal (HBG) including cost of conveneyance of all materials, labour charges etc complete for finished item of work and directed by the engineer incharge | Elect | Labour | SWR10860 | 2113 | M3 | 12678
| 242 | 6 | Supply &Filling with Borrowed Stone Dust | Elect | Labour | SWR33054 | 1062 | M3 | 6372
| 243 | 15 | Brick masonry in cement mortar (1:6) for superstructure using well burnt country made second class bricks of approved quality including cost and conveyance of all materials curing, scaffolding with all leads and lifts etc., complete for finished item of work - Ground Floor | Civil | Labour | SWR33068 | 7209 | M3 | 108135
| 244 | 25 | Earth Work Mass Excavation to a depth as directed, in soils such as Mixture of Gravel and Soft Disintegrated Rock like Shales, Ordinary Gravel, Stoney Earth and Earth Mixed with Fair Sized Boulders and in all conditions such as dry, wet, slurry etc.and in dense or hard soils, disposal and depositing of excavated soil with intial lead of 10 mt and intial lift of 2m or as directed, including cost and conveyance of all materials, ramping and lifting of materials, and labour charges, hire charges of machinery, tools & plants, bailing of water ( either sub soil water, stoMts water, rain water, surface water or of any kind) if any at any stage of work until all works below ground level is finished to the satisfaction ,and from work such as shoring, timbering, strutting with required supports etc. for the work and removal of form work after completion of work etc all complete as directed by the engineer-incharge. | Civil | Labour | SWR33015 | 486 | M3 | 12150
| 245 | 3 | Supply &Fixing of 15 mm brass body CP finish bib tap of not less than 300 grams weight with quarter turn spindle with either internal or external threaded connection conforming to IS 8931 including all operational, incidental and labour charges etc. complete for the finished item of work | Civil | Labour | SWR34330 | 684 | EA | 2052
| 246 | 20 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007) 22.20mm OD Pipe - SDR 11 including all operational, incidental and labour charges etc. complete for the finished item of work | Civil | Labour | SWR34362 | 313 | M | 6260
| 247 | 2 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) in existing Substation | Elect | Labour | SWR11769 | 144.84 | EA | 289.68
| 248 | 2 | Supply of GI wire No 8 | Elect | Supply | SMR11486 | 105 | KG | 210
| 249 | 2 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Elect | Labour | SWR12331 | 146.63 | EA | 293.26
| 250 | 25 | Supply of GI Bolts & Nuts etc | Elect | Supply | SMR11488 | 117.5 | KG | 2937.5
| 251 | 3 | Excavation of earth pit, supply of cast iron pipe with flange on one end (as per ISS7181/86) of nominal dia 125mm and 2.75 meters long in side the pit including supply and fixing RCC collars 0.75 meter dia (OD), 50mm thick and 0.60meters long complete as per APTRANSCO standards | Elect | Labour | SWR10924 | 9804 | EA | 29412
| 252 | 3 | Supply of 33KV TC Structure as per DATA-II | Elect | Supply | SMR40102 | 50703 | EA | 152109
| 253 | 6 | Supply of33KV BD Boom as per DATA-IV | Elect | Supply | SMR40104 | 18244 | EA | 109464
| 254 | 3 | Erection of33KV TC Structure as per DATA-II | Elect | Labour | SWR11010 | 17393.04 | EA | 52179.12
| 255 | 6 | Erection of 33KV TD Structure as per DATA-I | Elect | Labour | SWR11009 | 14839.78 | EA | 89038.68
| 256 | 167 | Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc.M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) | Elect | Labour | SWR10919 | 41 | RMT | 6847
| 257 | 24 | Supplying of Earth Mat 100x16mm GI Flat from Earth | Elect | Supply | SMR23228 | 975 | M | 23400
| 258 | 24 | Laying of earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication100x16mm M.S./G.I earth flat | Elect | Labour | SWR22054 | 65 | RMT | 1560
| 259 | 6 | Supply of Alluminum LA clamps conforming to A6 of IS 617, with hot dip galvanised bolts and nuts suitable for single zebra/Panther | Elect | Supply | SMR40027 | 357 | EA | 2142
| 260 | 10 | Providing of control cable trench as per DATA-XII | Elect | Labour | SWR22093 | 3148 | RMT | 31480
| 261 | 1 | Supply of MS Powder coated CT Marshalling Box | Elect | Supply | SMR40047 | 3675 | EA | 3675
| 262 | 6 | Painting of feeder name on support including cost of paint | Elect | Labour | SWR12101 | 53 | EA | 318
| 263 | 1 | Erection of Marshalling boxes | Elect | Labour | SWR10940 | 374.85 | EA | 374.85
| 264 | 2 | Supply of 33KV 800A DB Break AB Switch | Elect | Supply | SMR12315 | 40658.78 | EA | 81317.56
| 265 | 400 | Supply of MS Flat 50x6mm | Elect | Supply | SMR12322 | 56.5 | KG | 22600
| 266 | 1000 | Supply of MS Channel 100x50mm | Elect | Supply | SMR22745 | 57.45 | KG | 57450 | 1092660.2737 | 132KV BAY EXTENSION
|  |  | Total | [5 empty] | 19355281.1414 | 19355281.1414
|  |  | 18% GST | [5 empty] | 3483950.6054
| Total Cost (Without GST)=Electrical | [7 empty] | 19355281.1414
| Total Cost (With 18 % GST)=Electrical | [7 empty] | 22839231.7468
|  |  | 33KV Cable | 3000 | Mtrs
|  |  | 11 KV Cable | 5420 | Mtrs

## Allwyn Colony (hidden)
SCHEDULE
Name of the work: Erection, testing and commissioning of 33/11KV Indoor Sub Station with 2x 8MVA PTRs at ALLWYN COLONY , Sanath Nagar area under TGIIC, BanjaraHills Operation Division, Jubileehills Constituency Under T& D Improvement Works.
WBS No: S-1754-12-01-01-01-001 (Electrical)
SNo | S No. | Estimate Quantity (only FigurEs) | Item DEtailEd SpEcification Description | Work Type | Item Short Descripti | Service Code | Rate | UOM | Amount
Electrical Portion
| 1 | 2 | Loading of 8MVA PTR | Elect | Labour | SWR10613 | 5805.84 | EA | 11611.68
| 2 | 2 | Transport of Power transformers (0 to 100 KM) from one place to another place in GHMC Area.(excluding of loading & unloading )-8MVA power transformer | Elect | Labour | SWR10854 | 21945 | EA | 43890
| 3 | 2 | Unloading of 8MVA PTR | Elect | Labour | SWR10627 | 5085.84 | EA | 10171.68
| 4 | 2 | Erection of PTR on constructed plinth-Erection of 8 MVA PTR. | Elect | Labour | SWR21321 | 49480.2 | EA | 98960.4
| 5 | 1 | Loading of 50,63, 75 & 100 KVA DTR | Elect | Labour | SWR10195 | 350 | EA | 350
| 6 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 3299.7
| 7 | 1 | Un loading of 50,63, 75 & 100 KVA DTR | Elect | Labour | SWR10513 | 280 | EA | 280
| 8 | 1 | Construction of DTR Plinth- RCC Column type DTR Plinth of size 1'X1'X10',topslab 4'x4'x6" & beam size 4'X8'X8" upto 160KVA | Elect | Labour | SWR21843 | 25967.57 | EA | 25967.57
| 9 | 1 | Erection of 3 Phase DTRs 63,75 & 100 KVA including loading and Unloading DTR on the Structure/Plinth etc | Elect | Labour | SWR20905 | 1650 | EA | 1650
| 10 | 16 | Loading of 11 KV VCBs along with Panel boards | Elect | Labour | SWR10199 | 1024 | EA | 16384
| 11 | 8 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 26397.6
| 12 | 16 | Un loading of 11 KV VCBs along with Panel boards | Elect | Labour | SWR10517 | 1044.48 | EA | 16711.68
| 13 | 16 | Erection of 11KV indoor switch gear panel/indoor PT panel /Bus section panel / Bus raiser panel/Capacitor panel/Switch fuse panel for DTR. | Elect | Labour | SWR10931 | 8894 | EA | 142304
| 14 | 10 | Loading of 33 KV VCBs along with Panel boards | Elect | Labour | SWR10198 | 1024 | EA | 10240
| 15 | 5 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 16498.5
| 16 | 10 | Un loading of 33 KV VCBs along with Panel boards | Elect | Labour | SWR10516 | 1044.48 | EA | 10444.8
| 17 | 10 | Erection of 33KV indoor switch gear panel/33KV indoor PT panel / Bus section panel / Bus raiser panel | Elect | Labour | SWR10930 | 9847 | EA | 98470
| 18 | 1 | Loading of 220 V Batterry with charger | Elect | Labour | SWR11166 | 1612 | SET | 1612
| 19 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 3299.7
| 20 | 1 | Un loading of 220 V Batterry with charger | Elect | Labour | SWR11147 | 1024 | SET | 1024
| 21 | 1 | Erection of 220 V, 80 AH battery in complete shape fit for charging . Conventional lead acid | Elect | Labour | SWR12295 | 7666 | EA | 7666
| 22 | 1 | Supply of AC Supply panel inluding providing of changeover switch, SFU, metering unit, 32 A three phase MCB, 16 A Single phase MCB complete as per specification. | Elect | Supply | SMR40045 | 42000 | EA | 42000
| 23 | 1 | Erection of control/Relay panels, AC Panels, announciationpanels etc in the control room duly mounting them on channels and grouting them with foundation bolts excluding cost of channels & foundation bolts | Elect | Labour | SWR11893 | 2122 | EA | 2122
| 24 | 44 | Cutting Charges for RS joist 150x150mm | Elect | Labour | SWR10297 | 48 | EA | 2112
| 25 | 0.83 | Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elect | Labour | SWR10869 | 3426 | TO | 2843.58
| 26 | 3.83 | Alligning the Main and Auxiliary structures such as RS joist,M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication. | Elect | Labour | SWR10867 | 1470 | TO | 5630.1
| 27 | 3.83 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes,labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Elect | Supply | SMR40009 | 2181 | TO | 8353.23
| 28 | 3.83 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters ofthinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes,labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Elect | Labour | SWR10877 | 851 | TO | 3259.33
| 29 | 3.83 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc | Elect | Supply | SMR40010 | 1293 | TO | 4952.19
| 30 | 3.83 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium | Elect | Labour | SWR10879 | 482 | TO | 1846.06
| 31 | 43 | Painting of Name Plates for any equipment | Elect | Labour | SWR10963 | 122 | EA | 5246
| 32 | 36 | Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Elect | Supply | SMR11482 | 3486 | EA | 125496
| 33 | 36 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 44431.2
| 34 | 36 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50M height | Elect | Labour | SWR10359 | 386 | EA | 13896
| 35 | 531.9 | Laying of MS Flats /GI Flats 75x 8mm earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment andconnecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes including fabrication | Elect | Labour | SWR10920 | 65 | RMT | 34573.5
| 36 | 208.3 | Fabrication and connecting of M.S./ G.I. Flat 50x6mm to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. | Elect | Labour | SWR10919 | 41 | RMT | 8540.3
| 37 | 50 | Supply of GI Bolts & Nuts | Elect | Supply | SMR11488 | 117.5 | KG | 5875
| 38 | 314 | Paint-Black to all Earth Flat incl. Pain | Elect | Labour | SWR12217 | 55 | M | 17270
| 39 | 2 | Supply of Copper Flexible jumper with 75 X 8 of length 250 mm at neutral of Power tranformer end and 50 X 6 of length 50mm two Nos at double neutral end duly brasing with flexible jumper of capacity of 5kA/3 sec for power transformer neutral | Elect | Supply | SMR40033 | 4725 | EA | 9450
| 40 | 2 | Providing of double earthing for neutral with flexible copper jumpers including arrangement by fixing M.S.Channel 100x50mm | Elect | Labour | SWR11892 | 1323 | EA | 2646
| 41 | 106 | Laying of 4No's single core 630 sqmm UG cable (Single Circuit with one spare cable) including excavation of trench of size 0.7 Mtrs width and 1.2 Mtrs depth from road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.Lay-4 SC 33KV 630sqmm UG Cb HG/BC/RE/NS | Elect | Labour | SWR12110 | 2463.3 | M | 261109.8
| 42 | 56 | Raising of Single Run 33KV 1x630sqmm UG Cb on Support | Elect | Labour | SWR12448 | 133 | M | 7448
| 43 | 106 | Laying of second cable 33KV UG Cb in Existing Duct | Elect | Labour | SWR12452 | 200 | M | 21200
| 44 | 14 | Raising of Single Run 33kV 3x400 Sqmm Cu cable on already erected support with wooden / MS clamps and connecting it to over head line withcable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Elect | Labour | SWR11954 | 135.66 | M | 1899.24
| 45 | 8 | Supply of 33KV 1x630Sqmm GIS ID Unit EndTermination | Elect | Supply | SMR12473 | 2500 | EA | 20000
| 46 | 8 | Supply of 33KV 1x630Sqmm OD Unit EndTermination | Elect | Supply | SMR12474 | 4200 | EA | 33600
| 47 | 8 | Installation of 33KV 1x630Sqmm GIS ID EndTermination | Elect | Labour | SWR12473 | 17600 | EA | 140800
| 48 | 8 | Installation of 33KV 1x630Sqmm OD Unit EndTermination | Elect | Labour | SWR12474 | 4000 | EA | 32000
| 49 | 4 | Making of Outdoor/Indoor 33 KV 3x400 Sqmm End Termination | Elect | Labour | SWR10387 | 2764.76 | EA | 11059.04
| 50 | 85 | Laying of XLPE UG cable Single Run including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders/Normal soil / CC/BT Road 11KV 3x185 Sqmm Cable | Elect | Labour | SWR11920 | 465.46 | M | 39564.1
| 51 | 15 | Raising of Single Run 11 KV 3x185 Sqmm Cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Elect | Labour | SWR11956 | 126.23 | M | 1893.45
| 52 | 2 | Making of Outdoor/Indoor 11 KV 3x185 Sqmm Cable End Termination | Elect | Labour | SWR10390 | 2370.63 | EA | 4741.26
| 53 | 90 | Laying of XLPE UG cable Single Run including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders/Normal soil / CC/BT Road LT 3 1/2 x 185 Sqmm Cable | Elect | Labour | SWR11923 | 377.63 | M | 33986.7
| 54 | 10 | Raising of Single Run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-LT 3 1/2 x 185 Sqmm Cable | Elect | Labour | SWR11959 | 85.43 | M | 854.3
| 55 | 2 | Fixing of Oout Door/Indoor end termination LT 3 1/2 x185 Sqmm Cable | Elect | Labour | SWR10765 | 968.9 | EA | 1937.8
| 56 | 2200 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends . | Elect | Labour | SWR11879 | 27 | M | 59400
| 57 | 500 | Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per specification (including cost of ferrules, lugs and glands) | Elect | Labour | SWR12510 | 27 | EA | 13500
| 58 | 1.6 | Fabrication of Main and Auxiliary structures with welding using raw steel such as RS joist, M.S.Angles, Plates, Channels, including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elect | Labour | SWR10869 | 3426 | TO | 5481.6
| 59 | 1.6 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Elect | Supply | SMR40009 | 2181 | TO | 3489.6
| 60 | 1.6 | Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Elect | Labour | SWR10877 | 851 | TO | 1361.6
| 61 | 1.6 | Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. | Elect | Supply | SMR40010 | 1293 | TO | 2068.8
| 62 | 1.6 | Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . | Elect | Labour | SWR10879 | 482 | TO | 771.2
| 63 | 5 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Elect | Labour | SWR11040 | 990.68 | EA | 4953.4
| 64 | 5 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Box pole 9/10/11 Mtr | Elect | Labour | SWR11266 | 2643.83 | EA | 13219.15
| 65 | 4.7 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.-Including the cost of cement | Elect | Labour | SWR10356 | 6579 | M3 | 30921.3
| 66 | 0.155 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Elect | Labour | SWR11890 | 3893.03 | M3 | 603.4197
| 67 | 5 | Paint of coping with 2 coats of white cement incl cost of paints etc. | Elect | Labour | SWR11089 | 48 | EA | 240
| 68 | 1 | Erection of 11 KV HG Fuse set including earthing | Elect | Labour | SWR10395 | 740.52 | SET | 740.52
| 69 | 1 | Erection of 11KV 200A TT type AB Switch including fixing of cross angles and alignment complete | Elect | Labour | SWR20102 | 1813.49 | EA | 1813.49
| 70 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.-Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elect | Labour | SWR10881 | 142 | EA | 142
| 71 | 1 | Erection of LT distribution box including laying of LT cable from distribution box to LT OH line and DTR to distribution box including earthing of distribution box and crimping of lugs connecting of jumpers etc | Elect | Labour | SWR10674 | 1594.67 | EA | 1594.67
| 72 | 18 | Supply of earthing pipe with materials GI Flat 25X3 mm | Elect | Supply | SMR11485 | 105 | KG | 1890
| 73 | 30 | Running of GI eartn flat of size 25X3mm from all metallic parts of channels, AB Switch, HG fuse set, DTr neutral and LT Distribution box and inter connection of earth pits etc complete. | Elect | Labour | SWR12125 | 14.03 | M | 420.9
| 74 | 2 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 2048
| 75 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 3299.7
| 76 | 2 | Un loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11231 | 1024 | DR | 2048
| 77 | 8 | Supply of stepped tubular poles single way made of steel of length 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9 mm, 2.1 mtrs with outer dia 76.1 mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79 kgf as per IS 2713. | Elect | Supply | SMR40051 | 13913 | EA | 111304
| 78 | 8 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Elect | Labour | SWR11039 | 928 | EA | 7424
| 79 | 8 | Erection of tubular poles | Elect | Labour | SWR10955 | 1379 | EA | 11032
| 80 | 6.1 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.-Including the cost of cement | Elect | Labour | SWR10356 | 6579 | M3 | 40131.9
| 81 | 0.248 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Elect | Labour | SWR11890 | 3893 | M3 | 965.464
| 82 | 8 | Paint of coping with 2 coats of white cement incl cost of paints etc. | Elect | Labour | SWR11089 | 48 | EA | 384
| 83 | 8 | Supply of Metal Handle Lamp 150W | Elect | Supply | SMR24635 | 6450 | EA | 51600
| 84 | 50 | Supply of GI Bolts & Nuts,washers etc. | Elect | Supply | SMR11488 | 117.5 | KG | 5875
| 85 | 8 | Fixing of Metal halide lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5 GI pipe complete. | Elect | Labour | SWR10956 | 1268 | EA | 10144
| 86 | 1 | Supply of Steel almarah(61/2 X 3ft) Godrej | Elect | Supply | SMR40061 | 9818 | EA | 9818
| 87 | 750 | Supplying & fabrication erection of 6mm Checkerd plates as per the field conditions | Elect | Labour | SWR10873 | 83 | KG | 62250
| 88 | 12 | Supply of Rubber mats ( 6’x3’) size for indoor SS | Elect | Supply | SMR40068 | 1386 | EA | 16632
| 89 | 1 | Supply of Alluminium Ladder for indoor works | Elect | Supply | SMR40062 | 4410 | EA | 4410
| 90 | 2 | Supply of Trolley mounted CO2 (6.5Kgs) | Elect | Supply | SMR40087 | 9240 | EA | 18480
| 91 | 2 | Supplu of Fire Buckets Stand with Buckets | Elect | Supply | SMR40088 | 1386 | SET | 2772
| 92 | 6 | Supply of Fire Extinguisher for Control Room | Elect | Supply | SMR40089 | 4620 | EA | 27720
| 93 | 4 | Supply of Safety Helmet of standard make | Elect | Supply | SMR40071 | 231 | EA | 924
| 94 | 4 | Supply of Earth Rods (8ft) Screw & clamp type | Elect | Supply | SMR40066 | 578 | EA | 2312
| 95 | 4 | Supply of Hand Gloves | Elect | Supply | SMR40067 | 289 | SET | 1156
| 96 | 1 | Supply of Stand basic cell phone with charger | Elect | Supply | SMR40069 | 1386 | EA | 1386
| 97 | 1 | Supply of Table (3x6ft) Godrej | Elect | Supply | SMR40057 | 6050 | EA | 6050
| 98 | 4 | Supply of S type chairs (Godrej) | Elect | Supply | SMR40058 | 924 | EA | 3696
| 99 | 1 | Supply of Angle racks(18x36.6inches) Godrej | Elect | Supply | SMR40060 | 1733 | EA | 1733
| 100 | 10 | Supply of Danger boards with clamps | Elect | Supply | SMR40070 | 116 | EA | 1160
| 101 | 1 | Supply of 33/11kv S.S Permanent name board | Elect | Supply | SMR40086 | 10238 | EA | 10238
| 102 | 1 | Supply of Wall clock standard make | Elect | Supply | SMR40059 | 578 | EA | 578
| 103 | 1 | Supply of Taparia Tool kit complete as per Spec | Elect | Supply | SMR40063 | 4925 | SET | 4925
| 104 | 1 | Supply of Rechargeable LED torch light. | Elect | Supply | SMR40064 | 1733 | EA | 1733
| 105 | 1 | Supply of Hack saw (12 inches) | Elect | Supply | SMR40065 | 289 | EA | 289
| 106 | 8 | Supply of LC Boards | Elect | Supply | SMR40072 | 116 | EA | 928
| 107 | 2 | Supply of Gum Boots | Elect | Supply | SMR40073 | 693 | EA | 1386
| 108 | 1 | Supply of Digital clamp meter. | Elect | Supply | SMR40076 | 2888 | EA | 2888
| 109 | 1 | Supply of 5000v megger | Elect | Supply | SMR40074 | 13860 | EA | 13860
| 110 | 1 | Supply &fixing of board ind Switchyard layout | Elect | Labour | SWR20032 | 1654 | EA | 1654
| 111 | 1 | Supply & fixing safety inst/SS Op. inst board | Elect | Labour | SWR22090 | 2205 | EA | 2205
| 112 | 1 | Supply of 10ft Aluminium Ladder | Elect | Supply | SMR12378 | 1654 | EA | 1654
| 113 | 3000 | Supply of RS Joist Grider Pole (150x150mm) | Elect | Supply | SMR12302 | 59.25 | KG | 177750
| 114 | 830 | Supply of MS Channel 100x50mm | Elect | Supply | SMR22745 | 57.45 | KG | 47683.5
| 115 | 2500 | Supply of MS Flat 75x8mm | Elect | Supply | SMR12321 | 56.42 | KG | 141050
| 116 | 500 | Supply of MS Flat 50x6mm | Elect | Supply | SMR12322 | 56.5 | KG | 28250
| 117 | 400 | Supply of MS Channel 100x50mm | Elect | Supply | SMR22745 | 57.45 | KG | 22980
| 118 | 2 | Supply of 33KV 3x400Sqmm O/D End Kit | Elect | Supply | SMR22222 | 4554 | EA | 9108
| 119 | 2 | Supply of of 33KV 3x400Sqmm Indoor end kit | Elect | Supply | SMR11506 | 3589.96 | EA | 7179.92
| 120 | 1 | Supply of 11KV 3x185 Heat Shble O/d End Term Kit | Elect | Supply | SMR25201 | 1182.97 | EA | 1182.97
| 121 | 1 | Supply of 11KV 3x185 Heat Shble I/d End Term Kit | Elect | Supply | SMR25202 | 1085 | EA | 1085
| 122 | 100 | Supply of LT XLPE Cable 3 1/2 C 185 sqmm | Elect | Supply | SMR25204 | 547 | M | 54700
| 123 | 1500 | Supply of RS Joist Pole (175x85mm) | Elect | Supply | SMR12303 | 60.75 | KG | 91125
| 124 | 100 | Supply of MS Channel 75x40 mm | Elect | Supply | SMR25205 | 58.45 | KG | 5845
| 125 | 1 | Supply of 11KV HG FuseSet for StationTransformer | Elect | Supply | SMR12324 | 1974 | EA | 1974
| 126 | 1 | Supply of 11KV 200A Tilting Type AB Switch | Elect | Supply | SMR12318 | 8991 | EA | 8991
| 127 | 1 | Supply of LT Distribution Box (SMC) | Elect | Supply | SMR25200 | 7797 | EA | 7797
| 128 | 60 | Supply of LT XLPE Cable 1C 150 sqmm | Elect | Supply | SMR25203 | 114.83 | M | 6889.8 | 2705165.3936 | SS LABOUR
| 129 | 1 | survey line&cabl inc peg mark&tree clear | Elect | Labour | SWR22092 | 765 | KM | 765
| 130 | 28 | Loading of 11/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 28672
| 131 | 28 | Unloading of 11/33KV XLPE UG Cable all sizes | Elect | Labour | SWR11231 | 1024 | DR | 28672
| 132 | 14 | Transport of Cond Drum,VCBs upto 10Km | Elect | Labour | SWR11860 | 2720.34 | EA | 38084.76
| 133 | 4200 | Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters ,providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet,3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts,Along the CC / BT multi layer road requiring compressor for 33 KV 3x400 Sqmm Cable | Elect | Labour | SWR11980 | 1388.84 | M | 5833128
| 134 | 4200 | Lay-2nd Cable in Excavated Trench | Elect | Labour | SWR10988 | 204.1 | M | 857220
| 135 | 42 | Supply & Erection of Smart RFID marker | Elect | Labour | SWR25089 | 2745 | EA | 115290
| 136 | 34 | Making of Straight through joint 33kv 3x400 xlpe | Elect | Labour | SWR10382 | 5700.78 | EA | 193826.52
| 137 | 1000 | Supply of 6" B class GI pipe | Elect | Supply | SMR40081 | 1044 | M | 1044000
| 138 | 100 | Supply of 6" DWC pipe | Elect | Supply | SMR11610 | 1012 | M | 101200
| 139 | 100 | Supply of Hume pipe 9" size | Elect | Supply | SMR40001 | 125 | M | 12500
| 140 | 10 | Making of OD/Idoor end termination 33kv 3x400 xlpe | Elect | Labour | SWR10387 | 2764.76 | EA | 27647.6
| 141 | 80 | Raising of single run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)33KV 3x400sqmm UG Cb on support | Elect | Labour | SWR11954 | 135.66 | M | 10852.8
| 142 | 4200 | Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours. | Elect | Labour | SWR21903 | 30 | M | 126000
| 143 | 12 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Elect | Labour | SWR10642 | 512.55 | EA | 6150.6
| 144 | 12 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Elect | Labour | SWR10640 | 1132 | EA | 13584
| 145 | 6 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Elect | Labour | SWR11040 | 990.68 | EA | 5944.08
| 146 | 2 | Erection of 9/10/11Meter Box pole | Elect | Labour | SWR11266 | 2643.83 | EA | 5287.66
| 147 | 208.3 | Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc.M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) | Elect | Labour | SWR10919 | 41 | RMT | 8540.3
| 148 | 5.64 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.Including the cost of cement | Elect | Labour | SWR10356 | 6579 | M3 | 37105.56
| 149 | 0.186 | Coping & Muffing-Iron Pole,Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Elect | Labour | SWR11890 | 3893.01 | M3 | 724.0999
| 150 | 0.6 | Fabrication of Main and Auxiliary structures with welding using raw steel such as RS joist, M.S.Angles, Plates, Channels, including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elect | Labour | SWR10869 | 3426 | TO | 2055.6
| 151 | 2 | Erection of 33 KV LAS station/Line type including earthing | Elect | Labour | SWR10396 | 880 | SET | 1760
| 152 | 2 | Erection of 33 KV AB Switch including alignment and earthing | Elect | Labour | SWR10392 | 4500 | EA | 9000
| 153 | 4 | Supply of CI Pipe earthing 80mm dia 2.75m long | Elect | Supply | SMR11483 | 2789 | EA | 11156
| 154 | 4 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and | Elect | Labour | SWR10357 | 1234.2 | EA | 4936.8
| 155 | 4 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Elect | Labour | SWR10359 | 386 | EA | 1544
| 156 | 42 | Supply of Pre-cast cable Joint markersSupply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters , CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | Elect | Supply | SMR40085 | 484 | EA | 20328
| 157 | 6 | Painting of feeder name on support including cost of paint | Elect | Labour | SWR12101 | 53 | EA | 318
| 158 | 100 | Supply of GI Bolts & Nuts,Washers etc., | Elect | Supply | SMR11488 | 117.5 | KG | 11750
| 159 | 2 | AB Switch Coil Earthing GI No. 8 Wire | Elect | Labour | SWR12331 | 146.63 |  | 293.26
| 160 | 2 | Painting AB switch OP rods with PO red | Elect | Labour | SWR10881 | 142 | EA | 284
| 161 | 2 | 33 KV DP Structure with 175x85/150x75mm RS joist Assembly and erection of Structure as per specification which includes fixing of top channels and cross bracings, transport of all materials from road side to the location, earthing, back filling with earth ramming etc excluding pit excavation and concreting. | Electrical | Labour | SWR11276 | 5670 | SET | 11340
| 162 | 6 | Loading of 33 KV, 10 KA LAs Station type | Electrical | Labour | SWR10266 | 41 | EA | 246
| 163 | 6 | Un loading of 33 KV, 10 KA LAs Station type | Electrical | Labour | SWR10584 | 35 | EA | 210
| 164 | 34 | Supply of 33KV3x400Sqmm Straight thr kit | Elect | Supply | SMR22223 | 24151 | EA | 821134
| 165 | 8 | Supply of 33KV 3x400Sqmm O/D End Kit | Elect | Supply | SMR22222 | 4554 | EA | 36432
| 166 | 2 | Supply of 33KV 3x400Sqmm Indoor end kit | Elect | Supply | SMR11506 | 3589.96 | EA | 7179.92
| 167 | 3000 | Supply of RS Joist Pole (175x85mm) | Elect | Supply | SMR12303 | 60.75 | KG | 182250
| 168 | 500 | Supply of MS Flat 50x6mm | Elect | Supply | SMR12322 | 56.5 | KG | 28250
| 169 | 600 | Supply of MS Channel 100x50mm | Elect | Supply | SMR22745 | 57.45 | KG | 34470
| 170 | 2 | Supply of 33KV 800A DB Break AB Switch | Elect | Supply | SMR12315 | 40658.78 | EA | 81317.56 | 9761450.1199 | 33KV LINE LABOUR
| 171 | 1 | survey line&cabl inc peg mark&tree clear | Elect | Labour | SWR22092 | 765 | KM | 765
| 172 | 10 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 10240
| 173 | 10 | Un loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11231 | 1024 | DR | 10240
| 174 | 5 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 16498.5
| 175 | 2920 | Laying of Single Run XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.Along the CC / BT multi layer road requiring compressor for 11 KV 3x300 Sqmm Cable | Elect | Labour | SWR11928 | 1073.94 | M | 3135904.8
| 176 | 80 | Raising of Single RUN cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)11 KV 3x300 Sqmm Cable | Elect | Labour | SWR11955 | 144.08 | M | 11526.4
| 177 | 30 | Supply & Erection-Smart RFID marker | Elect | Labour | SWR25089 | 2745 | EA | 82350
| 178 | 12 | Making of Straight through joint 11kv 3x300 xlpe | Elect | Labour | SWR10386 | 3725.45 | EA | 44705.4
| 179 | 600 | Supply of 4" B class GI pipe | Elect | Supply | SMR40080 | 740 | M | 444000
| 180 | 100 | supply of 4" DWC pipe | Elect | Supply | SMR11609 | 759 | M | 75900
| 181 | 200 | Suppy of Hume pipe 4" size | Elect | Supply | SMR40003 | 80 | M | 16000
| 182 | 16 | Making 11 KV 3x300 Sqmm Cable Out Door/Indoor end termination | Elect | Labour | SWR10391 | 2370.63 | EA | 37930.08
| 183 | 2920 | Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours. | Elect | Labour | SWR21903 | 30 | M | 87600
| 184 | 16 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Elect | Labour | SWR10642 | 512.55 | EA | 8200.8
| 185 | 16 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Elect | Labour | SWR10640 | 1132 | EA | 18112
| 186 | 8 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Elect | Labour | SWR11040 | 990.68 | EA | 7925.44
| 187 | 8 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Box pole 9/10/11 Mtr | Elect | Labour | SWR11266 | 2643.83 | EA | 21150.64
| 188 | 208.3 | M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground)Fabrication and connecting to risers from earth mat to structures, equipment,marshalling boxes, electrical panels, PLCC panels, fencing posts etc. | Electrical | Labour | SWR10919 | 41 | RMT | 8540.3
| 189 | 7.52 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.Including the cost of cement | Elect | Labour | SWR10356 | 6579 | M3 | 49474.08
| 190 | 0.248 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Elect | Labour | SWR11890 | 3892.98 | M3 | 965.459
| 191 | 0.9 | Fabrication of Main and Auxiliary structures with welding using raw steel such as RS joist, M.S.Angles, Plates, Channels, including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elect | Labour | SWR10869 | 3426 | TO | 3083.4
| 192 | 8 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Elect | Labour | SWR10393 | 3200 | EA | 25600
| 193 | 8 | Supply of CI eath pipe with 80mm dia,2.0 M Length | Elect | Supply | SMR11483 | 2789 | EA | 22312
| 194 | 8 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 9873.6
| 195 | 8 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Elect | Labour | SWR10359 | 386 | EA | 3088
| 196 | 30 | Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters , CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | Elect | Supply | SMR40085 | 484 | EA | 14520
| 197 | 8 | Painting of feeder name on support including cost of paint | Elect | Labour | SWR12101 | 53 | EA | 424
| 198 | 100 | S-GI Bolts & Nuts,Washers etc., | Elect | Supply | SMR11488 | 117.5 | KG | 11750
| 199 | 8 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Elect | Labour | SWR12331 | 146.63 | EA | 1173.04
| 200 | 8 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elect | Labour | SWR10881 | 142 | EA | 1136
| 201 | 12 | Supply of 11KV 3x300 Heat Shble str thr JointKit | Elect | Supply | SMR25210 | 4110.17 | EA | 49322.04
| 202 | 8 | Supply of 11KV 3x300 Heat Shble O/d End Term Kit | Elect | Supply | SMR25208 | 1372.88 | EA | 10983.04
| 203 | 8 | Supply of 11KV 3x300 Heat Shble I/d End Term Kit | Elect | Supply | SMR25209 | 1459.83 | EA | 11678.64
| 204 | 4000 | Supply of RS Joist Pole (175x85mm) | Elect | Supply | SMR12303 | 60.75 | KG | 243000
| 205 | 500 | Supply of MS Flat 50x6mm | Elect | Supply | SMR12322 | 56.5 | KG | 28250
| 206 | 600 | Supply of MS Channel 75x40 mm | Elect | Supply | SMR25205 | 58.45 | KG | 35070
| 207 | 300 | Supply of MS Angle 65X65X6 | Elect | Supply | SMR25207 | 57.25 | KG | 17175
| 208 | 8 | Supply of 11KV 800A DB Break AB Switch | Elect | Supply | SMR12316 | 30847.46 | EA | 246779.68 | 4823247.339 | 11KV LINE LABOUR
| 209 | 3 | Erection of 33 KV AB Switch including alignment and earthing | Elect | Labour | SWR10392 | 4500 | EA | 13500
| 210 | 1 | Erection of 33 KV LAS station/Line type including earthing | Elect | Labour | SWR10396 | 880 | SET | 880
| 211 | 1 | Loading of 33 KV VCBs along with Panel boards | Elect | Labour | SWR10198 | 1024 | EA | 1024
| 212 | 1 | Un loading of 33 KV VCBs along with Panel boards | Elect | Labour | SWR10516 | 1044.48 | EA | 1044.48
| 213 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excludingof loading unloading)Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 3299.7
| 214 | 1 | Erection of 33 KV VCB with Control Panel | Elect | Labour | SWR10460 | 12500 | EA | 12500
| 215 | 1 | Erection of 33 KV CTs | Elect | Labour | SWR10399 | 1079 | EA | 1079
| 216 | 4.8 | Excavate-Pit for 33KV VCB | Elect | Labour | SWR23224 | 331 | EA | 1588.8
| 217 | 40 | Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per specification (including cost of ferrules, lugs and glands) | Elect | Labour | SWR12510 | 27 | EA | 1080
| 218 | 3 | Supply of stepped tubular poles single way made of steel of length 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9 mm, 2.1 mtrs with outer dia 76.1 mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79 kgf as per IS 2713. | Elect | Supply | SMR40051 | 13913 | EA | 41739
| 219 | 3 | Erection of tubular poles | Elect | Labour | SWR10955 | 1379 | EA | 4137
| 220 | 3 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE / CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA/OSRAM/SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life morethan 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existingpoles in the Substations, with five years warranty,90W LED Fixture set | Elect | Supply | SMR11594 | 8200 | EA | 24600
| 221 | 3 | Fixing of Metal halide lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5GI pipe complete | Elect | Labour | SWR10956 | 1268 | EA | 3804
| 222 | 60 | Labour for Fixing of all types of clamps | Elect | Labour | SWR10917 | 65 | EA | 3900
| 223 | 1100 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends . | Elect | Labour | SWR11879 | 27 | EA | 29700
| 224 | 5.109 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc, Including the cost of cement | Elect | Labour | SWR10356 | 6579 | M3 | 33612.111
| 225 | 0.186 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Elect | Labour | SWR11890 | 3893 | M3 | 724.098
| 226 | 3 | Excavation of pits in all soils except hard rock requiring blasting 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") 1.05 cum | Elect | Labour | SWR10107 | 700 | EA | 2100
| 227 | 6 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Elect | Labour | SWR10642 | 512.55 | EA | 3075.3
| 228 | 3 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Box pole 9/10/11 Mtr | Elect | Labour | SWR11266 | 2643.83 | EA | 7931.49
| 229 | 6 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Elect | Labour | SWR10640 | 1132 | EA | 6792
| 230 | 0.04 | Extention of 33KV Bay at 132/33KV Sub-station Supply of Zebra condutor | Elect | Supply | SMR24910 | 299369 | KM | 11974.76
| 231 | 9 | Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | Elect | Labour | SWR10884 | 224 | EA | 2016
| 232 | 7 | Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Elect | Supply | SMR11482 | 3486 | EA | 24402
| 233 | 18 | Supply of T Clamps | Elect | Supply | SMR24912 | 500 | EA | 9000
| 234 | 9 | Supply of Twin Zebra connector | Elect | Supply | SMR24911 | 600 | EA | 5400
| 235 | 10 | Supply & spreading of 20mm machine crushed metal (HBG) including cost of conveneyance of all materials, labour charges etc complete for finished item of work and directed by the engineer incharge | Elect | Labour | SWR10860 | 2113 | M3 | 21130
| 236 | 7 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4Mts.) duly filling with bentonite, earth , running of earth wireetc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 8639.4
| 237 | 7 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Elect | Labour | SWR10359 | 386 | EA | 2702
| 238 | 6 | Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x1.8 x 0.75 cum for VCB Plinth | Elect | Labour | SWR20685 | 5160 | M3 | 30960
| 239 | 6.4 | Plastering 2 Coats,20/16mm(1:6)(1:4) | Elect | Labour | SWR10862 | 373 | Sqm | 2387.2
| 240 | 3 | Loading of 33 KV, 10 KA LAs Station type | Elect | Labour | SWR10266 | 41 | EA | 123
| 241 | 3 | Un loading of 33 KV, 10 KA LAs Station type | Elect | Labour | SWR10584 | 35 | EA | 105
| 242 | 3 | Making of coil earthing pole with 8mm GI wireNut&Bolts for ABSwitch | Elect | Labour | SWR12331 | 146.63 | EA | 439.89
| 243 | 3 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elect | Labour | SWR10881 | 142 | EA | 426
| 244 | 3 | 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M (1.31cum) | Elect | Labour | SWR10108 | 629.85 | EA | 1889.55
| 245 | 166.67 | Fabrication and connecting to risers from earth mat to structures, equipment,marshalling boxes, electrical panels, PLCC panels, fencing posts etc.M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) | Elect | Labour | SWR10919 | 41 | RMT | 6833.47
| 246 | 1 | Fabrication of Main and Auxiliary structures with welding using raw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elect | Labour | SWR10869 | 3426 | MT | 3426
| 247 | 3 | Supply of 33KV 800A DB Break AB Switch | Elect | Supply | SMR12315 | 40658.78 | EA | 121976.34
| 248 | 400 | Supply of MS Flat 50x6mm | Elect | Supply | SMR12322 | 56.5 | KG | 22600
| 249 | 1500 | Supply of RS Joist 175x85mm | Elect | Supply | SMR12303 | 60.75 | KG | 91125
| 250 | 1000 | Supply of MS Channel 100x50mm | Elect | Supply | SMR22745 | 57.45 | KG | 57450 | 623116.589 | 33KV BAY EXTENSION
|  |  | Total | [5 empty] | 17912979.4416 | 17912979.4415
|  |  | 18% GST | [5 empty] | 3224336.2995
| Total Cost (Without GST)=Electrical | [7 empty] | 17912979.4416
| Total Cost (With 18 % GST)=Electrical | [7 empty] | 21137315.741
|  |  | 33KV Cable | 4200 | Mtrs
|  |  | 11 KV Cable | 2920 | Mtrs