## Stretch IA
Name of the work:Shifting of 33KV&11KV Lines, DTRs & Erection of 11KV RMUs at Stretch -IA: NeoPolis Circle to ORR Service Roadfor Integrated Development of Kokapet Layout including construction of Trumpet and interchange at Narsingi (V)of Ibrahimbagh Division of ECGH Division in Master Plan/Rangareddy Circle under DC Works. Estimate Number-Y-2022-13-03-02-01-001.
SI.No. | Estimate Quantity | Item Detailed Specification Description | Work Type eg. Earth Work, Electrical works. Etc | Item Short Description | APSS / Morth Cl. Number | Rate (INR) | UOM | Amount
1 | 90 | Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) - 33 KV 3x400 Sqmm Cable | Elec | Labour | SWR12004 | 323.85 | M | 29146.5
2 | 800 | Excavation & laying of UG Cable (Four Run)-Laying of XLPE UG cable Four Run including excavation of trench of size 1050mm wide to 1200mm wide as per the site conditions and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second,third or more cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. Across the CC/ BT road crossing multi layer road requiring compressor (excluding the cost of Hume pipe) 33 KV 3x400 Sqmm Cable | Elec | Labour | SWR12045 | 2244 | M | 1795200
3 | 250 | Excavation & laying of UG Cable (Four Run)-Laying of XLPE UG cable Four Run including excavation of trench of size 1050mm wide to 1200mm wide as per the site conditions and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second,third or more cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. Along the CC / BT multi layer road requiring compressor -33 KV 3x400 Sqmm Cable | Elec | Labour | SWR12040 | 2103.75 | M | 525937.5
4 | 1000 | Lay-Second 33KV UG Cb in Existing Duct | Elec | Labour | SWR12452 | 200 | M | 200000
5 | 3150 | Laying of 2nd cable in excavated trench | Elec | Labour | SWR10988 | 204.1 | M | 642915
6 | 23 | UG Cables Joints-Making of Straight through joints-33 KV 3x400 Sqmm Cable | Elec | Labour | SWR10382 | 5700.78 | EA | 131117.94
7 | 18 | Un loading of 11KV/33KV XLPE UG Cable for all sizes | Elec | Labour | SWR11231 | 1024 | DR | 18432
8 | 18 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Elec | Labour | SWR11230 | 1024 | DR | 18432
9 | 9 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)- Above 30 Km and upto 50 Km with Lorry for each trip | Elec | Labour | SWR11863 | 4372.74 | EA | 39354.66
10 | 100 | Supply of GI Bolts & Nuts etc | Elec | Supply | SMR11488 | 117.5 | KG | 11750
11 | 65 | Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters , CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | Elec | Supply | SMR40085 | 484 | EA | 31460
12 | 100 | Supply of earthing pipe with materials-Supply of GI Flat 25X3 mm | Elec | Supply | SMR11485 | 105 | KG | 10500
13 | 5 | Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Elec | Supply | SMR11482 | 3486 | EA | 17430
14 | 2 | Erection of OH Lines including AB Cable (33KV, 11KV, LT)-Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation- Box pole 12 Mtr | Elec | Labour | SWR11267 | 3901.37 | EA | 7802.74
15 | 2 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation - Erection of 5 Mts RS Joist (Bit) Pole including fixing of Pole Mounted Box | Elec | Labour | SWR20863 | 1044.23 | EA | 2088.46
16 | 3.86 | Earth work excavation of pits in hard murram/rock boulders | Elec | Labour | SWR20959 | 1530 | M3 | 5905.8
17 | 3.86 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.- Including the cost of cement | Elec | Labour | SWR10356 | 6579 | M3 | 25394.94
18 | 350 | Supply of 9" B class GI pipe | Elec | Supply | SMR40082 | 1113 | M | 389550
19 | 2 | Erection of 33 KV AB Switch including alignment and earthing | Elec | Labour | SWR10392 | 4500 | EA | 9000
20 | 1 | Erection of 33 KV LAS station/Line type including earthing | Elec | Labour | SWR10396 | 880 | SET | 880
21 | 1.6 | Fabrication of Main and Auxiliary structures with welding using raw steel such as RS joist, M.S.Angles, Plates, Channels, including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elec | Labour | SWR10869 | 3426 | TO | 5481.6
22 | 1.6 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub- station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.-Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Elec | supply | SMR40009 | 2181 | TO | 3489.6
23 | 1.6 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub- station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete- Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Elec | Labour | SWR10877 | 851 | TO | 1361.6
24 | 1.6 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete-(*)Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc.(*) Note:-The requirement of 2nd coat is to be justified by the concerned Divisional Engineer /Executive Engineer before execution of this work | Elec | supply | SMR40010 | 1293 | TO | 2068.8
25 | 1.6 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete-(*) Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium .(*) Note:-The requirement of 2nd coat is to be justified by the concerned Divisional Engineer /Executive Engineer before execution of this work | Elec | Labour | SWR10879 | 482 | TO | 771.2
26 | 0.375 | "Providing of Base Concreting with 1:3:6 Concrete Mix including materials & curing with water | Elec | Labour | SWR12294 | 5053.01 | M3 | 1894.88
27 | 1300 | Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours. | Elec | Labour | SWR21903 | 30 | M | 39000
28 | 10.527 | Loading of MS Scrap | Elec | Labour | SWR10258 | 578 | TO | 6084.61
29 | 1.227 | Loading of ACSR conductor scrap | Elec | Labour | SWR10257 | 491 | TO | 602.46
30 | 1.227 | Un loading of ACSR conductor scrap | Elec | Labour | SWR10575 | 491 | TO | 602.46
31 | 10.527 | Un loading of MS Scrap | Elec | Labour | SWR10576 | 578 | TO | 6084.61
32 | 11.754 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) - Above 30 KM and upto 50 KM | Elec | Labour | SWR10134 | 587.52 | TO | 6905.71
33 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)- Above 30 Km and upto 50 Km with Lorry for each trip | Elec | Labour | SWR11863 | 4372.74 | EA | 4372.74
34 | 8 | S&E-Smart RFID marker | Elec | Labour | SWR25089 | 2745 | EA | 21960
35 | 5 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elec | Labour | SWR10357 | 1234.2 | EA | 6171
36 | 5 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Elec | Labour | SWR10359 | 386 | EA | 1930
37 | 1 | Erection of 33KV 3 Way RMU | Elec | Labour | SWR11335 | 5775 | EA | 5775
38 | 1 | Raising of RMU plinth with Bricks 4 sides including crane cost, labour with white washing excluding cable jointing for 3 Way/5 Way RMUs | Elec | Labour | SWR12210 | 4200 | EA | 4200
39 | 22.63 | Fabrication of Main and Auxiliary structures with welding using raw steel such as RS joist, M.S.Angles, Plates, Channels, including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elec | Labour | SWR10869 | 3426 | TO | 77530.38
40 | 22.63 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. -Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Elec | supply | SMR40009 | 2181 | TO | 49356.03
41 | 22.63 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. -Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Elec | Labour | SWR10877 | 851 | TO | 19258.13
42 | 22.63 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. -(*)Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. (*) Note:-The requirement of 2nd coat is to be justified by the concerned Divisional Engineer /Executive Engineer before execution of this work | Elec | supply | SMR40010 | 1293 | TO | 29260.59
43 | 22.63 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. -(*) Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium .(*) Note:-The requirement of 2nd coat is to be justified by the concerned Divisional Engineer /Executive Engineer before execution of this work | Elec | Labour | SWR10879 | 482 | TO | 10907.66
44 | 10 | Making of Outdoor/Indoor End Termination - 33 KV 3x400 Sqmm Cable | Elec | Labour | SWR10387 | 2764.76 | EA | 27647.6
45 | 1.2 | Dismantling of 100 sqmm Conductor DC | Elec | Labour | SWR22064 | 11816.7 | KM | 14180.04
46 | 8 | Dismatling of M type tower | Elec | Labour | SWR11122 | 3484 | EA | 27872
47 | 8 | Dimantle-Extension of M+3 Tower | Elec | Labour | SWR12480 | 2584.48 | EA | 20675.84
48 | 10 | Dism of Box pole 9/10/11 Mtr | Elec | Labour | SWR11329 | 1130 | EA | 11300
49 | 50 | UG Cable Joint - Making of Straight through joints-11 KV 3x300 Sqmm Cable | Elec | Labour | SWR10386 | 3725.45 | EA | 186272.5
50 | 375 | Supply of 6" B class GI pipe | Elec | supply | SMR40081 | 1044 | M | 391500
51 | 33 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Elec | Labour | SWR11230 | 1024 | DR | 33792
52 | 33 | Un loading of 11KV/33KV XLPE UG Cable for all sizes | Elec | Labour | SWR11231 | 1024 | DR | 33792
53 | 17 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)- Above 30 Km and upto 50 Km with Lorry for each trip | Elec | Labour | SWR11863 | 4372.74 | EA | 74336.58
54 | 2 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Elec | Labour | SWR10393 | 3200 | EA | 6400
55 | 150 | Supply of GI Bolts & Nuts etc | Elec | Supply | SMR11488 | 117.5 | KG | 17625
56 | 4 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation- RS Joists 150x75/175 x 85 mm | Elec | Labour | SWR10346 | 1934 | EA | 7736
57 | 4.2 | Earth work excavation of pits in hard murram/rock boulders | Elec | Labour | SWR20959 | 1530 | M3 | 6426
58 | 4.2 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.- Including the cost of cement | Elec | Labour | SWR10356 | 6579 | M3 | 27631.8
59 | 85 | Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters , CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | Elec | Supply | SMR40085 | 484 | EA | 41140
60 | 3 | Raising of RMU plinth with Bricks 4 sides including crane cost, labour with white washing excluding cable jointing for 3 Way/5 Way RMUs | Elec | Labour | SWR12210 | 4200 | EA | 12600
61 | 3 | Loading of 11KV 3 Way RMU/Twin feeder panel | Elec | Labour | SWR10615 | 907.8 | EA | 2723.4
62 | 3 | Un loading of 11KV 3 Way RMU/Twin feeder panel | Elec | Labour | SWR10629 | 907.8 | EA | 2723.4
63 | 2 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) - Above 30 Km and upto 50 Km with Lorry for each trip | Elec | Labour | SWR11863 | 4372.74 | EA | 8745.48
64 | 60 | Supply of GI Flat 25X3 mm | Elec | Supply | SMR11485 | 105 | KG | 6300
65 | 1650 | Hard Rock Cutting 11KV- Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours. | Elec | Labour | SWR21903 | 30 | M | 49500
66 | 3 | Erection of 11KV 3 Way RMU | Elec | Labour | SWR10664 | 2051.48 | EA | 6154.44
67 | 1 | Erection of 11KV 5 Way RMU | Elec | Labour | SWR11069 | 2783.33 | EA | 2783.33
68 | 1 | Loading of 11KV 5 Way RMU | Elec | Labour | SWR10616 | 1268.63 | EA | 1268.63
69 | 1 | Un loading of 11KV 5 Way RMU | Elec | Labour | SWR10630 | 1268.63 | EA | 1268.63
70 | 7 | S&E-Smart RFID marker | Elec | labour | SWR25089 | 2745 | EA | 19215
71 | 15 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elec | Labour | SWR10357 | 1234.2 | EA | 18513
72 | 15 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Elec | Labour | SWR10359 | 386 | EA | 5790
73 | 45 | Making of Outdoor/Indoor End Termination- 11 KV 3x300 Sqmm Cable | Elec | Labour | SWR10391 | 2370.63 | EA | 106678.35
74 | 50 | Supply of GI Bolts & Nuts etc | Elec | Supply | SMR11488 | 117.5 | KG | 5875
75 | 15 | Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Elec | Supply | SMR11482 | 3486 | EA | 52290
76 | 9.1 | Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x 1.8 x 0.75 cum for VCB Plinth | Elec | Labour | SWR20685 | 5160 | M3 | 46956
77 | 1.05 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.- Including the cost of cement | Elec | Labour | SWR10356 | 6579 | M3 | 6907.95
78 | 2000 | Laying of11KV XLPE UG cable Double Run of Size in Hard Rock(1.05*0.5x1=0.525cum) | Elec | Labour | SWR11004 | 1194 | RMT | 2388000
79 | 1900 | Excavation & laying of UG Cable (Double Run)-Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.-Along the CC / BT multi layer road requiring compressor- 11 KV 3x300 Sqmm Cable | Elec | Labour | SWR11981 | 1264.64 | M | 2402816
80 | 50 | Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)- 11 KV 3x300 Sqmm Cable | Elec | Labour | SWR12005 | 275.4 | M | 13770
81 | 1000 | Excavation & laying of UG Cable (Double Run )-Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.- In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil/CC-11 KV 3x300 Sqmm Cable | Elec | Labour | SWR11973 | 631.06 | M | 631060
82 | 4900 | Laying of XLPE UG cable Six Run including excavation of trench of size 1050mm wide to 1200mm wide as per the site conditions and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second,third or more cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.Across the CC/ BT road crossing multi layer road requiring compressor (excluding the cost of Hume pipe)-Laying of 2nd cable in excavated trench | Elec | Labour | SWR10988 | 204.1 | M | 1000090
83 | 2 | Fabrication of Main and Auxiliary structures with welding using raw steel such as RS joist, M.S.Angles, Plates, Channels, including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elec | Labour | SWR10869 | 3426 | TO | 6852
84 | 2 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. - Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Elec | Suppy | SMR40009 | 2181 | TO | 4362
85 | 2 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.- Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Elec | Labour | SWR10877 | 851 | TO | 1702
86 | 2 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. - (*)Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc.(*) Note:-The requirement of 2nd coat is to be justified by the concerned Divisional Engineer /Executive Engineer before execution of this work | Elec | Suppy | SMR40010 | 1293 | TO | 2586
87 | 2 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. - (*) Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium .(*) Note:-The requirement of 2nd coat is to be justified by the concerned Divisional Engineer /Executive Engineer before execution of this work | Elec | Labour | SWR10879 | 482 | TO | 964
88 | 2.5 | Dismantling of 11KV 34/55 sqmm SC | Elec | Labour | SWR22065 | 4500 | KM | 11250
89 | 19 | Dism of 9.1M PSCC Pole | Elec | Labour | SWR11320 | 948.09 | EA | 18013.71
90 | 2 | Dismantling of 11kv TT type AB switch | Elec | Labour | SWR12172 | 889.73 | EA | 1779.46
91 | 5 | Erection of 3 Phase DTRs 63,75 & 100 KVA | Elec | Labour | SWR20905 | 1650 | EA | 8250
92 | 5 | RCC Column type DTR Plinth of size 1'X1'X10',topslab 4'x4'x6" & beam size 4'X8'X8" upto 160KVA | Elec | Labour | SWR21843 | 25967.57 | EA | 129837.85
93 | 15 | Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Elec | Suppy | SMR11482 | 3486 | EA | 52290
94 | 5 | Erection of 11KV 200A TT type AB Switch including fixing of cross angles and alignment complete | Elec | Labour | SWR20102 | 1813.49 | EA | 9067.45
95 | 5 | Erection of 11 KV HG Fuse set including earthing | Elec | Labour | SWR10395 | 740.52 | SET | 3702.6
96 | 5 | Erection of OH Lines including AB Cable (33KV, 11KV, LT)-Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation- Box pole 9/10/11 Mtr | Elec | Labour | SWR11266 | 2643.83 | EA | 13219.15
97 | 5.25 | Earth work excavation of pits in hard rock requiring blasting.(wherever feasible/ required) | Elec | Labour | SWR20769 | 1012.35 | M3 | 5314.84
98 | 5.25 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.-Including the cost of cement | Elec | Labour | SWR10356 | 6579 | M3 | 34539.75
99 | 2.25 | Fabrication of Main and Auxiliary structures with welding using raw steel such as RS joist, M.S.Angles, Plates, Channels, including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elec | Labour | SWR10869 | 3426 | TO | 7708.5
100 | 2.25 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. - Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Elec | Suppy | SMR40009 | 2181 | TO | 4907.25
101 | 2.25 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. - Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Elec | Labour | SWR10877 | 851 | TO | 1914.75
102 | 2.25 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. - (*)Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc.(*) Note:-The requirement of 2nd coat is to be justified by the concerned Divisional Engineer /Executive Engineer before execution of this work | Elec | supply | SMR40010 | 1293 | TO | 2909.25
103 | 2.25 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. - (*) Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium .(*) Note:-The requirement of 2nd coat is to be justified by the concerned Divisional Engineer /Executive Engineer before execution of this work | Elec | Labour | SWR10879 | 482 | TO | 1084.5
104 | 5 | Dismantling of DTR plinth (Column type) | Elec | Labour | SWR20070 | 2008.13 | EA | 10040.65
105 | 160 | Supply of GI Flat 25X3 mm | Elec | Suppy | SMR11485 | 105 | KG | 16800
106 | 5 | Dismantling of 11 KV HG fuse set including earthing | Elec | Labour | SWR11745 | 353.43 | SET | 1767.15
107 | 5 | Dismantling of 11kv TT type AB switch | Elec | Labour | SWR12172 | 889.73 | EA | 4448.65
108 | 5 | Dismantle of 3-Ph DTR ( Upto 160 KVA) | Elec | Labour | SWR11729 | 975.12 | EA | 4875.6
109 | 15 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elec | Labour | SWR10357 | 1234.2 | EA | 18513
110 | 15 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Elec | Labour | SWR10359 | 386 | EA | 5790
| Total Estimate | [6 empty] | 12322212.68
| Service Tax 18% Rs. | [6 empty] | 2217998.2824
| Grand Total Rs. | [6 empty] | 14540210.9624